## Significant
OE Reports
Event Summary Monthly by Significance (2017 August)
Report Status: Published
User(s): admin, N/A, WMMOS42
Centre(s): Atlanta, Moscow, Paris, Tokyo
Member(s): Multiple members selected
Date Range (Published Date): 01.08.2017 To 31.08.2017
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER PAR 14-0097 | 2014-03-27 03:53 | Doel 3 | 2014-03-25 |  | Units conservatively shutdown as Reactor Vessel test results for the time being not in accordance with expectations | 01 | 2017-08-22 04:54 | Significant | A test about mechanical resistance on an irradiated material sample of reactor vessel with hydrogen flakes didn't deliver the expected values at the two sites. The utility then conservatively decided to shut down the reactor and start the outage one month earlier than scheduled. This event is classified as significant because the unplanned outage extension of more than 20 days. | The origin of hydrogen flakes was probably due to the manufacturing process. The stations provided detailed analysis of the flakes in the attachments. |  | 2 - Important lessons, reactor shutdown, reactor vessel | CM.1

## Noteworthy
OE Reports
Event Summary Monthly by Significance (2017 August)
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 17-0329 | 2017-08-07 21:13 | Fuqing 3 | 2017-01-01 |  | Main control room operator station unavailable | 00 | 2017-08-07 21:13 | Noteworthy | During normal operation, the digital computer information and control system (KIC) in the main control room became unavailable for 4.7 hours caused by the clock hopping failure. This result in an unplanned reduction in power to 78%. This event is Noteworthy because operators lost an important information and control systems. | The direct cause was the code transmission from primary master clock to secondary master clock got wrong information. The clock signal hopping caused the KIC being lost efficiency because of the disordered internal clock signal of system. The root causes were the design deficiencies of primary main and spare master clocks and the problem with timing mechanism of the KIC system. The maintenance personnel did not track the synchronization mechanism of repaired software and push the manufacturer to finish the modification. |  | 2 - Important lessons, computer, design criteria / design basis, digital control system / digital components, power reduction | ER.3 , MA.2 , PI.2
WER PAR 17-0443 | 2017-08-17 06:58 | Hongyanhe 1 | 2017-01-03 |  | Startup Failures during low power test on emergency diesel generator train A | 00 | 2017-08-17 06:58 | Noteworthy | During normal operation, four start-up failures were observed during low power test of one emergency diesel generator (EDG) train. This event is classified as Noteworthy because of potential common mode failure of all the diesel generators installed at the plant. (see WER PAR 17-0325) | The direct causes were fracture of the cylinder starting air valve core, failure of the self-locking nuts and faulty startup circuits. The root cause was inadequate material (nylon) of the cylinder starting valve nut and defective relays. |  | 2 - Important lessons, common mode failure, design criteria / design basis, diesel engine, diesel generator, vendor, vibration | EN.1 , ER.3
WER ATL 17-1070 | 2017-08-29 14:21 | Mcguire 2 | 2017-02-23 19:22 |  | Safety Injection Pressure Boundary Leak due to Thermal Fatigue caused by Cross-Flow In-Leakage | 00 | 2017-08-29 14:21 | Noteworthy | During normal operation, a reactor coolant system (RCS) pressure boundary leak occurred from a safety injection pipe. The reactor was shut down to carry out repair. The event is Noteworthy because it resulted in a 13-day forced outage. | The root cause was thermal fatigue damage to the safety injection line from RCS cross-loop interactions due to leaking check valves. This was a design vulnerability. The contributing causes were back leakage across check valves and inadequate monitoring. |  | 2 - Important lessons, check valve, design criteria / design basis, fatigue cracking, leak, reactor coolant, reactor shutdown, safety injection | CM.1 , ER.2 , ER.3
WER ATL 17-1042 | 2017-08-25 09:30 | Limerick 2 | 2017-05-08 06:09 |  | Instrument Line Nozzle Leak Identified During Reactor Pressure Vessel Leakage Test | 00 | 2017-08-25 09:30 | Noteworthy | During cold shutdown and while performing reactor pressure vessel leakage test, a 2-inch diameter water level instrument nozzle penetration was visibly leaking in the drywell. This resulted in an outage extension of two weeks. This event is Noteworthy due to long duration of repairs. | The most probable root cause was intergranular stress corrosion cracking originated from a construction defect. The contributing causes was high residual stresses during the welding process and the alloy 600 material bored out to its final dimension after it was annealed. |  | 2 - Important lessons, erosion/corrosion, leak, nozzle, outage extension , reactor vessel, stress corrosion, weld | ER.3 , ER.4
WER ATL 17-0991 | 2017-08-03 15:54 | Turkey Point 3 | 2017-03-18 |  | #PRELIMINARY# Unplanned Reactor Trip from 100% as a Result of the Loss of a 4kv Bus | 00 | 2017-08-03 15:54 | Noteworthy | During normal operation, an internal bus fault resulted in an arc flash and loss of a safety-related 4.16 kV electrical bus. This caused an automatic reactor scram and declaration of an alert emergency. Following the reactor scram, one train of decay heat removal was lost. All three reactor coolant pumps tripped and an emergency diesel generator started but did not load. In addition, a worker sustained a burn and ankle injuries. This event is classified as Noteworthy because it resulted in loss of safety-related bus, declaration of emergency and a personal injury. | The direct cause was a foreign material which entered the 4.16 kV bus current limiting reactor coil cubicle. The thermo-lag installation procedure did not include instructions for the control of foreign material and did not include precautions for the control of the carbon fiber mesh that was used as part of the thermo-lag installation. A faulty mental model for prevention of foreign material intrusion and inadequate risk assessment were contributors. |  | 2 - Important lessons, automatic scram, bus bar, FME, injury, procedure inadequacy, risk assessment | MA.1 , MA.2

## Trending
OE Reports
Event Summary Monthly by Significance (2017 August)
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 17-0368 | 2017-08-29 21:49 | Qinshan 3 1 | 2016-12-20 |  | Leakage Rate of Internal Ball Valve of Spent Fuel Channel Exceeded the Limit | 00 | 2017-08-29 21:49 | Trending | During normal operation and while testing leakage of a ball valve clearance of spent fuel channel, the leakage rate exceeded the test limit. This resulted in entry into a limiting condition of operation. | The direct cause was damage to the graphite seat gaskets at floating end of the ball valve. The root cause was inadequate pre-compressing force of the graphite seat gasket due to undefined installation standard and incomplete technical requirement. |  | 1 - For information only, gasket, leak, limiting condition of operation, procedure inadequacy, procurement, valve | ER.1 , ER.3 , MA.2
WER TYO 17-0366 | 2017-08-24 20:23 | Qinshan 2 3 | 2017-07-13 |  | Fire on the insulation of No.2 main steam isolation valve body of Unit 3, Qinshan 2 | 00 | 2017-08-24 20:23 | Trending | During normal operation, smoke and open flames were detected on the insulation of a main steam isolation valve (MSIV). The reactor was manually scrammed and the unit was entered in an emergency standby state. | The direct cause was a failure of a hydraulic oil control box resulting on a fire due to high surface temperature of the valve's body. The root cause was installation deficiency of pipe joint O-ring seal during vendor's maintenance. Causal factors were problem of oil inleakage into insulated cotton was not considered and protection device in case of oil leakage has not been designed in MSIV actuator. |  | 2 - Important lessons, fire, insulation thermal, leak, main steam isolation valve, manual scram, oil, o-ring , risk assessment, vendor | CM.1 , ER.3
WER TYO 17-0363 | 2017-08-24 02:41 | Hanul 3 | 2017-05-07 |  | Foreign Materials Leading to Essential Service Water Blockage | 00 | 2017-08-24 02:41 | Trending | During normal operation, an outlet pressure of an essential service water (ESW) pump increased following a sudden drop of the ESW flow. Three days later affected ESW train was stopped and entry into limiting condition for operation was required. Inspection of the piping system internals found that foreign materials (coating fragments) were partially blocked the orifice, which in turn reduced the ESW flow. | The direct cause was a polyethylene coat separated from the interior surface of the ESW piping and acted as foreign material in the system. The root cause was inadequate ESW system piping inspection procedure. Contributing cause was ineffective periodic internal checks for the ESW piping. |  | 2 - Important lessons, essential service water, FME, limiting condition of operation, preventive maintenance, procedure inadequacy | ER.2 , MA.2
WER TYO 17-0362 | 2017-08-24 02:39 | Hanul 4 | 2017-05-25 |  | Spurious Indication of Control Element Assembly Out-of-position due to Optical Modem Failure | 00 | 2017-08-24 02:39 | Trending | During normal operation, a spurious indication generated alarms for out-of-position of a control rod. Two limiting condition for operation was entered to rectify this issue. | The direct cause was a signal hunting of the optical transmitter-receiver modem for the control rod. The root cause was ageing of the transmit-receive isolation modem due to long-term service use above recommended by the manufacturer. The contributing cause was a lack of preventive maintenance for the optical modem. |  | 1 - For information only, ageing, control circuit, digital control system / digital components, limiting condition of operation, preventive maintenance | ER.2 , ER.3
WER TYO 17-0360 | 2017-08-24 02:14 | Hanbit 4 | 2017-06-01 |  | Abnormal Startup of Emergency Diesel Generator B during Refueling Outage | 00 | 2017-08-24 02:14 | Trending | During the refuelling outage and while measuring insulation resistance on one train of engineered safety features actuation system sub-group relay contacts, an emergency diesel generator was automatically started due to a false signal of engineered safety features. | The direct cause was a false signal due to the closing of the subgroup relay contacts. The root cause was a latent error due to improperly connected cables from the construction period. Contributing cause was inadequate signal blocking. |  | 1 - For information only, diesel generator, reactor protection system, relay | ER.3
WER TYO 17-0355 | 2017-08-23 21:50 | Wolsong 2 | 2017-06-23 |  | Internal Leak of Liquid Injection Shutdown System Quick Opening Valve (PV1J) | 00 | 2017-08-23 21:50 | Trending | During normal operation and while conducting the liquid injection shutdown system low-pressure channel functional test, a level decrease of the poison injection tank was observed once a channel tripped. A limiting condition for operation was entered. | The direct cause was an internal leak on a pressure regulating valve. The probable root cause was local plastic deformation had taken place from a prolonged three years use of the soft disk material. |  | 1 - For information only, leak, limiting condition of operation, reactor protection system, surveillance | ER.1 , ER.3
WER TYO 17-0354 | 2017-08-23 21:01 | Wolsong 1 | 2017-05-28 |  | Automatic Reactor Trip Due to Reactor Coolant Pumps Shutdown Following Failed Power Transfer during Outage | 00 | 2017-08-23 21:01 | Trending | During power reduction for a planned outage and while transferring from onsite power to offsite power, closing an alternate breaker caused a normal breaker to open. Due to opening of normal breaker, a loss of a 13.8 kV bus occurred, two primary heat transport pumps stopped, the reactor automatically scrammed and start up of a standby diesel generator occurred. | The root cause was inadequate adjustment of the breaker's compressive spring and coupling bar. Contributing cause were inadequate coupling bar margin and insufficient design data collection and delivery process of the manufacturer. |  | 1 - For information only, automatic scram, breaker, loss of offsite power, power reduction, vendor | CM.1 , EN.1 , MA.1
WER TYO 17-0353 | 2017-08-23 20:58 | Wolsong 2 | 2017-06-21 |  | Fuel Oil Leakage during Operation of Standby Diesel Generator No. 2 | 00 | 2017-08-23 20:58 | Trending | During normal operation, a fuel oil leakage was found in the fuel oil return line of a standby diesel generator (SDG), specifically at mechanical union connection in a bypass line upstream of a pipe for SDG fuel oil system. A limiting condition for operation was entered and the SDG was declared inoperable. | The direct cause was two leaks, first from the fuel oil return line of the SDG due to uneven thread surfaces produced by small vibration and second from flexible connection in the discharge side of injection pump of the SDG due to ageing related failure of O-rings. Contributing cause low quality maintenance on the SDG during last planned outage and use of O-ring for long period of time. |  | 1 - For information only, ageing, diesel fuel, diesel generator, leak, limiting condition of operation, o-ring , vibration | ER.3 , MA.1
WER TYO 17-0350 | 2017-08-22 03:50 | Kanupp 1 | 2017-03-03 |  | Manual Reactor Shutdown due to Steam Pressure Sagging | 00 | 2017-08-22 03:50 | Trending | During normal operation, primary pump seal differential pressure alarms start annunciated and a steam pressure was found sagging. As a result a primary charging tank level started decreasing and when the steam pressure reached a limit, a reactor was manually shutdown. | The direct cause was sheared shaft of a helium pump. Contributing causes were previous maintenance was overdue due to operation check in uncouple and couple condition did not indicate any issue, helium blowers were not available at that time and the bearings used in existing pump have become obsolete. |  | 1 - For information only, preventive maintenance, procurement, reactor coolant pump seal, reactor shutdown, vendor | ER.2 , ER.3
WER TYO 17-0349 | 2017-08-20 21:39 | Maanshan 2 | 2017-04-28 |  | Foreign material was found on the lower core plate of reactor vessel. | 00 | 2017-08-20 21:39 | Trending | During an outage and while cutting thimble tubes, foreign material was found on the lower core plate of reactor vessel. It resulted in delay in fuel reloading for 8 hours. | The direct cause was falling of the brushes used during thimble tube cutting. The root cause was a failure to exclude foreign material. |  | 1 - For information only, FME, outage extension , reactor vessel | MA.2
WER TYO 17-0348 | 2017-08-20 20:53 | Qinshan 2 1 | 2017-03-23 |  | Card failure of safety injection system of unit 1 caused a safety injection train’s automatic control unavailable. | 00 | 2017-08-20 20:53 | Trending | During normal operation and after test on a reactor protection system, an operator in the main control room found safety injection differential pressure transmitter high flow alarm left illuminated on a board. One train of low pressure safety injection automatic control was unavailable. | The direct cause was a fault on an alarm card relay contact. The root cause was that the rack 24V relay did not have backward diode installed in parallel as required by design, and the counter electromotive force generated in coil did not have energy consumption circuit. |  | 1 - For information only, reactor protection system, relay, safety injection, surveillance | ER.1 , ER.3
WER TYO 17-0347 | 2017-08-20 20:48 | Qinshan 2 4 | 2017-03-25 |  | Break of flange gasket in 4VVP005PU caused large high-temperature and high-pressure steam leakage | 00 | 2017-08-20 20:48 | Trending | During normal operation, high temperature and high pressure steam leakage was observed from steam trap of main steam pipeline system bypass. There was a potential for personnel injury and equipment safety. | The direct cause was a break of the medium flange gasket. The root cause was a wrong gasket material. Differences between old and new gaskets were not recognized due to lack of questioning attitude. |  | 1 - For information only, gasket, leak, steam, vendor | ER.3 , MA.1
WER TYO 17-0346 | 2017-08-16 01:55 | Takahama 3 | 2017-07-12 |  | Injury of a contractor’s worker | 00 | 2017-08-16 01:55 | Trending | During the tunnel construction work, a worker got injured in his right leg being hit by a pipe which came off from the concrete blaster when he was engaged in the cleaning of the concrete blaster. The worker was absence from work for 2 months. | The direct cause was a leakage in the compressed air supply valve, which was placed in the closed position in preparation of the cleaning work. The leakage had pressurized the inside of the pipe due to the valve disc was not fully closed. Accordingly, when the woker was loosening the pipe fitting, the pipe came off. |  | 1 - For information only, industrial safety, injury | ER.1 , IS.1
WER TYO 17-0345 | 2017-08-13 19:43 | Maanshan 2 | 2017-04-14 |  | The Containment Liner thickness in Unit 2 was less than acceptance criteria when performing Liner UT | 00 | 2017-08-13 19:43 | Trending | During an outage and while performing the containment liner ultrasonic testing, the liner thickness was below the acceptance criteria. | The cause was a dent caused by an unknown physical impact. |  | 1 - For information only, containment penetration | ER.1
WER TYO 17-0343 | 2017-08-09 01:47 | Qinshan 2 1 | 2017-06-27 |  | Reactor tripped during T3 test of Unit 1. | 00 | 2017-08-09 01:47 | Trending | During normal operation and while performing a routine test of the reactor protection system, simultaneous trip of three main feedwater pumps triggered protection signal resulting in a reactor scram and turbine trip. | The direct cause of the feedwater pumps trip was short-circuit. The root cause was human error. Inadequate risk analysis for short-circuit operations in the procedures was a contributor. |  | 1 - For information only, anticipated transient without scram, automatic scram, feedwater pump, human error, procedure inadequacy, risk assessment, single point vulnerability, turbine trip | MA.1 , MA.2 , OF.2
WER TYO 17-0342 | 2017-08-09 01:19 | Qinshan 2 4 | 2016-11-23 |  | The emergency diesel generator train B of Unit 4 became inoperable due to fault trip of the electric pre-heater | 00 | 2017-08-09 01:19 | Trending | During normal operation, the electric heater of the high-temperature-water preheating loop of an emergency diesel generator (EDG) tripped. This resulted in the preheating water temperature lower than 55 degree C during hot standby of the EDG and consequently entry into a limiting condition of operation. | The direct cause was a faulty drawer thermal relay. The root cause was a manufacturing defect by vendor in the slider of the in-drawer thermal relay. |  | 1 - For information only, diesel generator, limiting condition of operation, relay, vendor | ER.3
WER TYO 17-0340 | 2017-08-08 20:10 | Rajasthan 2 | 2016-11-02 |  | Reactor trip on PHT High pressure. | 00 | 2017-08-08 20:10 | Trending | During operation at 84% power, the turbine generator (TG) tripped on high boiler level. Primary heat transport (PHT) system pressure went high, resulting in automatic reactor scram on PHT high pressure. The event resulted in a 3-day outage. | The cause was clogging of the measuring leg of the boiler level transmitter resulting on the level indication not changing. The cause of the clogging was crud accumulation due to inadequate boiler blow down during previous startup. The cause of PHT pressure increase was a delay in the opening of atmospheric steam discharge control valves due to a faulty relay. |  | 1 - For information only, automatic scram, debris / crud, level instrument, preventive maintenance, relay, steam generator / boiler, turbine trip | ER.2 , OP.1
WER TYO 17-0339 | 2017-08-08 19:53 | Fuqing 2 | 2015-05-25 |  | Unblocked low-pressure 4 safety injection signal of diverse actuation system (DAS) pressurizer resulted in mistake start up of safety injection in train A | 00 | 2017-08-08 19:53 | Trending | During commissioning stage, unblocked low pressure safety injection signal of diverse actuation system (DAS) pressuriser resulted in start up of a safety injection pump. | The commissioning personnel did not check the blocking signal of the DAS for confirmation. The operator did not identify the abnormal alarm, and did not response to such alarm according to the alarm card. | SOER 2013-1 Rec 3 | 1 - For information only, human error, safety injection pump | OP.1 , OP.2
WER TYO 17-0335 | 2017-08-08 02:24 | Fuqing 1 | 2016-11-18 |  | Plate heat exchangers of Component Cooling System Blocked Frequently | 00 | 2017-08-08 02:24 | Trending | During normal operation, the plate heat exchangers of component cooling system (CCS) blocked frequently resulting in low flow rate of the CCS. | The cause was internal blocking of the heat exchanger with sediment. Sediment or shellfish entered into the heat exchanger through the gap between the shellfish trap and cylinder. The root cause was improper management of water intake during the commissioning and operation with no desilting work for a long period. Large size of mesh opening of the shellfish trap filter and poor dosing effect, resulting in shells growing in the pipeline were contributors. | SOER 2007-2 Rec 4 | 1 - For information only, essential service water, intake, preventive maintenance | CM.1 , ER.2 , ER.3
WER TYO 17-0333 | 2017-08-08 02:21 | Fuqing 3 | 2016-10-07 |  | Abnormal vibration of steam turbine | 00 | 2017-08-08 02:21 | Trending | During commissioning and while performing a test at 100% power, the turbine generator was shut down manually due to abnormal vibration of turbine bearing. | The direct cause was the exhaust steam temperature of intermediate pressure cylinder dropped too quickly, and intermediate pressure cylinder was heated unevenly causing friction. The root cause was the opening of secondary reheat control valve failed to adjust the downstream pressure in time. Inadequate operating procedure&nbsp;was a&nbsp;contributor. |  | 1 - For information only, bearing, procedure inadequacy, turbine trip, vibration | ER.3 , OP.2
WER TYO 17-0331 | 2017-08-08 01:13 | Fuqing 2 | 2016-12-01 |  | Rod bank SA was elevated to 232 steps without plan during Dynamic Rod Worth Measurement in outage | 00 | 2017-08-08 01:13 | Trending | During startup and while performing the dynamic rod worth measurement test, a rod bank was raised to lifting upper limit unnecessarily. | The direct cause was the rod bank had a wrong demanded rod position, causing 29 more lifting orders to be sent to rod bank. The root causes were deficient skills of the tester, inadequate communication, inadequate design and a deficient procedure. Operator did not pay close attention to deal with the alarm. Human error prevention tools were not fully used. |  | 1 - For information only, control rod, human error, procedure inadequacy, reactivity management | CM.4 , OP.1 , OP.2
WER TYO 17-0330 | 2017-08-07 22:42 | Fuqing 2 | 2015-07-25 |  | Failure to refresh operator station display trend resulted in loss of effective supervision in power rise process | 00 | 2017-08-07 22:42 | Trending | During hot standby and while performing zero-power and level power distribution measurement test, the operator station display trend was not refreshed resulting in the leader not timely identifying the power rise. This resulted in increase in the reactor power beyond the level required by the inspection procedure. | The direct cause was human error as the trend group data was not refreshed and the display screen became a straight line after a period of time. The root cause was inadequate design of the computer control system software.&nbsp; | SOER 2013-1 Rec 3 | 1 - For information only, computer, design criteria / design basis, digital control system / digital components, human error, reactivity management | CM.1 , OP.1
WER TYO 17-0327 | 2017-08-07 19:33 | Chinshan 2 | 2017-04-05 |  | Several vital load trips due to latent problems in uninterruptible power supply (UPS) system | 01 | 2017-08-09 04:10 | Trending | During normal operation, several vital AC loads tripped when the uninterruptible power supply (UPS) was manually switched to the alternate AC source. This resulted in the unit half scram. | The direct cause was malfunction of the static switch. The root cause was latent problems in the UPS system. |  | 1 - For information only, power supply, switch | ER.1
WER TYO 17-0326 | 2017-08-06 21:18 | Chasnupp 3 | 2017-07-06 |  | #PRELIMINARY# Manual Reactor Trip due to Condensers Vacuum Degradation. | 00 | 2017-08-06 21:18 | Trending | During normal operation, all circulating water pumps tripped on loss of pump/motor bearing lubricating and cooling water. This resulted in rapid degradation of the condenser vacuum. The reactor was manually scrammed. | Analysis is in progress. |  | 1 - For information only, bearing, condenser vacuum, gas intrusion, manual scram, pump motor | ER.1
WER TYO 17-0321 | 2017-08-04 01:49 | Qinshan 1 | 2016-12-22 |  | Unit outage start up mode rolled back due to a leakage through the weld seam of the platinum resistance thermometer of the main system | 00 | 2017-08-04 01:49 | Trending | During an outage and while performing a reactor heatup, a leakage through the weld seam of the platinum resistance thermometer of the main system was found. The outage critical path was delayed by 48 hours. | The direct cause was defects in the welds of the thermometer adapter and the sockets. The root cause was welding quality defects caused by arc suppression of more than one welds at the same position. |  | 1 - For information only, leak, outage extension , weld | MA.1 , MA.2
WER TYO 17-0320 | 2017-08-03 22:55 | Qinshan 1 | 2016-08-27 |  | Short-time fault of ex-core nuclear instrumentation power range B2 channel (N44) | 00 | 2017-08-03 22:55 | Trending | During operation at 95% power, a power range channel indicated zero power and consequently a control rod automatically lifted. This resulted in increase in nuclear power by 2.3%, which returned to normal after 30 seconds. | The direct cause was zero output of the power range channel. The root cause was failure of central processing unit of the power range channel. |  | 1 - For information only, ageing, nuclear instrumentation, power surge | ER.3
WER TYO 17-0315 | 2017-08-03 02:14 | Kuosheng 1 | 2017-04-14 |  | One Control Rod Drifting out One Notch While Conducting Core Alternations during Refueling Outage | 00 | 2017-08-03 02:14 | Trending | During an outage and while conducting core alterations, one control rod drifted out one notch from the fully inserted position. A limiting condition of operation was entered. | The cause was the channel bowing from the fuel assemblies in the same control cell. The friction exerted by irradiated fuel assemblies in the same control cell to support the control blade was disturbed, thereby causing the control rod to drift out by gravity and become engaged in the notch position. |  | 1 - For information only, control rod drive, limiting condition of operation | CM.4 , FA.1
WER TYO 17-0314 | 2017-08-03 01:31 | Qinshan 2 4 | 2017-03-14 |  | Pressure gauge burst in the Moisture separator reheater of unit 4 and a large amount of steam ejection | 00 | 2017-08-03 01:31 | Trending | During normal operation, a pressure gauge in the pipeline of moisture separator reheater burst and a large amount of high pressure steam leaked out. There was a potential for personnel injury. | The direct cause was bursting of a tin welding joint of red copper bourdon tube in the pressure gauge. The root cause was internal tin welding quality defect of the pressure gauge. |  | 1 - For information only, industrial safety, leak, steam, weld | ER.3 , IS.1
WER TYO 17-0313 | 2017-08-02 22:54 | Maanshan 2 | 2017-05-15 |  | Unit-2 Essential Bus Train-A LOV(Loss Of Voltage) induced by Maloperation | 00 | 2017-08-02 22:54 | Trending | During an outage and while tagging out a standby startup transformer, in-service 345 kV startup transformer tripped causing an essential bus train losing its off-site power and startup of an emergency diesel generator. | The cause was human error. Failure to use three way communication and lack of questioning attitude were contributors. There was inconsistency in disconnect switch operation direction and indication. |  | 1 - For information only, human error, label, loss of offsite power, transformer | OP.1 , OP.2
WER TYO 17-0310 | 2017-08-02 22:31 | Qinshan 1 | 2016-12-01 |  | Abnormal baffle and guide vane of fuel assembly found during the outage unloading process | 00 | 2017-08-02 22:31 | Trending | While fuel unloading during an outage, the grid baffle and guide vane of four groups of fuel assemblies were scratched. | The direct cause was mutual hooking of fuel assemblies during fuel unloading. The root cause was inadequate design of fuel assemblies guide vanes. |  | 1 - For information only, design criteria / design basis, fuel defect | CM.4 , FA.1
WER PAR 17-0476 | 2017-08-29 08:16 | Hartlepool 1 | 2017-04-07 |  | Fire on High Pressure Back Up Cooling Pump No.1 during 12hr test run | 00 | 2017-08-29 08:16 | Trending | During normal operation and while testing a high pressure back up cooling (HPBUC) pump, a fire occurred on top of the HPBUC diesel engine due to oil sprayed on it. The fire was extinguished with a CO2 extinguisher. The event resulted in unavailability of one of the three safety related pumps and consequently entry into a limiting condition of operation. | The direct cause was failure of a fuel injector pipe due to excessive tightening and cyclic vibrations. The root cause was lack of technical oversight of the HPBUC engine repair. The contributing causes were inadequate corrective actions after previous similar event, insufficient quality control during the engine overhaul and inadequate fire protection system. |  | 1 - For information only, contractor, fire, fire suppression, human error, leak, limiting condition of operation, management oversight, vibration | FP.1 , MA.1 , MA.2 , PI.2
WER PAR 17-0474 | 2017-08-29 08:14 | Yangjiang 3 | 2017-02-15 |  | Jetting Leak from Packing of the hydraulic test pump resulted in forced maitenance and limiting condition of operation | 00 | 2017-08-29 08:14 | Trending | During normal operation, leakage was found from the high pressure packing of a safety injection pump. The pump was isolated for maintenance and consequently a limiting condition of operation was entered for both units. | The direct cause was inadequate compression of the packing. The root cause was defect in equipment health status judgment criteria. The contributing factor was incomplete manufacturer completion report. |  | 1 - For information only, charging pump, documentation, leak, limiting condition of operation, vendor | ER.2 , MA.1
WER PAR 17-0467 | 2017-08-28 04:23 | Heysham B1 | 2017-01-11 |  | Turbo-generator 7 overspeed head fault | 00 | 2017-08-28 04:23 | Trending | Since 2012, issues with on load oil injection testing made not possible to successfully test turbine generator overspeed head. Troubleshooting was unsuccessful and it resulted in a fire event of the shaft end cover (see WER PAR 16-0502), reactor downpowers and additional repairs with production loss of about 10 days. | The root cause was significant eccentricity of overspeed load due to inadequate preventive maintenance. The contributors were poor fitting insulation discs, no procedure for refitting the head and clocking overspeed head, inadequate procedure use and inadequate operating experience feedback process. |  | 1 - For information only, preventive maintenance, procedure adherence, procedure inadequacy, vibration | ER.2 , MA.1 , MA.2 , PI.2
WER PAR 17-0465 | 2017-08-21 07:59 | Tricastin 4 | 2017-04-07 |  | Extended overshooting of the limit on maximum permissible power following a turbine control malfunction | 00 | 2017-08-21 07:59 | Trending | During normal operations and while troubleshooting a turbine control malfunction, oscillation of the position of the turbine control valves caused a power increase to an average value of 100.69% with a maximum value of 101.2%. The turbine control function was not working. This event is Noteworthy because the shift manager and safety manager did not recognise the technical specification limit until the following shift challenged this decision. | The causes were failure of a module in the digital frequency correction loop for turbine control. The risk of oscillations in the position of the control valves, and their impact, were not identified during the turbine control measurement activities. Operations fundamentals, inadequate procedures and ineffective communication were contributors. | SOER 2013-1 Rec 3 | 1 - For information only, digital control system / digital components, power surge, procedure inadequacy, risk assessment, turbine control valve | ER.1 , OF.2 , OP.1 , OP.2
WER PAR 17-0462 | 2017-08-17 07:50 | Tihange 1 | 2017-05-20 |  | Emergency shutdown by turbine trip following failure of recirculation pumps | 00 | 2017-08-17 07:50 | Trending | During restart of the unit following a prolonged shutdown, the condenser recirculation system was brought back into service. When the second recirculation pump started, the substantial increase in flow to the suction side of the circulating pumps dislodged a large mass of shellfish and algae that had accumulated in the pipes. The rotating screens became saturated, tripping of both circulating pumps, which in turn tripped the turbines, thereby triggering an emergency shutdown of the reactor. | The direct cause was a high differential pressure in the rotating screens caused by clogging of the condenser recirculation pipes. The root causes were system alignment, the cooling tower return was only partially aligned towards discharge and conditioning of system over a prolonged period. Causal factor was Operations was not aware of the presence of 'dead legs' filled with stagnant river water. | SOER 2007-2 rec.2 | 1 - For information only, condensate booster pump, intake, reactor shutdown, risk assessment, turbine trip | OF.2 , OP.1
WER PAR 17-0460 | 2017-08-17 07:48 | Paluel 3 | 2017-03-31 |  | Dose-rate alarm trip on source-operator’s active dosimeter during valve radiography survey | 00 | 2017-08-17 07:48 | Trending | During an outage and while performing a radiography survey on a valve, a contract worker entered into the radiography area and was exposed with three times higher radiation dose than planned. | The cause was organisational malfunctions such as ineffective coordination between stakeholders, inadequate risk assessment during work execution and use of baseline standards and rules. |  | 1 - For information only, radiation dose, radiation protection, radiograph | RP.2 , RS.1
WER PAR 17-0459 | 2017-08-17 07:47 | Nogent S/Seine 2 | 2017-04-03 |  | Partial unavailability of iodine filtration function due to the degradation of an electrical terminal block | 00 | 2017-08-17 07:47 | Trending | During startup after an outage and while performing a visual inspection of electrical boxes installed as part of a modification, signs of degradation of an electrical thermal block for the control room ventilation system was found. One of the iodine ventilation trains was declared unavailable, resulting in partial unavailability of iodine filtration function. A group 1 limiting condition of operation was entered. | The direct cause was a failure of the thermal block due to overheating. The root cause was incorrect assembly of electrical boxes at the factory. Lack of periodic thermal inspections of electrical boxes was a contributor. |  | 1 - For information only, heating ventilating and air conditioning, limiting condition of operation, preventive maintenance | ER.2 , ER.3
WER PAR 17-0458 | 2017-08-17 07:46 | Fangchenggang 1 | 2017-02-07 |  | Boron Crystallization was Found on the Conduit Surface of Thermocouple Column in In-core Instrumentation (RIC) System | 00 | 2017-08-17 07:46 | Trending | During an outage and while conducting the hydraulic test of primary system at 154bar.g pressure, a small amount of boron crystallization on the surface of a conduit of in-core instrumentation system thermocouple column was identified. This was an indication of damaged integrity of the primary circuit pressure boundary. | The direct cause was a leak on medium of the primary circuit thermocouple conduit weld of the thermal couple column. The root cause was incidental quality defect of the thermocouple column. |  | 1 - For information only, incore detector, leak, vendor, weld | ER.3
WER PAR 17-0457 | 2017-08-17 07:44 | Belleville 2 | 2017-03-14 |  | Spent fuel pool drained by 6 m3 | 00 | 2017-08-17 07:44 | Trending | During normal operation, two spent fuel pool (SFP) sampling valves were found left open for around five hours resulting in the SFP to be drained by 6m3. | The cause was human error. Human error prevention tools were not used during routine laboratory activities. Operating experience from a similar event in Unit 1 in 2015 was not correctly used. Sampling risk analysis was not comprehensive. |  | 1 - For information only, human error, risk assessment, spent fuel storage | CY.1 , OE.1
WER PAR 17-0456 | 2017-08-17 07:43 | Belleville 1 | 2017-03-14 |  | Load variation performed in violation of technical specification action statements | 00 | 2017-08-17 07:43 | Trending | During normal operation in prohibiting load reduction stage requested by the grid operator, the plant conducted a surveillance test on radiation monitoring channel on a steam generator when the grid message 'general alert &ndash; system safety compromised' was activated. This meant the channel was unavailable and entailed declaring one group 1 limiting condition for operation (LCO) and one group 2 LCO. The operators decided to down-powered the unit to 990MW. | The direct cause was a human error. The apparent causes were workers did not adhere to requirements such as no checks were performed of the action statements for the LCOs, the operations fundamentals of control configuration changes at the plant and adopt a careful approach when operating the units were not applied and the shift turnovers did not sufficiently target important points. | SOER 2013-1 rec.3 | 1 - For information only, human error, limiting condition of operation, power reduction, surveillance | NP.1 , OP.1 , OP.2
WER PAR 17-0455 | 2017-08-17 07:42 | Isar 2 | 2017-07-25 |  | Reactor tripped due to a malfunction of the control fluid system during turbine protection test | 00 | 2017-08-17 07:42 | Trending | After power increase to 100% and while performing a turbine protection test, a pressure drop of the turbine trip fluid resulted in a turbine trip and reactor scram. | The direct cause was a wrong position of a solenoid valve in the turbine control fluid system. Inadequate post-maintenance testing was a contributor. The positions of the solenoid valves were not checked before the test. |  | 1 - For information only, automatic scram, configuration control, solenoid valve, turbine trip, valve misposition | CM.2 , MA.2 , OP.1
WER PAR 17-0446 | 2017-08-17 07:01 | Sizewell B 1 | 2016-11-28 |  | Trip of Station Transformer 8 | 00 | 2017-08-17 07:01 | Trending | During normal operation and while switching a circuit breaker in the 400kV sub-station, the plant experienced an unexpected trip of a station transformer and a grid operator circuit. Due to a coincident inoperability of an essential diesel generator (EDG), the station entered a 24 hour technical specification action to restore electrical supplies. The station output remained unaffected. | The direct cause was a failure of the 400kV disconnector owned by the grid. The root cause was a reduced awareness of the importance of reviewing the transmission outage planning monitoring system six week ahead outage programme against the cycle plan. Apparent cause was a very high workload of the duly authorised persons. | SOER 1999-1 rec.1 | 1 - For information only, breaker, risk assessment, transformer, work control | WM.1
WER PAR 17-0445 | 2017-08-17 07:01 | Sizewell B 1 | 2016-11-07 |  | Instrument cable cut during Reserve Ultimate Heat Sink Refurbishment. | 00 | 2017-08-17 07:01 | Trending | With the unit in normal operation, an instrument cable associated with the reserve ultimate heat sink (RUHS) system was accidentally cut during the refurbishment of the RUHS system. One of the RUHS trains was declared inoperable and a 72-hour limiting condition of operation was entered. | The direct cause was human error. The risk of damage to existing cables was not covered in the risk assessment. The risk mitigation did not include a requirement to protect plant cabling during cutting and grinding works. |  | 1 - For information only, human error, limiting condition of operation, risk assessment | MA.2 , WM.1
WER PAR 17-0444 | 2017-08-17 06:59 | Ningde 1 | 2016-09-30 |  | Pressure in the Reactor Coolant System Exceeded the Requirements of Operation Technical Specifications.. | 00 | 2017-08-17 06:59 | Trending | During normal shutdown with a residual heat removal system (RRA) connected, a reactor coolant pump (RCP) was shut down to treat breaking of the aluminum sheet at the expansion joint of a main transformer neutral point due to a typhoon. Two days later a requirement was raised for working on the transformer to stop RCP 2 and RCP 3. It was decided to shut down RCP 3 before RCP 2, due to this pressure in the reactor coolant system increased and temporarily exceeded the limit for RRA mode, violating the operation technical specifications. | The direct cause was shut down of the RCP 2. The root cause was operators lacks of knowledge about the thermal-hydraulic phenomena when RCP2 was shut down and coolant in the pressurizer existed in double states. In addition, inadequate risk analysis of operating values and effective experience feedback was unavailable. | SOER 2002-1 rec.1, SOER 2013-1 rec.3. | 1 - For information only, design criteria / design basis, reactor coolant, reactor coolant pump, technical specification | OE.1 , OP.1
WER PAR 17-0441 | 2017-08-17 06:56 | Hongyanhe 3 | 2017-03-04 |  | A spent fuel pit cooling filtration pump started for 9.5 hours with outlet valve closed. | 00 | 2017-08-17 06:56 | Trending | During an outage with fuel unloaded and when restoring a penetration test, the spent fuel pit cooling filtration pump was mistakenly started for 9.5 hours with outlet valve closed. There was a risk of pump cavitation and damage. | The cause was human error. The isolation manager issued wrong instruction for removing isolation and restoration of online operation. The root causes were insufficient knowledge, skills, and experience of isolation manager and site operators. Lack of questioning attitude was a contributor. |  | 1 - For information only, configuration control, human error, spent fuel storage, valve misposition | CM.2 , OP.1 , OP.2
WER PAR 17-0438 | 2017-08-17 06:51 | Hongyanhe 2 | 2017-05-08 |  | Source range channel signal not triggered exceeding maintenance deadline | 00 | 2017-08-17 06:51 | Trending | During normal shutdown and while performing bi-monthly test on a source range detection channel, a signal loss alarm was not triggered on one backup control panel. This led to violation of the technical specification. | The direct cause was an alarm did not trigger as expected. The root cause was wrong alarm configuration logic. Contributing factors were failure to verify wrong configuration logic by commissioning and the procedure did not cover contents of the program, testing method was wrong, and expected alarm contents were not complete. |  | 1 - For information only, configuration control, procedure inadequacy, source range monitor, surveillance, technical specification | ER.3 , MA.1 , MA.2
WER MOW 17-0181 | 2017-08-26 05:39 | Rovno 4 | 2017-08-25 |  | #PRELIMINARY# Generator 6 of Unit 4 tripped followed by reactor sctram | 01 | 2017-08-27 01:52 | Trending | During normal operation, the turbine generator tripped on ground protection actuation. It resulted in reactor scram on reactor protection actuation. Diesel generator automatically started to energize the vital bus. | The direct cause was degradation of the control cable insulation in the protection circuit. The root cause was under investigation. |  | 1 - For information only, automatic scram, insulation electrical | ER.1
WER MOW 17-0179 | 2017-08-22 10:53 | Bohunice 3 | 2017-06-17 |  | Foreign material detected on the surface of the refuelling pool | 00 | 2017-08-22 10:53 | Trending | During an outage, foreign material was detected on the surface of the refuelling pool. | The cause could not be determined. |  | 1 - For information only, FME | ER.1 , MA.2
WER MOW 17-0177 | 2017-08-22 10:27 | Temelin 2 | 2017-05-25 |  | Deformations in the area of sealing grooves of the main reactor flange joint | 00 | 2017-08-22 10:27 | Trending | During an outage and while performing an inspection, mechanical deformations were found in the sealing grooves of the reactor pressure vessel flange. | The direct cause was human error. Contractor workers were not aware of the damage made to the reactor main dividing plane during removal of the nickel sealing rings. The root causes were ineffective self-checking, use of inadequate tools, poor questioning attitude and deficiencies in personnel work practices. The maintenance instruction did not provide sufficient guidance on taking out the sealing rings. |  | 1 - For information only, contractor, human error, procedure inadequacy, reactor vessel, risk assessment | MA.1 , MA.2
WER MOW 17-0176 | 2017-08-22 10:14 | Rostov 3 | 2017-01-07 |  | Routine Maintenance Extension Due to a Loss of Quick Close Isolation Valve Indication | 00 | 2017-08-22 10:14 | Trending | During restarting of the unit after outage, a loss of a main steam isolation valve position indication was identified on the main control room panels. Consequently, the outage was extended for 60.5 hours. | The direct cause was a plastic deformation on the retainer base metal. The root cause was deficient design due to material used to make the retainer was inadequate to ensure reliable magnet fastening on the stem. |  | 1 - For information only, main steam isolation valve, outage extension | ER.3
WER MOW 17-0175 | 2017-08-17 01:03 | Paks 3 | 2017-01-09 |  | Diesel generator inoperability due to short circuit in excitation circuit diodes | 00 | 2017-08-17 01:03 | Trending | During normal operation and while preforming the emergency diesel generator (EDG) load sequencer test, a short circuit in the excitation system resulted in the EDG being inoperable for approximately 7.5 hours. A limiting condition of operation was entered. | The direct cause was a short circuit in three diodes in the excitation controller. The root cause could not be determined. A similar event had already occurred at unit 4 in 2012. |  | 1 - For information only, diesel generator, diode, limiting condition of operation | ER.1 , PI.2
WER MOW 17-0173 | 2017-08-15 01:56 | Rovno 1 | 2017-08-06 |  | #PRELIMINARY# Reactor Power Reduction to 10% to Repair a Leak from the Non-isolable portion of the Oil Line Associated with the Circulating Water Pump | 00 | 2017-08-15 01:56 | Trending | During normal operation, an oil leak from the non-isolable section of the drain line of circulating water pump was observed.The power was reduced to about 75% to repair the leak. | The cause investigation is in progress. |  | 1 - For information only, leak, oil, power reduction | ER.1
WER MOW 17-0172 | 2017-08-10 13:11 | Temelin 2 | 2017-05-15 |  | False alarm of the lower limit position of the Cluster Control Rod | 00 | 2017-08-10 13:11 | Trending | During normal operation, as part of the mobility verification of all cluster control rods (CCRs), the indication of a lower limit switch (LLS) of the CCR (1st CR of the 3rd bank) failed, resulting into entry into a limiting condition of operation for fault-finding process and replacement of defective component. | The direct cause was hardware cards failure in the control unit. The root cause was failure during estimated service life. |  | 1 - For information only, circuit card, control rod, limiting condition of operation, preventive maintenance | ER.2
WER MOW 17-0171 | 2017-08-10 13:02 | Bohunice 3 | 2017-02-11 |  | Incorrect set pressure switches of steam generator safety valves and unwanted partial opening of the steam generator safety valve when checking of control cabinet pressure switches | 00 | 2017-08-10 13:02 | Trending | During operation at 73% power and while checking&nbsp;pressure switches for one steam generator safety valve, the safety valve partially opened unexpectedly at a pressure lower than the required opening pressure. | The direct cause was incorrect setting of activation pressures of pressure switches. The root cause was inadequate use of human performance tools and inadequate work procedure. The change of setting of pressure switches was caused by high temperature composed to the temperature of the original setting. |  | 2 - Important lessons, common mode failure, human error, procedure adherence, procedure inadequacy, safety relief valve, setpoint | ER.2 , MA.1 , MA.2
WER MOW 17-0170 | 2017-08-02 11:00 | Novovoronezh-2 1 | 2017-07-31 |  | #PRELIMINARY# The Unit Was Tripped Off Line to Troubleshoot High Vibration On Oil Supply Pipelines Associated With the Turbine Control System | 00 | 2017-08-02 11:00 | Trending | During operation at 72% power, high vibration occurred on oil supply pipelines associated with the turbine control system. The unit was shut down to rectify the problem. . | Investigation of the event is in progress. |  | 1 - For information only, reactor shutdown, turbine control, vibration | ER.1
WER MOW 17-0141 | 2017-06-30 04:14 | Zaporozhye 6 | 2017-06-29 |  | The Unit Was Down Powered Due to Loss of Reactor Coolant Pump No.1 (RCP No.1). | 01 | 2017-08-22 10:01 | Trending | During normal operation and while switching an oil cooler to standby, a reactor coolant pump tripped. The unit power was reduced to 25%. | The direct cause was human error. The root causes were deficient documentation, lack of work organization and inadequate work control. |  | 1 - For information only, oil, power reduction, reactor coolant pump | OP.1 , OP.2 , WM.1
WER ATL 17-1096 | 2017-08-31 10:28 | St. Lucie 1 | 2017-01-31 05:00 |  | Reactor Coolant Pressure Boundary Leakage Due to Piping Defect | 00 | 2017-08-31 10:28 | Trending | During a plant shutdown to investigate potential reactor coolant pump seal degradation, a through wall defect was identified on piping of the lower seal heat exchanger of a reactor cooling pump. This resulted in entry into a limiting condition of operation. The reactor was shut down for seven days to carry out repairs. | The most probable cause was the seal heat exchanger design deficiency, which permitted stresses exceeding the yield strength of the assembly tubing during torqueing of the component cooling water flange connection. This caused low stress high cycle fatigue failure of the weld joint. |  | 1 - For information only, design criteria / design basis, fatigue cracking, leak, limiting condition of operation, reactor coolant pump seal, reactor shutdown, torque, weld | ER.3
WER ATL 17-1093 | 2017-08-31 08:32 | Laguna Verde 1 | 2017-07-04 |  | Main Control Room Emergency ventilation automatic startup due to loss of electrical supply to Reactor Protection System Train A | 00 | 2017-08-31 08:32 | Trending | After a manual reactor scram (See WER ATL 17-1091) and while re-establishing the normal electrical supply, a half scram and half isolation signal occurred due to the loss of a reactor protection system (RPS) bus, causing the automatic startup of main control room emergency ventilation filters. | The direct cause was failure to change state of a RPS power panel contactor coil. The root cause was there had been no preventive maintenance plans for the coil during the 25-year operation. A contributing factor was ageing of the components. |  | 1 - For information only, ageing, manual scram, preventive maintenance, reactor protection system | ER.2 , ER.3
WER ATL 17-1091 | 2017-08-30 13:34 | Laguna Verde 1 | 2017-07-04 |  | Manual Reactor SCRAM due to loss of Reactor Recirculation Pump | 00 | 2017-08-30 13:34 | Trending | While operating at 90% power, a switchgear breaker tripped due to a over voltage condition on the grid, causing the trip of a transformer which feeds a 480 VAC bus. One of the result was a reactor recirculation (RRC) pump trip. During the subsequent transient, another RRC pump tripped due to failure to transfer to low speed when required by low feedwater flow. A manual reactor scram was performed. | The direct cause of the over voltage condition was a degraded transformer lightning arrester. The root cause was inadequate original design because the essential raw cooling water pump electrical circuit lacks lightning arresters to prevent an over tension condition entering the plant electrical grid. A contributing cause was the inadequate preventive maintenance. The cause of the second RCC pump trip was due to inadequate preventive maintenance. |  | 1 - For information only, breaker, bus bar, design criteria / design basis, lightening protection system , manual scram, preventive maintenance, reactor recirculation pump, transformer | CM.1 , ER.2
WER ATL 17-1090 | 2017-08-30 13:29 | Grand Gulf 1 | 2016-09-23 16:30 |  | Technical Specification Violation with Alternate Decay Heat Removal Cooling Water Valves Found Isolated | 00 | 2017-08-30 13:29 | Trending | During shutdown and while placing the alternate decay heat removal (ADHR) system in service, the ADHR heat exchanger cooling water was found isolated. This resulted in ADHR not being available as an alternate cooling system, constituting a condition prohibited by technical specifications. | The direct cause was that service water supply isolation valves for the ADHR heat exchangers were not returned to the normal open position after heat exchanger cleaning. The root causes were inconsistent reinforcement of nuclear professional behaviours in the operators and inadequate operating procedure. | SOER 2013-1 Rec 3 | 1 - For information only, configuration control, human error, isolation valve, procedure inadequacy, residual heat removal, valve misposition | CM.2 , OP.1 , OP.2
WER ATL 17-1089 | 2017-08-30 13:25 | South Texas 1 | 2017-01-14 02:15 |  | Pre-Stressed Concrete Cylinder Open Loop Auxiliary Cooling Piping Degradation | 00 | 2017-08-30 13:25 | Trending | During normal operation, a 30-inch diameter pre-stressed concrete cylinder pipe on open loop auxiliary cooling water (OLACW) supply piping was identified to be leaking. Operation decision was made to continue operation. After approximately two months, the pipe ruptured resulting in a decrease in OLACW flow. The operators performed a rapid shutdown and about 20'000 cubic meters water flooded into non-safety related protected areas. | The root cause of the leak of the pre-stressed concrete cylinder OLACW line was a latent design error during the construction phase. The operation decision making issue (ODMI) compensatory measures were less than adequate and were insufficiently challenged. More detailed cause analysis is included in the attachment. | SOER 2015-2 Rec 1 | 2 - Important lessons, leak, reactor shutdown, risk assessment, safety culture | ER.3 , OF.2 , OR.2
WER ATL 17-1088 | 2017-08-30 13:19 | Browns Ferry 2 | 2016-11-28 22:00 |  | Recirculation Pump Motor Lower Bearing Oil Level Alarm Results in Unit Being Taken Offline | 00 | 2017-08-30 13:19 | Trending | During normal operation, a recirculation pump motor lower bearing oil level alarm was received. The unit power was reduced to 19% with the generator breaker open to perform inspection and add oil to the bearing reservoir. | The cause was gradual evaporation of the oil and a lower than optimal initial oil fill. Procedure inadequacy was a contributor. |  | 1 - For information only, bearing, human error, lube oil, power reduction, procedure inadequacy, reactor recirculation pump | MA.1 , MA.2
WER ATL 17-1087 | 2017-08-30 12:58 | Cooper 1 | 2016-11-08 11:27 |  | Reactor Core Isolation Cooling Steam Leak | 00 | 2017-08-30 12:58 | Trending | During startup after an outage and while performing a surveillance test, the reactor core isolation cooling (RCIC) was tripped due to a steam leak from a air operated pressure control valve. The RCIC was declared inoperable, resulting in entry into a limiting condition of operations. | The cause was that the correct air operated valve was not purchased because material master purchase order text and associated drawing didn't detail the requirement of an open travel stop. The contributors were the failure to catch the vendor quote and vendor drawing showed the incorrect actuator travel stop. A relevant procedure and the attachment did not provide sufficient direction to set the travel stop. |  | 1 - For information only, leak, limiting condition of operation, procedure inadequacy, procurement, reactor core isolation cooling , steam, valve, valve actuator, vendor | EN.1 , ER.3
WER ATL 17-1086 | 2017-08-30 12:46 | Farley 1 | 2016-11-17 19:51 |  | Unit Shutdown Required Per Technical Specification for Two Inoperable Steam Flow Channels on One Steam Generator | 00 | 2017-08-30 12:46 | Trending | During normal operation, two steam flow transmitters on one steam generator were found outside the acceptance criteria. This resulted in entry into a limiting condition of operation (LCO). This condition resulted in engineered safety feature actuation system instrumentation function for high steam flow in two steam lines declared inoperable and consequently entry into another LCO. The reactor was shut down in accordance with the LCO. | The direct cause was inability to adjust channel card within the acceptance criteria. The root cause was inadequate procedures. The contributing cause was failure to identify risk associated with conditions of steam flow transmitters. |  | 1 - For information only, limiting condition of operation, procedure inadequacy, reactor shutdown, risk assessment | MA.2 , OF.2 , PI.2
WER ATL 17-1085 | 2017-08-30 12:41 | Millstone 3 | 2017-01-20 |  | Secondary Containment Door Failure to Close | 00 | 2017-08-30 12:41 | Trending | A fire door failed to close due to failure of the door closure mechanism and remained stuck open about 12 inches, disabling its safety function as part of the secondary containment boundary. This resulted in entry into a limiting condition of operations and a reportable event. | The direct cause was the mechanical door closer mechanism internal shaft failure. The other cause was inadequate preventive maintenance. |  | 1 - For information only, fire door, limiting condition of operation, preventive maintenance, relay, technical specification | ER.2
WER ATL 17-1084 | 2017-08-30 12:37 | Fermi 2 | 2017-02-05 13:53 |  | Trip of Heater Drain Pump Results in Unplanned Downpower | 00 | 2017-08-30 12:37 | Trending | During normal operation, a heater drain pump (HDP) tripped followed by a trip of a reactor feed pump and an automatic reactor recirculation pump runback. This resulted in reduction in reactor power to 44%. | The direct cause was a ground fault on the HDP motor. The root cause was low operational margin for loss of feedwater following a trip of a single HDP. A contributing cause was set point drift of feedwater heater level controls. |  | 1 - For information only, design criteria / design basis, feedwater control system, feedwater heater, feedwater pump, power reduction, setpoint | CM.1 , ER.2
WER ATL 17-1083 | 2017-08-30 12:29 | LaSalle 1 | 2017-02-13 23:09 |  | Main Generator Tripped In Response To Main Power Transformer Current Inrush | 00 | 2017-08-30 12:29 | Trending | During normal operation and when a 345 kV switchyard breaker was closed to backfeed the opposite unit main power transformers (MPTs), a differential current relay tripped the main generator in response to inrush current, leading to an automatic reactor scram. | The root cause was a marginal generator differential relay scheme design prone to responding to events outside its zone of protection. The contributing causes were the switchyard alignment methodology used for MPT backfeeding and recent replacement of the MPTs with larger transformers. | SER 2005-3 | 2 - Important lessons, automatic scram, configuration control, design change, design criteria / design basis, relay, turbine generator | CM.1 , CM.2 , CM.3
WER ATL 17-1082 | 2017-08-30 12:04 | LaSalle 1 | 2017-02-17 23:53 |  | Manual Scram Due to Feed Regulating Valve Failing Open | 00 | 2017-08-30 12:04 | Trending | During power ascension at 29% power, a feed regulating valve (FRV) failed open causing an abrupt increase in the reactor water level. The reactor was manually scrammed. | The root cause was inadequate design change of the FRV positioner/feedback assembly. The contributing causes were inadequate preventive maintenance and FRV cycling during operation. | SER 2005-3 | 1 - For information only, design criteria / design basis, feedwater control system, manual scram, preventive maintenance, valve | CM.3 , ER.2
WER ATL 17-1081 | 2017-08-30 11:59 | Pilgrim 1 | 2017-04-05 |  | Secondary Containment Testing Led to Loss of Safety Function to Both Trains of Standby Gas Treatment System | 00 | 2017-08-30 11:59 | Trending | During normal operation and while performing the secondary containment leak rate test, both trains of standby gas treatment system were inoperable, resulting in the loss of secondary containment integrity. This test had been performed 11 times in the past without knowing the consequence of the loss of safety function. | The root cause was that the test was moved from cold shutdown to run mode about 10 years ago. The contributors were that the provoking entry into a limiting condition of operations when the test is performed is accepted as well as the unclear technical specification surveillance requirements and out-of- date and inadequate information in the preventive maintenance database. |  | 2 - Important lessons, limiting condition of operation, preventive maintenance, standby gas treatment, technical specification | CM.2 , EN.1
WER ATL 17-1079 | 2017-08-30 11:44 | Pilgrim 1 | 2017-02-14 |  | Condenser Vacuum Degradation Due to a Seaweed Intrusion | 00 | 2017-08-30 11:44 | Trending | While operating at 89%, the main condenser vacuum started to degrade and reactor power was reduced to 44% then reduced to 30% in order to support a backwash of the main condenser. | The cause was seaweed intrusion. | SOER 2007-2 Rec 2 | 1 - For information only, condenser vacuum, debris / crud, intake, power reduction | ER.1
WER ATL 17-1077 | 2017-08-30 11:30 | Hatch 1 | 2017-04-20 03:02 |  | Momentary Intermediate Range Monitor Signal Spiking Causes Automatic Reactor Scram | 00 | 2017-08-30 11:30 | Trending | During startup with the reactor critical and while withdrawing a control rod, an automatic reactor scram occurred on momentary intermediate range monitor (IRM) high neutron flux trip signals. | The cause was degradation of IRM signal cable electro-magnetic interference (EMI) shielding. The action preventing IRM EMI from the same events in 2009 and 2011 were weakened and stopped due to process gaps. The contributing causes were inadequate risk perception associated with not performing IRM signal cable testing prior to startup and an inadequate IRM system design. |  | 1 - For information only, automatic scram, design criteria / design basis, intermediate power range monitor, risk assessment | CM.1 , OF.2 , PI.2
WER ATL 17-1076 | 2017-08-30 11:21 | Peach Bottom 3 | 2017-05-20 22:07 |  | Adjustable Speed Drive Failure on Reactor Recirculation Pump | 00 | 2017-08-30 11:21 | Trending | During operation at 44% power and while recovering from single loop operation to perform maintenance on an adjustable speed drive (ASD) of a reactor recirculation pump, the ASD tripped with indication of an arc flash in one of the ASD cells. This caused overvoltage conditions and additional arcing/damage on other cells in the drive. The unit returned to single loop operation and the reactor power was reduced to 30%. | The cause was a fault signal generated due to a spurious cell arc flash. |  | 1 - For information only, dc bus, fire, power reduction, reactor recirculation pump | ER.1
WER ATL 17-1075 | 2017-08-30 10:50 | Point Lepreau 1 | 2017-06-14 |  | Confirmed Defect Fuel Bundles since Refurbishment | 00 | 2017-08-30 10:50 | Trending | After a refurbishment in 2012, seven fuel defects was identified in the time frame between 2012 and 2014 as well as in 2016. | The cause of one fuel defect identified in 2016 was a failed upstream endcap weld that resulted in the loss of sheath material from the heat affected zone due to manufacturing deficiencies. Other defects were under evaluation. |  | 1 - For information only, debris / crud, fuel defect, vendor, weld | CM.4
WER ATL 17-1072 | 2017-08-29 15:01 | Hatch 1 | 2017-02-22 18:20 |  | Safety Relief Valve Seat Leak | 00 | 2017-08-29 15:01 | Trending | During normal operation, a safety relief valve (SRV) pilot started leaking. The unit was shut down few months after to replace the SRV pilot. | The cause was inadequate manufacturing tolerances and poor vendor workmanship. The purchase order and specifications did not include manufacturing tolerances and the dimensions were not consistently measured and recorded. |  | 1 - For information only, leak, management oversight, pilot valve, procurement, reactor shutdown, safety relief valve, vendor | ER.3 , MA.1
WER ATL 17-1071 | 2017-08-29 14:31 | Oconee 1 | 2017-02-18 00:26 |  | Reactor Coolant Pump Excessive Seal Leakage Due to Seal Face Degradation | 00 | 2017-08-29 14:31 | Trending | Two days after reaching 100% power from an outage, a reactor coolant pump (RCP) seal started to show signs of degradation from both the upper and lower seal stages in the form of seal pressures dramatically changing and increasing leakage from the upper seal stage. The unit was shutdown for more than 7 days to repair the leakage after monitoring and analysis of the leakage for several weeks . | The direct cause was improper system venting which led to a slight reverse pressurization of the seal package stripping grease off of accessible O-rings and depositing it in adverse locations within the seal package. The apparent cause was inaccurate procedure which was used for the first time after the revision in 2008. |  | 1 - For information only, FME, leak, procedure inadequacy, reactor coolant pump seal, reactor shutdown | OP.2
WER ATL 17-1069 | 2017-08-29 14:14 | Cooper 1 | 2017-03-06 21:08 |  | Main Steam Safety Relief Valve Failures | 00 | 2017-08-29 14:14 | Trending | During an outage, two main steam safety relief valves (SRVs) failed as-found lift pressure testing after being sent to an off-site testing facility. This was a technical specification violation, requiring regulatory notification. | The direct cause of one of the SRV failure was the corrosion bonding vulnerability with the valve design. The second valve failure was the valve's pilot assembly was inadvertently disassembled prior to testing. There was a lack of barriers between the valve manufacturer and the testing company to prevent the inadvertent disassembly prior to the as-found testing. |  | 2 - Important lessons, design criteria / design basis, erosion/corrosion, main steam safety valve, technical specification, vendor | CM.1 , MA.2
WER ATL 17-1068 | 2017-08-28 15:19 | Mcguire 2 | 2017-02-23 19:22 |  | Pressurizer Spray Bypass Valve Leak Discovered During Forced Outage | 00 | 2017-08-28 15:19 | Trending | During a forced outage and while a containment walk-down inspection, reactor coolant system pressure boundary leakage was observed from the body of a pressurizer spray bypass valve (PSBV). It resulted in valve replacement that extended the forced unit outage. | The apparent cause was random manufacturing defects in in a PSBV. A flaw attributed to a combination of defects during the casting process that resulted in a through wall pinhole leak in the valve body. |  | 1 - For information only, leak, outage extension , pressuriser safety valve, vendor | ER.3
WER ATL 17-1067 | 2017-08-28 15:10 | Davis Besse 1 | 2017-03-09 04:54 |  | Reactor Power Increased During Transition of Feedwater Integrated Control System to Hand | 00 | 2017-08-28 15:10 | Trending | While reducing power to 99.5% with the steam generator feedwater main valve in hand, the valve unexpectedly opened approximately 2% resulting in increased feedwater flow to a steam generator and a rise in reactor power to 101%. | The apparent cause was the lag of the valve movement due to its degraded condition. The operator was not aware of the lagging valve issue identified in 2016. |  | 1 - For information only, feedwater control system, power surge, reactivity management, valve | ER.1 , OF.2 , OP.2
WER ATL 17-1066 | 2017-08-28 15:05 | Pilgrim 1 | 2017-03-17 |  | Reactor Power Reduced for Condenser Backwash and Condenser Differential Temperatures | 00 | 2017-08-28 15:05 | Trending | During normal operation, the reactor power was reduced to 45% to carry out backwash of the main condenser. | The cause was degraded efficiency of the main condenser due to ocean debris. | SOER 2007-2 Rec 2 | 1 - For information only, condenser vacuum, debris / crud, intake, power reduction | ER.1
WER ATL 17-1065 | 2017-08-28 14:55 | River Bend 1 | 2017-03-23 03:48 |  | Loss of High Pressure Core Spray Function Due to Motor Operated Valve Malfunction | 00 | 2017-08-28 14:55 | Trending | During normal operation and while performing the high pressure core spray system (HPCS) test, the HPCS was declared inoperable due to a malfunction of a motor-operated valve (MOV) position indication. As a consequence, a limiting condition of operations was entered. | The direct cause was a loose anti-rotation collar on the valve operator caused the limit switches to lose accuracy. The apparent cause was an inadequate preventive maintenance (PM) task instruction without specifications regarding tightening torque for the set screw securing the anti-rotation collar. There was a lack of technical information from the supplier or misunderstanding of the information available. |  | 1 - For information only, containment penetration, high pressure core spray, limiting condition of operation, motor operated valve, preventive maintenance, procedure inadequacy, torque, vendor | MA.1 , MA.2
WER ATL 17-1064 | 2017-08-28 10:11 | Darlington 1 | 2017-07-26 |  | Inattention to Detail during Scaffold Removal result in Minor Hand Injury | 00 | 2017-08-28 10:11 | Trending | During operation at 92% power and while attempting to remove scaffolding material, a worker misjudged the distance and reached for the scaffold tube jamming their finger, resulting in a medically treated injury. | The cause were less than adequate situational awareness and incorrect use of existing processes to prevent human error. |  | 1 - For information only, human error, industrial safety, injury | IS.1
WER ATL 17-1062 | 2017-08-28 10:01 | South Texas 1 | 2017-03-14 15:10 |  | Technical Specification was Not Completed within 72 Hour Requirement | 00 | 2017-08-28 10:01 | Trending | During normal operation and while testing an under-voltage timing relay in a safety related switchgear, operating time of the relay was found exceeding the technical specification limits. This was a failure of one channel in a 2 out of 4 logic. The inoperable channel was not placed in the tripped condition within 72 hours as required by the technical specification. | The causes were unidentified material condition of the relay and inadequate questioning attitude by electrical maintenance and operational personnel. |  | 1 - For information only, human error, relay, technical specification | ER.1 , MA.1 , OP.1
WER ATL 17-1060 | 2017-08-28 09:46 | Nine Mile Point 1 | 2017-03-20 02:28 |  | Manual SCRAM Due to Pressure Oscillations | 00 | 2017-08-28 09:46 | Trending | While shutting down the rector for a planned outage and during a turbine overspeed test, excessive reactor pressure oscillations caused a manual reactor scram. | The apparent cause of the reactor pressure swings was that crud/debris in the mechanical pressure regulator (MPR) partially blocked the MPR pressure sensing bellows. The cause of the crud/debris buildup was inadequate preventive maintenance. Contributing causes were hysteresis in the cylinder stroke of the mechanical hydraulic control bypass relay and the turbine overspeed testing was completed at low power levels rather than higher level. |  | 1 - For information only, debris / crud, manual scram, preventive maintenance | ER.2 , OF.2
WER ATL 17-1059 | 2017-08-28 09:35 | Fitzpatrick 1 | 2017-04-04 07:35 |  | Connection of Test Equipment to Incorrect Component Resulted in Unplanned High Pressure Coolant Injection Isolation | 00 | 2017-08-28 09:35 | Trending | During normal operation and while performing tests, the high pressure coolant Injection system (HPCI) was inadvertently isolated because the test equipment was connected to the incorrect component. This resulted in isolation of one HPCI train and entry into a limiting condition of operations. | The cause was the technicians failed to stop and re-verify correct component due to not implementing required human performance error reduction tools. Another cause was not addressing technician accountability issues. |  | 1 - For information only, emergency core cooling system, human error, limiting condition of operation | LF.1 , MA.1 , MA.2
WER ATL 17-1058 | 2017-08-28 09:30 | Browns Ferry 1 | 2017-03-26 04:52 |  | Diesel Generator Building Auxiliary Equipment Room Damper Did Not Re-Open During Testing | 00 | 2017-08-28 09:30 | Trending | While performing the diesel generator building (DGB) CO2 system functional test, a 480-volt diesel auxiliary board room inlet damper did not re-open as expected, resulting in unavailability of the DGB ventilation and entry into a limiting condition of operations. | The cause was a failed damper motor due to unidentified short circuits. |  | 1 - For information only, damper, heating ventilating and air conditioning, limiting condition of operation | ER.1
WER ATL 17-1057 | 2017-08-28 09:25 | Fitzpatrick 1 | 2017-04-09 04:21 |  | Main Turbine Manually Tripped Due to High Vibration | 00 | 2017-08-28 09:25 | Trending | Following power reduction (see WER ATL 2017-1055) to support drywell entry, reactor power was at 15% when turbine vibrations on bearings 5 and 6 began rising. The turbine was manually tripped. | The cause was inadequate operating procedure allowed operation of the turbine at low power with condenser vacuum too high, causing an internal rub. |  | 1 - For information only, bearing, low pressure turbine, procedure inadequacy, turbine generator, turbine trip, vibration | OP.2
WER ATL 17-1056 | 2017-08-28 09:18 | Brunswick 1 | 2017-03-30 21:45 |  | Emergency Diesel Generator Overspeed Trip During Post-Modification Testing | 00 | 2017-08-28 09:18 | Trending | During an outage and while performing the post-modification testing for the emergency diesel generator (EDG) governor replacement, an EDG tripped on overspeed. This resulted in unplanned outage extension of approximately 66 hours. | The apparent cause was that a vendor installation information was omitted from the governing procedure and work order, resulting in a misalignment between the new governor/actuator and the engine drive assembly. The contributors were inadequate questioning attitude from the technician and the vendor-supplied governor base casting was slightly larger. | SER 2005-3 | 1 - For information only, actuator, design change, diesel generator, human error, outage extension , vendor | CM.3 , MA.1
WER ATL 17-1055 | 2017-08-28 09:11 | Fitzpatrick 1 | 2017-04-08 |  | Plant Down Power Due to Elevated Identified Drywell Leakage | 00 | 2017-08-28 09:11 | Trending | During normal operation, a downpower to 12.7% was needed to repair the increased drywell leakage from a reactor water recirculation pump discharge drain isolation valve. | The cause was the internal leakage of two closed drain valves which deteriorated over time. |  | 1 - For information only, drain valve, drywell, leak, power reduction | ER.3
WER ATL 17-1054 | 2017-08-28 09:04 | Hatch 1 | 2017-04-13 |  | Feedwater Heater Tube Damage Caused Downpower | 00 | 2017-08-28 09:04 | Trending | During power ramp up after a forced outage and while troubleshooting low discharge pressure on a heater drain pump, a feedwater heater was identified with a tube leak(s). The power was reduced from 89/% to 69% to perform inspections and repairs was required. | The direct cause was excessive vibration caused wearing of the tube and ultimately failure. The previous test did not adequately identify the wear indications in 2010 eddy current test and the frequency of EC testing was extended. |  | 1 - For information only, feedwater heater, leak, power reduction, preventive maintenance, vendor, vibration | ER.2 , ER.3
WER ATL 17-1053 | 2017-08-28 08:54 | South Texas 1 | 2017-04-12 04:15 |  | A 55 Gallon Barrel of Oil was Dropped Over Reactor Coolant Pump Motor | 00 | 2017-08-28 08:54 | Trending | During an outage, a 55 gallon drum of oil slipped from its barrel strap when workers were moving drums of oil from the operating floor in the reactor containment building to the top of the reactor coolant pump motor. It resulted in major replacement of pipe insulation that required 9 days outage extension. | The cause was negligence on the part of the qualified rigger who used the wrong barrel strap for the load. The contributor was availability of undersize barrel straps in the tool room. | SOER 2008-1 Rec 2 | 2 - Important lessons, oil, outage extension | IS.1 , MA.1
WER ATL 17-1052 | 2017-08-28 08:47 | Quad Cities 1 | 2017-04-15 13:00 |  | Main Turbine Control Valve Failed Closed | 00 | 2017-08-28 08:47 | Trending | During power ascension at about 79% power following an outage, a main turbine control valve failed closed. An unplanned power decrease to about 60% was required for troubleshooting and repair. | The cause was inadequate guidance on routing and supporting the servo valve cables. |  | 1 - For information only, electro hydraulic control, power reduction, procedure inadequacy, turbine control valve | MA.2
WER ATL 17-1051 | 2017-08-28 08:31 | Brunswick 2 | 2017-04-16 06:02 |  | Improper Packing Gland Clearances Lead to High Vibrations During Turbine Startup | 00 | 2017-08-28 08:31 | Trending | During main turbine startup after an outage, the main turbine was tripped on six separate occasions due to elevated bearing vibrations. This resulted in 72-hour outage extension. | The direct cause was improper clearances within the low pressure turbine packing glands due to incomplete maintenance guidance. The contributing cause was degradation of the system of hook fits and springs and a recommendation about condenser vacuum which affects turbine vibration was not fully implemented. |  | 1 - For information only, bearing, low pressure turbine, outage extension , procedure inadequacy, turbine generator, vibration | ER.1 , MA.2 , PI.3
WER ATL 17-1050 | 2017-08-28 08:24 | Hatch 2 | 2017-05-17 08:54 |  | Steam Jet Air Ejector Over-Adjustment Caused Degraded Main Condenser Vacuum and Down Power | 00 | 2017-08-28 08:24 | Trending | During normal operation, the in-service main condenser steam jet air ejector (SJAE) second stage pressure was over-adjusted, causing main condenser vacuum degradation. As a result, the reactor power was reduced from 100% to 85%. | The causes was human error because the operator did not take a time out when the adjustment of the controller was excessive and the governing procedure lacked sufficient detail. The other cause was that the control valve did not respond quickly as it had in the past. |  | 1 - For information only, condenser vacuum, human error, power reduction, procedure inadequacy | ER.1 , OP.1 , OP.2
WER ATL 17-1048 | 2017-08-25 10:35 | Brunswick 1 | 2017-04-17 00:04 |  | Failure of Main Generator Output Breakers to Open Results in Actuation of Emergency Diesel Generators | 00 | 2017-08-25 10:35 | Trending | During normal operation and while starting the main turbine after an outage, the main turbine was tripped due to elevated bearing vibrations and the generator output power circuit breakers (PCBs) failed to open. This caused a main generator primary lockout and the subsequent automatic actuation of all four emergency diesel generators. | The cause of the failure of the PCBs was full contact closure on a turbine stop valve closed limit switch did not occur due to foreign material (tie-wrap) inside the contact housing. The apparent cause was inadequate procedure. |  | 1 - For information only, breaker, diesel generator, FME, limit switch, procedure inadequacy, turbine stop valve, turbine trip, vibration | MA.2
WER ATL 17-1047 | 2017-08-25 10:24 | Brunswick 1 | 2017-04-19 10:35 |  | Slip and Fall Leads to OSHA-Recordable Lost Time Injury | 00 | 2017-08-25 10:24 | Trending | A worker was injured when he slipped and fell at the boat ramp used to access the site's diversion structure. He was transported to an off-site medical facility for treatment. | The direct cause was failure to maintain situational awareness and eyes on path. The contributors were not notifying his supervisor when his scope of work changed and unclear organizational interface between security technical support and the engineering cyber security project group. |  | 1 - For information only, human error, industrial safety, injury, work control | IS.1
WER ATL 17-1046 | 2017-08-25 10:03 | South Texas 2 | 2017-04-26 17:40 |  | Main Condenser Fouling Results in Down Power | 00 | 2017-08-25 10:03 | Trending | During normal operation, a failure of two intake traveling screens allowed a large amount of clam shells to enter the condenser water boxes, restricting the flow through the tubes. Consequentially, a downpower to 78% was required to clean the condenser tube fouling. | The cause was that two traveling screens could not automatically start as required on high differential level due to a level sensing instrumentation air leak. Monitoring of screen differential level was inadequate in detecting the differential level increase prior to screen failure. | SOER 2007-2 Rec 4 | 1 - For information only, condenser tube, debris / crud, instrument air, intake, leak, power reduction, travelling screen | ER.2
WER ATL 17-1041 | 2017-08-25 09:20 | Callaway 1 | 2017-05-20 03:48 |  | Main Feedwater Pump Lockout Light Not Indicating Properly | 00 | 2017-08-25 09:20 | Trending | During normal operation and while performing the main feedwater pump emergency lockout test, a main feedwater pump lockout light did not indicate properly, affecting the trip mechanism of the pump. A downpower to 58% was planned for repairs. | The cause was a blown fuse in the lockout solenoid fuse disconnect switch. |  | 1 - For information only, feedwater pump, fuse, power reduction, switch | ER.3
WER ATL 17-1040 | 2017-08-25 09:09 | Duane Arnold 1 | 2017-05-26 |  | Unplanned Downpower for Corrective Maintenance | 00 | 2017-08-25 09:09 | Trending | During normal operation, a steam leak was identified at the torque tube arm flanged joint associated with a level transmitter, resulting in a downpower to approximately 71% for approximately 12 hours. | The cause was failure of the torque tube arm gasket due to the assembly of the joint using a less than adequate torque value. |  | 1 - For information only, gasket, leak, power reduction, steam, torque | MA.1
WER ATL 17-1036 | 2017-08-23 12:48 | Hatch 2 | 2017-05-10 16:40 |  | Power Reduction Due to Rising Condensate Temperatures and Degrading Vacuum | 00 | 2017-08-23 12:48 | Trending | During normal operation and while removal from service of one of the high pressure heater, moisture separator reheater drains were not isolated from the heater while the coolant or feedwater was isolated. This resulted in the subsequent lift of the shell side relief valve and increased condenser in-leakage. Five months later the reactor power was reduced to 19%. | The apparent causes were inadequate removal from service of the feedwater heater (FWH) due to insufficient procedure guidance, flow accelerated corrosion affected piping downstream of the FWH shell side relief valve and inadequate operating procedure for injection of helium into steam jet air ejector. |  | 1 - For information only, configuration control, feedwater heater, power reduction, procedure inadequacy | CM.2
WER ATL 17-1033 | 2017-08-21 13:33 | Brunswick 2 | 2017-04-14 00:15 |  | Mode Change With Drywell and Suppression Chamber Simutaneously Aligned for Venting Results in Operation Outside Technical Specifications | 00 | 2017-08-21 13:33 | Trending | During startup operation, mode change with drywell and the suppression chamber simultaneously aligned for venting rendered the primary containment inoperable for 43 minutes. This resulted in a condition prohibited by technical specifications. | The cause was that personnel did not issue a limiting condition of operation (LCO) for tracking primary containment inoperability in preparation for plant mode change and startup. The condition was not identified during preparations for changing the plant mode. The contributing cause was technically incomplete operating procedure for the containment atmosphere control system. |  | 1 - For information only, drywell, human error, procedure inadequacy, technical specification | OP.1 , OP.2
WER ATL 17-1031 | 2017-08-21 13:30 | Wolf Creek 1 | 2017-04-25 09:11 |  | Clearance Order Resulted in Inoperability of Component Cooling Water System | 00 | 2017-08-21 13:30 | Trending | During normal operation, a work activity isolated the emergency makeup from the essential service water (ESW) system rendering a train of the component cooling water (CCW) system inoperable. This configuration resulted in a condition prohibited by technical specifications (TS). | The cause was a latent historical misinterpretation of TS requirements. Adequate information was not incorporated into the CCW bases identifying the requirement that makeup from ESW is necessary to maintain a CCW train operable. |  | 1 - For information only, configuration control, essential service water, procedure inadequacy, technical specification | OP.1 , OP.2
WER ATL 17-1030 | 2017-08-21 13:16 | Callaway 1 | 2017-04-20 17:00 |  | Reactor Coolant System Letdown Valve did not Respond as Expected | 00 | 2017-08-21 13:16 | Trending | A reactor coolant system letdown valve was returned to service from maintenance, and letdown flow exceeded the maximum allowed flow and the design based limits. | The direct cause was the design of the marriage block allowed for the threads to be stripped. The root cause was an engineering team did not recognize that design limits could be exceeded and did not consider to open the throttle valve in increments. The contributing cause was opened throttle valve. |  | 1 - For information only, chemical volume control system, design criteria / design basis, human error, throttle valve | CM.1 , EN.1
WER ATL 17-1025 | 2017-08-21 12:42 | Perry 1 | 2017-04-30 18:18 |  | Unexpected Main Turbine Bypass Valve Opening | 00 | 2017-08-21 12:42 | Trending | During normal operation, a main turbine bypass valve opened unexpectedly resulting in the power reduction to 74% to maintain the valve closed. During power reduction, the reactor protection system turbine stop valve closure and control valve fast closure trip functions were declared inoperable and loss of safety function existed for approximately 37 minutes. The main turbine was taken offline for planned repairs. | The cause of the bypass valve opening was failure of the card in the speed control circuit due to degraded transistor. The contributing cause was that the replacement of the speed control system with a digital control system was not implemented in a timely manner. |  | 1 - For information only, ageing, bypass valve, control board, electro hydraulic control, power reduction | ER.3
WER ATL 17-1024 | 2017-08-21 12:13 | Perry 1 | 2017-04-27 07:11 |  | Annulus Exhaust Gas Treatment System Recirculation Damper was not Coupled Properly | 00 | 2017-08-21 12:13 | Trending | While shifting annulus exhaust gas treatment system fan trains, a containment annulus pressure was reading low and not improving. This resulted in annulus pressure not being maintained within the required system operational band and entry into limiting condition for operation was required. | The apparent cause was a failure to adequately tighten the coupling that connects the actuator to the damper due to less than adequate procedure use and adherence by the workers. A contributing cause was less than adequate turnover/handoff between the personnel. |  | 1 - For information only, human error, limiting condition of operation, procedure adherence, procedure inadequacy | MA.1 , MA.2
WER ATL 17-1022 | 2017-08-21 12:07 | North Anna 1 | 2017-05-08 17:34 |  | Medical Evaluation Elevates Minor Injury to Lost Time | 00 | 2017-08-21 12:07 | Trending | While assisting removal of an aluminum rigging beam, a scaffold builder felt pain in his right shoulder while lifting about 35 pounds. The individual was seen by the station medical and released to be monitored as a minor injury. Subsequent evaluation by offsite medical identified damage to the shoulder that would require surgery and recordable injury. | No direct cause could be determined. No weight limit was exceeded and no policy was violated. Although this aluminum beam had been used in the past and successfully installed and removed without injury, the length of this beam required numerous people to handle the beam safely. |  | 1 - For information only, industrial safety, injury | IS.1
WER ATL 17-1018 | 2017-08-21 12:02 | Quad Cities 1 | 2017-06-05 08:15 |  | Supplemental Employee OSHA Recordable Hand Injury | 00 | 2017-08-21 12:02 | Trending | While threading a nut on a bolt for the hardened vent system tower, a metal burr detached from the bolt, punctured the glove the worker was wearing, and entered his finger. The worker was transported off-site and received medical treatment to remove the metal burr which required more than first aid. | The cause was due to a defect of the bolt. |  | 1 - For information only, industrial safety, injury | IS.1 , MA.1
WER ATL 17-1016 | 2017-08-21 11:47 | Pickering B5 | 2017-06-13 |  | Emergency Power Generator Failure to Start During Routine Test Resulted in a Partial Loss of Redundancy of the System | 00 | 2017-08-21 11:47 | Trending | During a routine black-start test attempt, an emergency power generator failed to start due to battery supply voltage low low. The event resulted in a partial (one out of three) loss of redundancy of the emergency power generator system. | The direct cause was an empty battery. The apparent causes were design change failed to prevent the problem and failure to learn from and use of internal operating experience. Lack of spare parts contributed to inability of the station to adequately respond to rapidly degrading condition of existing batteries. |  | 1 - For information only, battery, design change, diesel generator | CM.3 , OE.1
WER ATL 17-1014 | 2017-08-21 10:49 | Bruce B 7 | 2017-06-13 |  | Unit 7 Outage caused by Digital Control Computer malfunction | 00 | 2017-08-21 10:49 | Trending | During operation at 93% reactor power, the unit controlling digital control computer (DCC) stalled and caused a pressurizer high level transient. Following automatic transfer of control to another DCC, the pressurizer level did not restore to normal levels. This resulted in an automatic reactor setback to 55% power and after conservatively to take the unit offline. | The apparent cause was determined that the previous post maintenance test (PMT) performed on the DCC during the previous planned outage in 2016 was not able to detect the error. The PMT lacked detailed instructions in the control maintenance work task to identify the requirement to record a torque value or obtain a peer check when tightening screws on the DCC power supply chassis connection. |  | 1 - For information only, digital control system / digital components, preventive maintenance, reactor shutdown | MA.1 , MA.2
WER ATL 17-1012 | 2017-08-17 11:45 | Koeberg 2 | 2017-06-13 |  | Operating Control room air conditioning system temperature sensor was erroneously actuated when attempting to energise a heater during an annual heater service. | 00 | 2017-08-17 11:45 | Trending | During normal operation and while performing annual maintenance on a control room air conditioning system electric heater, another heater was erroneously actuated when attempting to energise the heater. A flow sensor was rendered inoperable due to the activation of the over temperature switch and a limiting condition of operation was declared. | The direct cause was a human error. Contributing factors were less than adequate procedure, failure to verify that the correct fan being placed in service and unauthorized plant manipulations by the maintenance personnel. |  | 1 - For information only, heating ventilating and air conditioning, human error, limiting condition of operation, procedure inadequacy | MA.1 , MA.2
WER ATL 17-1011 | 2017-08-16 12:04 | Darlington 1 | 2017-07-05 |  | Standby Generator #3 Tripped result in Reduced Redundancy Margin on Class III Power System | 00 | 2017-08-16 12:04 | Trending | During normal operation and while performing a safety related system test of a standby generator (SG), the SG tripped on high power turbine cooling air temperature. This resulted in the SG being declared unavailable and reduced redundancy of the standby power system. | The direct cause was a crack on the inner bellows of the power turbine cooling air flex line caused by cyclical temperatures and vibration. The root cause was inconsistent preventive maintenance strategy. |  | 1 - For information only, leak, power supply, preventive maintenance, vibration | ER.2
WER ATL 17-1010 | 2017-08-16 12:02 | Darlington 1 | 2017-06-18 |  | Shutdown System 2 Tripped during Maintenance Activities resulting in return of Unit to Guaranteed Shutdown State | 00 | 2017-08-16 12:02 | Trending | While conducting maintenance activities after reaching critical reactor power coming out of planned outage, shutdown system 2 tripped, resulting in an unplanned reactor shutdown and outage delay. | The root cause was inadequate risk assessment by maintenance personnel without a clear understanding of the potential consequences. Supervisor did not conduct an accurate risk assessment as required by procedure and the pre-job brief. Contributing causes were personnel did not adhere to strong maintenance fundamentals to ensure precision in executions of work activities and insufficient crew composition. |  | 1 - For information only, human error, outage extension , reactor protection system, reactor shutdown, risk assessment | MA.1
WER ATL 17-1009 | 2017-08-14 08:26 | Koeberg 2 | 2017-06-13 |  | A potential Operating Technical Specification (OTS) non-compliance event occurred as the OTS impact was not realised when a manual-auto selector push button for a Primary Circuit block valve was disconnected and replaced. | 00 | 2017-08-14 08:26 | Trending | During normal operation and while performing stroke time test for the primary circuit pilot operated relief valves (PORV) block valves, the manual-auto selector push button for a block valve did not reset back to auto after being placed in manual. The automatic and manual function of the block valve was not available when the circuit block valve was disconnected. However, the non-compliance with the technical specification was not realized. | The cause was lack of oversight by the shift supervisor and lack of questioning attitude. The risk review for emergent work was inadequate as this process was not formally stated in the work management process. | SOER 2013-1 Rec 3 | 1 - For information only, power operated relief valve, technical specification, work control | OP.1 , OP.2 , WM.1
WER ATL 17-1008 | 2017-08-14 08:11 | Bruce B 5 | 2017-05-16 |  | Unit 5 Turbine Manual Trip required due to faulty temperature transmitter | 00 | 2017-08-14 08:11 | Trending | During operation at 80% power, an increase in a turbine bearing metal temperature indication reached the shutdown limit of 115 degree C, resulting in reduction of reactor power to 55%, turbine manual trip and offline for 25 hours. | The cause was a fault of a turbine bearing metal temperature transmitter. |  | 1 - For information only, bearing, limiting condition of operation, power reduction, turbine trip | ER.1
WER ATL 17-1006 | 2017-08-09 14:12 | Cernavoda 2 | 2017-07-20 |  | Unplanned disconnection from the grid of Cernavoda Unit 2 due to generator excitation failure | 00 | 2017-08-09 14:12 | Trending | During normal operation, the turbine-generator tripped on generator excitation fault. The unit power was automatically reduced to 35% and then reactor was maintained at 60% power to prevent Xenon poisoning. Similar defects occurred twice during power increase and at 80% power a similar event resulted in power reduction to 36%. | The cause was spurious failure of electronic cards in the generator excitation panel. |  | 1 - For information only, ageing, circuit card, exciter, power reduction, turbine trip | ER.3 , PI.2
WER ATL 17-1004 | 2017-08-09 12:44 | Pickering B5 | 2017-06-27 |  | Prolonged Investigation of High Tritium Level Found in Tensioning Tower Resulted in On-going Tritium Emissions | 00 | 2017-08-09 12:44 | Trending | Airborne Tritium was first detected in the vicinity of unit 6 tensioning tower by operators. The Tritium spike was also noticed in bioassay results for various operators with a committed dose of 3 mRem. After 2 years the source of Tritium was found in the moderator room collection pit near the moderator compressor. It resulted in on-going Tritium emissions. | The direct cause was lack of dedicated and engaged resources. The root cause was low priority for the investigation. The contributor was inconsistencies in action tracking and decision making due to high turnover of team leadership. |  | 1 - For information only, airborne contamination, tritium, work control | OF.1 , OR.1 , RS.1
WER ATL 17-1003 | 2017-08-09 12:42 | Pickering A4 | 2017-06-23 |  | Replacement Dampers for Class I Power Supply Enclosure Air Conditioning Units not Seismically Qualified Resulted in Potential Operability Issue | 00 | 2017-08-09 12:42 | Trending | During normal operation, it was discovered that class one electrical equipment room ventilation damper actuators were replaced with non-seismically qualified components. This resulted in potential operability issue. | <span style="background-color: #f5f5f5;">The apparent cause was lack of seismic qualification due to inadequate design oversight.</span> |  | 1 - For information only, actuator, heating ventilating and air conditioning, seismic qualification | CM.3 , EN.1
WER ATL 17-0998 | 2017-08-09 12:17 | Bruce A 4 | 2017-06-09 |  | Reactor Inner Zone Inlet Header Temperature Causes Impairment During Reactor Power Raise | 00 | 2017-08-09 12:17 | Trending | While increasing power to 90% and testing the setbacks and stepbacks function of the reactor regulating system, a brief impairment to shutdown systems 1 and 2 occurred. Before reaching 89.8% power, the reactor inner zone inlet header (RIZIH) temperature was found approaching alarm point. Operators adjusted feeedwater flow to steam drums by placing the controllers into manual mode in order to reverse the temperature increase. The impairment alarm was resolved 20 seconds after setting the controllers back to automatic mode. | The cause was inappropriate operator actions to correct the RIZIH temperature balance. When placing controllers on manual, individuals must be able to achieve the same level of control as the controller does. The other causes were inadequate peer check and prejob brief. | SOER 2013-1 Rec 3 | 1 - For information only, human error, management oversight, reactor protection system | OP.1 , OP.2
WER ATL 17-0994 | 2017-08-09 12:05 | Koeberg 2 | 2017-06-14 |  | The unit 2 Secondary Heat Balance was reported by Engineering to be reading non conservative. A decision was thus taken to apply Operating Technical Specification and reduce power to less than 98%. | 00 | 2017-08-09 12:05 | Trending | During normal operation, a discrepancy was found between secondary heat balance (SHB) and generated electrical power. An investigation confirmed that the SHB was under reading. An operating technical specification was applied to reduce power to less than 98% to ensure that the unit is not in an overpower condition. | The cause was inadequate SHB procedure which did not account for the operation of one or two turbine driven feedwater pumps (APP). The analysis performed by engineering also neglected to account for only one APP pump in operation. |  | 1 - For information only, power reduction, procedure inadequacy, technical specification | EN.1 , EN.2

## Other
OE Reports
Event Summary Monthly by Significance (2017 August)
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 17-0365 | 2017-08-24 02:45 | Hanul 5 | 2017-05-12 |  | Air Compressor Stopped by Human Error during Operator Rounds | 00 | 2017-08-24 02:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0364 | 2017-08-24 02:43 | Hanul 3 | 2017-05-10 |  | Malfunction of Incore Instrumentation during Normal Operation | 00 | 2017-08-24 02:43 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0359 | 2017-08-24 02:05 | Shin-Kori 4 | 2017-04-20 |  | Unexpected Trip of Non-Class 1E Diesel Generator during Performance Test | 00 | 2017-08-24 02:05 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0358 | 2017-08-24 01:47 | Hanul 6 | 2017-05-18 |  | Lube Oil Leakage through Generator Seal Oil System during Main Turbine Shaft Alignment | 00 | 2017-08-24 01:47 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0357 | 2017-08-23 23:57 | Hanul 6 | 2017-04-18 |  | Fire Water Sprayed due to Mis-Operation of Deluge Valve | 00 | 2017-08-23 23:57 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0352 | 2017-08-23 19:58 | Fangjiashan 1 | 2017-03-06 |  | Air entered gas stripper of boron recycle system | 00 | 2017-08-23 19:58 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0351 | 2017-08-23 04:50 | Fangjiashan 2 | 2017-02-07 |  | High level of low-pressure heater drainage tank A resulted in isolation of 3# and 4# low-pressure heaters in train A | 00 | 2017-08-23 04:50 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0344 | 2017-08-09 02:07 | Qinshan 2 3 | 2017-06-01 |  | Abnormal damage of casing threads of some temperature detectors was found during Outage 306 of Qinshan 2. | 00 | 2017-08-09 02:07 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0341 | 2017-08-09 01:01 | Fuqing 2 | 2015-07-14 |  | When insulation of Fuqing-2 was tested with the control rod power supply system (RAM), mistake cutoff of circuit switch for bus low-frequency protection relay detection power source caused control rod drop | 00 | 2017-08-09 01:01 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0338 | 2017-08-08 06:40 | Fangjiashan 2 | 2017-02-01 |  | Resin in condensate polishing system contaminated | 00 | 2017-08-08 06:40 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0337 | 2017-08-08 05:44 | Fangjiashan 1 | 2017-04-02 |  | Grille Decontamination Machine of the Circulating Water System Got Stuck at the Bottom and Couldn’t Rise | 00 | 2017-08-08 05:44 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0334 | 2017-08-08 02:22 | Fuqing 2 | 2016-11-14 |  | Welding seams of instrument pipelines of trap in turbine hall failed radioactive ray inspection | 00 | 2017-08-08 02:22 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0332 | 2017-08-08 01:31 | Fuqing 2 | 2016-10-23 |  | Foreign materials found in secondary side of No. 1 steam generator during outage | 00 | 2017-08-08 01:31 | Other | During the hydraulic washing and video inspection of secondary side tube plate of steam generator, a rod like foreign materials was found in the external annulus of secondary hot side of steam generator. | Direct cause: The electrode used by the manufacturer was left in the pipe or equipment. Root cause: The manufacturer was not required to set the QC point in the cleanliness check. Causal factor: In the cleanliness check after welding, no left electrode was found. |  | 1 - For information only
WER TYO 17-0328 | 2017-08-07 20:39 | Fuqing 3 | 2016-10-20 |  | Foreign materials like welding electrodes and welding wires were found in the filter chamber | 00 | 2017-08-07 20:39 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0325 | 2017-08-04 03:24 | Hanbit 5 | 2017-04-19 |  | Tube Leaks in Low Pressure Feedwater Heaters 1B and 1C | 00 | 2017-08-04 03:24 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0323 | 2017-08-04 02:55 | Hanbit 5 | 2017-04-23 |  | Condenser Manway Gasket Damage | 00 | 2017-08-04 02:55 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0322 | 2017-08-04 02:45 | Shin-Kori 2 | 2017-05-02 |  | Air Reservoir Pressure Decrease due to Damaged Tubing of Air Compressor for Generator Circuit Breaker | 00 | 2017-08-04 02:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0319 | 2017-08-03 22:07 | Qinshan 1 | 2017-03-13 |  | Oil leaked from the hook connection of smoke exhaust header above #15/16 cylinder of emergency diesel generator 2# | 00 | 2017-08-03 22:07 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0317 | 2017-08-03 02:29 | Fangjiashan 2 | 2017-01-10 |  | Foreign material found on the lower core support plate in TV inspection during Fangjiashan outage 202 | 00 | 2017-08-03 02:29 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0316 | 2017-08-03 02:23 | Fangjiashan 1 | 2017-04-03 |  | Direct buried cable in wall was broken when replacing fire door | 00 | 2017-08-03 02:23 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0312 | 2017-08-02 22:46 | Qinshan 1 | 2017-05-10 |  | Misoperation Resulted in Malfunction of Foam Fire Extinguishing Device of 3# Emergency Diesel Generator (EDG) | 00 | 2017-08-02 22:46 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0311 | 2017-08-02 22:39 | Qinshan 1 | 2016-12-28 |  | Control system of stator cooling water three-way control valve (FSL-20V) was abnormal | 00 | 2017-08-02 22:39 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0309 | 2017-08-02 04:07 | Kuosheng 2 | 2017-04-06 |  | Tube Leaking in Feedwater Heaters 1A and 3B Identified and Plugged During Unit Extended Shutdown | 00 | 2017-08-02 04:07 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0308 | 2017-08-02 00:26 | Changjiang 1 | 2017-01-31 |  | Abnormal grinding of T-type temperature detector casing of Changjiang-1 | 00 | 2017-08-02 00:26 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0307 | 2017-08-02 00:15 | Changjiang 1 | 2016-10-13 |  | Water Pressure of Section I Kept Decreasing After Using New Reverse Osmosis Membrane | 00 | 2017-08-02 00:15 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0306 | 2017-08-01 21:24 | Tsuruga 1 | 2017-06-19 |  | Leakage in the concentrated liquid waste storage tank room on the 1st basement of waste treatment building | 02 | 2017-08-24 04:08 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0468 | 2017-08-28 04:27 | Olkiluoto 1 | 2016-06-16 |  | Release of noble gases into rooms of turbine building | 00 | 2017-08-28 04:27 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0466 | 2017-08-28 04:22 | Beznau 1 | 2017-05-02 |  | Findings on the reactor pressure vessel support brackets | 00 | 2017-08-28 04:22 | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER PAR 17-0464 | 2017-08-17 07:51 | Sizewell B 1 | 2017-02-21 |  | Failure to Supply Required ASME documentation in time for starting Dry Fuel Store Operations | 00 | 2017-08-17 07:51 | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER PAR 17-0463 | 2017-08-17 07:50 | Sizewell B 1 | 2017-02-18 |  | Pond Fuel Handling Machine (PFHM) traversed to in-correct cell when loading a Dry Fuel Store Storage Cask (DFSSC) | 00 | 2017-08-17 07:50 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0461 | 2017-08-17 07:49 | Sizewell B 1 | 2017-02-05 |  | Failure to Identify all Pre-Campaign Maintenance for Dry Fuel | 00 | 2017-08-17 07:49 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0454 | 2017-08-17 07:41 | Forsmark 3 | 2016-12-21 |  | Sprinkler station not ready for operation | 00 | 2017-08-17 07:41 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0453 | 2017-08-17 07:40 | Forsmark 1 | 2017-03-04 |  | Testing interval exceeded for plausibility check of measurement values in the condensation system | 00 | 2017-08-17 07:40 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0452 | 2017-08-17 07:40 | Forsmark 1 | 2017-02-23 |  | Breached fire cell boundary between the Electrical and Reactor Buildings | 00 | 2017-08-17 07:40 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0451 | 2017-08-17 07:38 | Forsmark 1 | 2016-12-25 |  | Fire alarm equipment not ready for operation | 00 | 2017-08-17 07:38 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0450 | 2017-08-17 07:37 | Forsmark 1 | 2016-11-14 |  | Fire damper interlock function not working in case of fire alarm | 00 | 2017-08-17 07:37 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0449 | 2017-08-17 07:36 | Sizewell B 1 | 2016-11-18 |  | Environmental Safety events outside of the security fence | 00 | 2017-08-17 07:36 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0448 | 2017-08-17 07:35 | Sizewell B 1 | 2017-04-25 |  | Discovery of contaminated hose in conventional waste skip | 00 | 2017-08-17 07:35 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0447 | 2017-08-17 07:28 | Sizewell B 1 | 2017-01-05 |  | Power Operated Relief Valve (PORV) Controller Loop C Work Suspended | 00 | 2017-08-17 07:28 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0442 | 2017-08-17 06:57 | Hongyanhe 3 | 2017-02-25 |  | Internal leakage of an isolation valve of the pressurizer relief lines during hydraulic test | 00 | 2017-08-17 06:57 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0440 | 2017-08-17 06:55 | Hongyanhe 1 | 2017-04-08 |  | Emergency generator sealing oil pump failed to start because of software bugs | 00 | 2017-08-17 06:55 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0439 | 2017-08-17 06:54 | Hongyanhe 3 | 2017-05-04 |  | A motor-driven feedwater pump tripped during full power operation | 00 | 2017-08-17 06:54 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 17-0180 | 2017-08-25 12:16 | Balakovo 2 | 2017-03-15 |  | Foreign Material Found at the Fuel Assembly Rim | 00 | 2017-08-25 12:16 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 17-0178 | 2017-08-22 10:39 | Bohunice 3 | 2017-06-12 |  | Actuation of the safety system caused by the signal “4 disconnected loops in Mode 3”. | 00 | 2017-08-22 10:39 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 17-0174 | 2017-08-17 00:51 | Kola 4 | 2017-04-26 |  | Unplanned Control Rod Drive Mechanism Replacement Due to Low Resistance on the Control Rod Assembly 21-40 Motor Windings | 00 | 2017-08-17 00:51 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1095 | 2017-08-31 08:42 | Bruce B 5 | 2017-07-21 |  | Lessons learned from Safety and Production Hot Particle challenges during Outages | 00 | 2017-08-31 08:42 | Other | See summary blow. | See causes below. |  | 1 - For information only
WER ATL 17-1094 | 2017-08-31 08:36 | Koeberg 2 | 2017-08-22 |  | During a reactor containment entry at power on unit 2 the Radiation Protection Monitor thought that he noticed a radwaste concrete drum on the 20m level in room R751. | 00 | 2017-08-31 08:36 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1092 | 2017-08-30 13:35 | Laguna Verde 1 | 2017-06-22 |  | Near-miss during material handling activities in the intake structure | 00 | 2017-08-30 13:35 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1078 | 2017-08-30 11:35 | Clinton 1 | 2017-05-07 22:16 |  | Unexpected Reactor Recirculation System Runback While Placing Motor Driven Reactor Feedwater Pump in Service | 00 | 2017-08-30 11:35 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1074 | 2017-08-30 10:47 | Cernavoda 2 | 2017-06-23 |  | Increased Hydrogen Concentration in Liquid Zone Control Cover Gas due to Passing Trap | 00 | 2017-08-30 10:47 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1073 | 2017-08-30 10:43 | Bruce B 6 | 2017-06-26 |  | Low Pressure Service Water copper pipe contacted during scaffolding construction | 00 | 2017-08-30 10:43 | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 17-1063 | 2017-08-28 10:10 | Darlington 4 | 2017-07-01 |  | Missed Procedure Step during sampling result in Heavy Water Spill and Radiation Incident | 00 | 2017-08-28 10:10 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1061 | 2017-08-28 09:54 | Pilgrim 1 | 2017-03-28 06:00 |  | Reactor Power Reduced to Maintain Main Condenser Differential Temperatures | 00 | 2017-08-28 09:54 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1049 | 2017-08-25 10:49 | Indian Point 3 | 2017-03-22 14:59 |  | Contaminated Equipment Removed from the Radiologically Controlled Area | 00 | 2017-08-25 10:49 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1045 | 2017-08-25 09:51 | Quad Cities 1 | 2017-05-01 12:50 |  | Station Black Out Diesel Generator Failed to Start | 00 | 2017-08-25 09:51 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1044 | 2017-08-25 09:43 | Perry 1 | 2017-05-02 04:53 |  | Reactor Recirculation Pump Failed to Downshift to Slow Speed | 00 | 2017-08-25 09:43 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1043 | 2017-08-25 09:35 | Palisades 1 | 2017-05-04 06:22 |  | Locked High Radiation Area Access Control Guard Left Entry Point Unguarded | 00 | 2017-08-25 09:35 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1039 | 2017-08-25 09:00 | Arkansas Nuclear One 1 | 2017-05-26 02:15 |  | Mechanic Felt Discomfort in Knee During Torquing Activities | 00 | 2017-08-25 09:00 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1038 | 2017-08-23 13:13 | Darlington 1 | 2017-07-06 |  | Deficiencies in Adherence to Foreign Material Exclusion Program | 00 | 2017-08-23 13:13 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1037 | 2017-08-23 13:04 | Pickering A4 | 2017-07-04 |  | Concerns over seismic qualification of equipment causing three Technical Operability Evaluations. | 00 | 2017-08-23 13:04 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1035 | 2017-08-21 13:36 | Fermi 2 | 2017-04-18 06:43 |  | Rod Movement Control Switch Intermittent Failure | 00 | 2017-08-21 13:36 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1034 | 2017-08-21 13:35 | Robinson 2 | 2017-03-22 05:00 |  | Work Performed Without a Clearance | 00 | 2017-08-21 13:35 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1032 | 2017-08-21 13:31 | Callaway 1 | 2017-04-13 17:00 |  | Control Room Annunciators Lost Due to a Blown Fuse | 00 | 2017-08-21 13:31 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1029 | 2017-08-21 13:12 | Sequoyah 1 | 2017-05-01 15:31 |  | Portable Air Compressor Fire | 00 | 2017-08-21 13:12 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1028 | 2017-08-21 13:03 | Arkansas Nuclear One 2 | 2017-04-24 16:17 |  | Unexpected Water in Heat Exchanger Identified During Replacement Causing Contamination and Outage Delays | 00 | 2017-08-21 13:03 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1027 | 2017-08-21 13:00 | South Texas 1 | 2017-05-01 02:53 |  | Pump Mini-flow Controller Misposition Results in Higher than Expected Flow | 00 | 2017-08-21 13:00 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1026 | 2017-08-21 12:43 | Browns Ferry 3 | 2017-05-05 22:38 |  | Catch Containment Issue Results in Increased Contamination Zone | 00 | 2017-08-21 12:43 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1023 | 2017-08-21 12:09 | Columbia Generating Station | 2017-04-26 10:43 |  | Unanticipated Dose Rate Alarm While Rigging Waste Container | 00 | 2017-08-21 12:09 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1021 | 2017-08-21 12:06 | Susquehanna 1 | 2017-06-05 |  | Dropped Object Near Miss | 00 | 2017-08-21 12:06 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1020 | 2017-08-21 12:05 | Catawba 1 | 2017-05-16 13:00 |  | Technicians Failed To Sign Into Work Order Clearance Prior to Performing Work | 00 | 2017-08-21 12:05 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1019 | 2017-08-21 12:04 | Peach Bottom 3 | 2017-05-25 08:08 |  | Extension Cord Failure Due to Excess Load | 00 | 2017-08-21 12:04 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1017 | 2017-08-21 11:52 | Oconee 1 | 2017-06-06 21:19 |  | Unintentional Entry into a High Radiation Area | 00 | 2017-08-21 11:52 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1015 | 2017-08-21 10:52 | Pickering B8 | 2017-07-04 |  | Startup of Emergency Seal Oil Pump During Seal Oil Fill in Seal Oil Heat Exchanger Resulted in Potential Loss of Generator Hydrogen Seal and Unit Shutdown | 00 | 2017-08-21 10:52 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1013 | 2017-08-17 11:46 | Koeberg 1 | 2017-07-17 |  | While topping up Unit 1 alternator with hydrogen, the Generator Hydrogen Supply valve (1GRV024VY) was found in the incorrect position. | 00 | 2017-08-17 11:46 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1007 | 2017-08-10 12:53 | Pickering A1 | 2017-05-29 |  | Review of Operations Human Performance Events Identified Opportunities for Improvements | 00 | 2017-08-10 12:53 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1005 | 2017-08-09 13:03 | Bruce B 5 | 2017-05-13 |  | Shutdown System 2 Poison Injection Room Door latch failure | 00 | 2017-08-09 13:03 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1002 | 2017-08-09 12:41 | Pickering A1 | 2017-06-15 |  | Recirculated Cooling Water Heat Exchanger Returned to Service with Potential Unapproved Modification Resulted in the System Impairment | 00 | 2017-08-09 12:41 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1001 | 2017-08-09 12:40 | Pickering A1 | 2017-06-12 |  | Elevated Crud in Heat Transport System Resulted in Potential for Pump Seal Failures and Delays to On-line Fuelling | 00 | 2017-08-09 12:40 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-1000 | 2017-08-09 12:39 | Pickering B8 | 2017-05-10 |  | Submergence of Boiler Blowdown Line due to High Lake Water Resulted in Water Hammer and Steam Leak in Screenhouse | 00 | 2017-08-09 12:39 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0999 | 2017-08-09 12:32 | Darlington 1 | 2017-06-13 |  | Two Channels Trip, resulting in Shutdown System 1 Reactor Trip while in Guaranteed Shutdown State | 00 | 2017-08-09 12:32 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0997 | 2017-08-09 12:14 | Bruce A 2 | 2017-06-03 |  | Instrument Air Compressor Drier Drain Hose Detaches | 00 | 2017-08-09 12:14 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0996 | 2017-08-09 12:11 | Bruce A 1 | 2017-05-26 |  | Lessons Learned From Human Machine Interface Display Power Supply Failures in Main Control Room | 00 | 2017-08-09 12:11 | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 17-0995 | 2017-08-09 12:10 | Bruce A 2 | 2017-04-05 |  | Lessons Learned from Missed Preventative Maintenance Tasks | 00 | 2017-08-09 12:10 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0993 | 2017-08-09 12:04 | Koeberg 2 | 2017-05-30 |  | Non-compliance to the Safety Related Surveillance Manual for testing of Auxiliary Feedwater System pumps in refueling outage 222. | 00 | 2017-08-09 12:04 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0992 | 2017-08-09 12:01 | Koeberg 2 | 2017-04-29 |  | Boron Injection Tank bypass valve unavailable from the control room due to the motor operated clutch forced into “in hand” condition. | 00 | 2017-08-09 12:01 | Other | See summary below. | See causes below. |  | 1 - For information only