## Сводный
Master Bill of work and labor input volume for MR-4
№: BOQ-1511-21, 22, 23, 24 Rev-0
| Department | Labor input
| RC | 52403.2165
| TC | 31425.585
| EED | 26463.058
| MS | 699.9983
| APCS | 8725.955
| TOTAL | 119717.8128
| Допобъем по ГЦНА (не согласован) | #REF!
| Допобъем по Турбине (не согласован) | #REF!

## РО
№ | Equipment description | AKZ/ ID of equipment | Type of equipment | List of scheduled works | Subdivision (company)– work executor | Ground of work | Labor input per equipment unit, m/hrs | Kspec (ensuring of RS) | К=1,15 (work in respirator) | К=1,1 to 1,5 (at the height) | К=1,15 (confined area) | К= 1,3 (work without HE m> 50 kg) 2. For valves - work as per i.2.3 OESN-81-26-11 | К=1,15 (KWU equipment) | К=1,15 (High temperature conditions) | Total labor inputs, m/hrs | OESN-2003 | Note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Department-owner:RC
1 | Reactor | YC00B001 | VVER 1000 (446В) | MR with partial refuelling,ISI | RUS AS |  | 1606.1 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 2655.0841 | 01-01-01 with note 2
[7 empty] | 1016.7 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 1680.7322 | 01-01-02-02 х 0,73
[7 empty] | 615.0123 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 1016.6922 | 01-01-02-03 х 0,63
[7 empty] | 1910.15 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 3157.7167 | 01-01-04 with note 2 х 0,99
[7 empty] | 73.8 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 122.0006 | 01-01-05-02 х 1,5
[7 empty] | 2915 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 4818.8594 | 01-01-02-01 х 0,9
[15 empty] | 13451.0852 | TOTAL Reactor
2 | Steam-generator | YB30W001 | PGV-1000M(V) | CR | RUS AS |  | 241.78 | 1.2 | 1.15 | 1.1 | 1 | 1 | 1 | 1.15 | 422.0753 | 01-06-01-02
|  |  |  | ECE of welded connection of TOT with primary headers | RUS AS |  | 2634.72 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 3635.9136 | 10-10-01-01
|  |  |  | UST of welded joints of flange part with primary headers | RUS AS |  | 333.3 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 459.954 | 10-18-03-02
|  |  |  | ECT of primary header jumpers metal | RUS AS |  | 541.78 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 747.6564 | 10-14-02
|  |  |  | ECT of heat exchanging tubes metal | RUS AS |  | 1468.558 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 2026.61 | 10-14-01
3 | Steam-generator | YB40W001 | PGV-1000M(V) | CR | RUS AS |  | 1294.3 | 1.2 | 1.15 | 1.1 | 1 | 1 | 1 | 1.15 | 2259.4595 | 01-06-01-01
|  |  |  | ECE of welded connection of TOT with primary headers | RUS AS |  | 2634.72 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 3635.9136 | 10-10-01-01
|  |  |  | UST of welded joints of flange part with primary headers | RUS AS |  | 333.3 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 459.954 | 10-18-03-02
|  |  |  | ECT of primary header jumpers metal | RUS AS |  | 541.78 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 747.6564 | 10-14-02
|  |  |  | ECT of heat exchanging tubes metal | RUS AS |  | 1468.558 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 2026.61 | 10-14-01
4 | Steam-generator | YB10W001 | PGV-1000M(V) | CR | RUS AS |  | 1294.3 | 1.2 | 1.15 | 1.1 | 1 | 1 | 1 | 1.15 | 2259.4595 | 01-06-01-01
|  |  |  | ECE of welded connection of TOT with primary headers | RUS AS |  | 2634.72 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 3635.9136 | 10-10-01-01
|  |  |  | UST of welded joints of flange part with primary headers | RUS AS |  | 333.3 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 459.954 | 10-18-03-02
|  |  |  | ECT of primary header jumpers metal | RUS AS |  | 541.78 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 747.6564 | 10-14-02
|  |  |  | ECT of heat exchanging tubes metal | RUS AS |  | 1468.558 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 2026.61 | 10-14-01
5 | Reactor coolant pump set | YD10D001 | RCPS-1391 | OR,EI,II,ISI | RUS AS |  | 2174.35 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 3594.4723 | 15-01-01-01 15-01-01-02 15-01-01-03 15-01-01-04 15-01-01-05 15-01-01-06 15-01-01-07 15-01-01-08 05-15-15-08
8 | Reactor coolant pump set | YD20D001 | RCPS-1391 | MR, CLT inspection | RUS AS |  | 1207.955 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 1917.0246 | 15-01-01-01 15-01-01-02 15-01-01-03х0,1 15-01-01-04х0,5 15-01-01-05 15-01-01-07 15-01-01-08х0,5 05-15-15-08
11 | Reactor coolant pump set | YD30D001 | RCPS-1391 | OR,EI,II,ISI | RUS AS |  | 2174.35 | 1.25 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 3594.4723 | 15-01-01-01 15-01-01-02 15-01-01-03 15-01-01-04 15-01-01-05 15-01-01-06 15-01-01-07 15-01-01-08 05-15-15-08
14 | Reactor coolant pump set | YD40D001 | RCPS-1391 | MR, CLT inspection | RUS AS |  | 1207.955 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1 | 1917.0246 | 15-01-01-01 15-01-01-02 15-01-01-03х0,1 15-01-01-04х0,5 15-01-01-05 15-01-01-07 15-01-01-08х0,5 05-15-15-08
17 | Units of tubular electric heater (PRZ TEH) 10pcs | YP10Wnn |  | Replacement | RUS AS |  | 508.5 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 701.73 | 01-04-04
18 | Emergency feedwater pump | RS42D001 | ACNA 150-90-2 | Defect removal | RUS AS |  | 60.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 60.1 | 05-06-15-02
19 | Diesel-generator | GY40D001 | 15-9DG | M-3 | RUS AS |  | 926.88 | 1 | 1 | 1 | 1 | 1 | 1 | 1.15 | 1065.912 | 08-01-01-01 08-01-02-08 ТО-2-9 ТО-2-16 ТО-3-6 ТО-3-44
| Control system |  | 38-СК016М | M | RUS AS |  | 398.55 | 1.2 | 1.15 | 1 | 1 | 1 | 1 | 1 | 549.999 | Appendix 1 to the Contract | The work is missing from the application. Maybe it was transferred to the Technical Support Contract
| TOTAL RC: | [13 empty] | 52403.2165

## ТО
№ | Equipment description | AKZ/ ID of equipment | Type of equipment | List of scheduled works | Subdivision (company)– work executor | Основание работ | Labor input per equipment unit, m/hrs | К=1,1 to 1,5 (at the height) | К=1,15 (confined area) | К= 1,3 (work as per i.2.3 OESN-81-26-11 | К=1,15 (KWU equipment) | Total labor inputs, m/hrs | OESN-2003 | Notes
1 | 2 | 3 | 4 | 5 | 6 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Department-owner: ТC
1 | Turbine set | SA, SP | К‑1000‑60/3000‑3 + ТВВ-1000-0/27TZ | Pendulum test. Alignment and crankiness measurement before repair | RUS AS |  | 622.3 | 1 | 1 | 1 | 1 | 622.3 | 03-04-15-12*0,7*4 03-04-15-13*0,7 | Pendulum testing of HPR and ER. Disassembly of TS rotors couplings. Measurement of alignment and crankiness of HPR, LPR-1,2,3, GR, ER by half-couplings at the closed cylinders before TS repair .
2 | High pressure cylinder | SA10 | К-1000‑60/3000‑3 1422367SB | CR, revealed defects removal | RUS AS |  | 360 | 1 | 1 | 1 | 1 | 360 | 03-05-16-01*2 | Repair of HPR journal, half-coupling support ridge by machining (2 journals)
[7 empty] | 150 | 1 | 1 | 1 | 1 | 150 | 03-05-16-03 | HPR support ridge repair by machining
[7 empty] | 225 | 1 | 1.05 | 1 | 1 | 236.25 | 03-04-07-09 | Repair of HPR-LPR1 half-coupling. Turbine K-1000.
[7 empty] | 129.2 | 1 | 1 | 1 | 1 | 129.2 | 03-05-15-02*0,8 | Rotors centering adjustment (2 bearings)
3 | Low pressure cylinder No.1 | SA20 | К-1000‑60/3000‑3 1422367СБ | CR, revealed defects removal | RUS AS |  | 7775 | 1 | 1 | 1 | 1 | 7775 | 03-03-01-09 | LPC-1 repair. Turbine K-1000.
[7 empty] | 240 | 1 | 1 | 1 | 1 | 240 | 03-04-07-10 | LPR1 - LPR2 half-coupling repair. Turbine K-1000.
[7 empty] | 167.9 | 1.1 | 1 | 1 | 1 | 184.69 | 03-04-12-03 | Repair of LPC-1 exhaust nozzles spraying system. Turbine K-1000.
[7 empty] | 225 | 1.1 | 1 | 1 | 1 | 247.5 | 03-05-16-02 | Repair of LPR-1 journal (one journal).
[7 empty] | 303.6 | 1.1 | 1 | 1 | 1 | 333.96 | 03-04-10-03*4 | Repair of LPC-1 vent valves (4 valves). Turbine К-1000.
[7 empty] | 614 | 1 | 1 | 1 | 1 | 614 | 03-05-06-01*2 | Repair of LPC-1 5st. diaphragm holder. Fault detection. Removal of horizontal joint defects by surface scouring (2 diaphragm holders).
[7 empty] | 120 | 1 | 1 | 1 | 1 | 120 | 03-05-07-03*2 | Repair of LPC-1 5st. diaphragm. Removal of horizontal joint defects with surface scouring (2 diaphragms)
[7 empty] | 400 | 1 | 1 | 1 | 1 | 400 | 03-05-56-01 10-21-04-07 03-05-51-01 03-05-58-03 | Repair of horizontal joint of LPC-1 inner shell (final labor input is to be defined by the fact of work performance on the shell repair)
[7 empty] | 225 | 1 | 1 | 1 | 1 | 225 | 03-04-06-04 | LPC-1 internal parts centering inspection (without defining the allowances)
[7 empty] | 393 | 1 | 1 | 1 | 1 | 393 | 03-04-06-08 | Defining allowances for centering LPC-1 holders and diaphragms
[7 empty] | 259 | 1 | 1 | 1 | 1 | 259 | 03-04-06-10 | LPC-1 assembly and disassembly for allowances determination
[7 empty] | 111.7 | 1 | 1.15 | 1 | 1 | 128.455 | 03-05-15-01 | Rotors centering adjustment. Number of movable bearings - 1
4 | Low pressure cylinder No.2 | SA30 | К-1000‑60/3000‑3 1422367SB | CR, revealed defects removal | RUS AS |  | 1440 | 1 | 1 | 1 | 1 | 1440 | 03-04-08-09 | LPC-2 opening for internal parts inspection without rotor extraction. The cylinder closing. Turbine К-1000.
[7 empty] | 240 | 1 | 1 | 1 | 1 | 240 | 03-04-07-10 | LPR2 - LPR3 coupling repair. Turbine К-1000.
[7 empty] | 167.9 | 1.1 | 1 | 1 | 1 | 184.69 | 03-04-12-03 | Repair of LPC-2 exhaust nozzles spraying system. Turbine K-1000.
[7 empty] | 225 | 1 | 1 | 1 | 1 | 225 | 03-05-16-02 | Repair of LPR-2 journal (one journal).
[7 empty] | 303.6 | 1.1 | 1 | 1 | 1 | 333.96 | 03-04-10-03*4 | Repair of LPC-2 vent valves (4 valves). Turbine К-1000.
[7 empty] | 614 | 1 | 1 | 1 | 1 | 614 | 03-05-06-01*2 | Repair of LPC-2 5st. diaphragm holder. Fault detection. Removal of horizontal joint defects by surface scouring (2 diaphragm holders).
[7 empty] | 120 | 1 | 1 | 1 | 1 | 120 | 03-05-07-03*2 | Repair of LPC-2 5st. diaphragm. Removal of horizontal joint defects with surface scouring (2 diaphragms)
[7 empty] | 400 | 1 | 1 | 1 | 1 | 400 | 03-05-56-01 10-21-04-07 03-05-51-01 03-05-58-03 | Repair of horizontal joint of LPC-1 inner shell (final labor input is to be defined by the fact of work performance on the shell repair)
[7 empty] | 46.2 | 1 | 1 | 1 | 1 | 46.2 | 03-05-08-01*0,7 | Distributor removal, mounting, cleaning, fault detection, adjustment (incomplete scope of works). At LPR-2 extraction from the cylinder.
[7 empty] | 436.8 | 1 | 1 | 1 | 1 | 436.8 | 03-05-08-02*0,7 | Diaphragm removal, mounting, cleaning, fault detection, adjustment (8 diaphragms, incomplete scope of works). At LPR-2 extraction from the cylinder.
[7 empty] | 268.8 | 1 | 1 | 1 | 1 | 268.8 | 03-04-01-06*0,7 | Hood chambers of K-1000 turbine cylinder seals (2 chambers, incomplete scope of works). At LPR-2 extraction from the cylinder.
[7 empty] | 302.4 | 1 | 1 | 1 | 1 | 302.4 | 03-05-08-03*0,7 | LPR-2 removal, mounting, cleaning, fault detection (without adjusting the internal parts location) incomplete scope of works). At LPR-2 extraction from the cylinder.
[7 empty] | 225 | 1 | 1 | 1 | 1 | 225 | 03-04-06-04 | LPC-2 internal parts centering inspection (without defining the allowances)
[7 empty] | 393 | 1 | 1 | 1 | 1 | 393 | 03-04-06-08 | Defining allowances for centering LPC-2 holders and diaphragms
[7 empty] | 259 | 1 | 1 | 1 | 1 | 259 | 03-04-06-10 | LPC-2 assembly and disassembly for allowances determination
[7 empty] | 111.7 | 1 | 1.15 | 1 | 1 | 128.455 | 03-05-15-01 | Rotors centering adjustment. Number of movable bearings - 1
5 | Low pressure cylinder No.3 | SA40 | К-1000‑60/3000‑3 1422367СБ | CR, revealed defects removal | RUS AS |  | 1440 | 1 | 1 | 1 | 1 | 1440 | 03-04-08-09 | LPC-3 opening for internal parts inspection without rotor extraction. The cylinder closing. Turbine К-1000.
[7 empty] | 240 | 1 | 1 | 1 | 1 | 240 | 03-04-07-10 | Repair of LPR3 - GR coupling. Turbine К-1000.
[7 empty] | 167.9 | 1.1 | 1 | 1 | 1 | 184.69 | 03-04-12-03 | Repair of LPC-3 exhaust nozzles spraying system. Turbine K-1000.
[7 empty] | 225 | 1 | 1 | 1 | 1 | 225 | 03-05-16-02 | Repair of LPR-3 journal (one journal).
[7 empty] | 303.6 | 1.1 | 1 | 1 | 1 | 333.96 | 03-04-10-03*4 | Repair of LPC-3 vent valve (4 valves). Turbine К-1000
[7 empty] | 614 | 1 | 1 | 1 | 1 | 614 | 03-05-06-01*2 | Repair of LPC-3 5st. diaphragm holder. Fault detection. Removal of horizontal joint defects by surface scouring (2 diaphragm holders).
[7 empty] | 120 | 1 | 1 | 1 | 1 | 120 | 03-05-07-03*2 | Repair of LPC-3 5st. diaphragm. Removal of horizontal joint defects with surface scouring (2 diaphragms)
[7 empty] | 400 | 1 | 1 | 1 | 1 | 400 | 03-05-56-01 10-21-04-07 03-05-51-01 03-05-58-03 | Repair of LPC-2 5st. diaphragm. Removal of horizontal joint defects with surface scouring (2 diaphragms)
[7 empty] | 46.2 | 1 | 1 | 1 | 1 | 46.2 | 03-05-08-01*0,7 | Distributor removal, mounting, cleaning, fault detection, adjustment (incomplete scope of works). At LPR-3 extraction from the cylinder
[7 empty] | 436.8 | 1 | 1 | 1 | 1 | 436.8 | 03-05-08-02*0,7 | Diaphragm removal, mounting, cleaning, fault detection, adjustment (8 diaphragms, incomplete scope of works). At LPR-3 extraction from the cylinder.
[7 empty] | 268.8 | 1 | 1 | 1 | 1 | 268.8 | 03-04-01-06*0,7 | Hood chambers of K-1000 turbine cylinder seals (2 chambers, incomplete scope of works). At LPR-3 extraction from the cylinder.
[7 empty] | 302.4 | 1 | 1 | 1 | 1 | 302.4 | 03-05-08-03*0,7 | LPR-3 removal, mounting, cleaning, fault detection (without adjusting the internal parts location) incomplete scope of works). At LPR-2 extraction from the cylinder.
[7 empty] | 225 | 1 | 1 | 1 | 1 | 225 | 03-04-06-04 | LPC-3 internal parts centering inspection (without defining the allowances)
[7 empty] | 393 | 1 | 1 | 1 | 1 | 393 | 03-04-06-08 | Defining allowances for centering LPC-3 holders and diaphragms
[7 empty] | 259 | 1 | 1 | 1 | 1 | 259 | 03-04-06-10 | LPC-3 assembly and disassembly for allowances determination
[7 empty] | 111.7 | 1 | 1.15 | 1 | 1 | 128.455 | 03-05-15-01 | Rotors centering adjustment. Number of movable bearings - 1
6 | Turbine set | SA, SP | К‑1000‑60/3000‑3 + ТВВ-1000-0/27Т3 | Pendulum test. Alignment and crankiness measurement after repair | RUS AS |  | 444.5 | 1 | 1 | 1 | 1 | 444.5 | 03-04-15-12*4*0,5 03-04-15-13*0,5 | Pendulum testing of HPR and ER. Final centering of HPR, LPR-1,2,3, GR, ER after TS repair (at the closed cylinders)
7 | Turbine set | SA, SP | К‑1000‑60/3000‑3 + ТВВ-1000-0/27Т3 | Vibration alignment works | RUS AS |  | 1424.6 | 1 | 1 | 1 | 1 | 1424.6 | 01-35-01-07 | Provision of vibration alignment works at TS after repair (finally, the labour input is to be determined by work performance fact)
8 | Turbine bearings No.1,2,3,4,5 | SB11 | 1422456 SB | Inspection + defects removal | RUS AS |  | 140 | 1 | 1 | 1 | 1 | 140 | 03-03-03-22 | HPC bearings repair at the closed cylinders: thrust bearing
[7 empty] | 270 | 1 | 1 | 1 | 1 | 270 | 03-03-03-23 | HPC bearings repair at the closed cylinders: support bearing
[7 empty] | 101 | 1 | 1 | 1 | 1 | 101 | 03-05-35-02 | Repair of the bearing centrifugal throwers at the closed cylinder (1 ring)
[7 empty] | 72 | 1 | 1 | 1 | 1 | 72 | 03-05-29-01 | Bearing assembly adjustment. Journal and thrust bearing
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of rotor hydrolift system for turbines K-1000-60/1500-1, К-1000-60/1500-2 k=0,15 (incomplete set)
9 |  | SB12 | 1422458 SB |  | RUS AS |  | 240 | 1 | 1 | 1 | 1 | 240 | 03-03-03-21 | Repair of HPC bearings at the closed cylinder: support bearing
[7 empty] | 101 | 1 | 1 | 1 | 1 | 101 | 03-05-35-02 | Repair of the bearing centrifugal throwers at the closed cylinder (1 ring)
[7 empty] | 58 | 1 | 1 | 1 | 1 | 58 | 03-05-29-02 | Bearing assembly adjustment (tightening, gap, rotor starting and axial position). Bearing HPR
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of rotor hydrolift system for turbines К-1000-60/1500-1, К-1000-60/1500-2 k=0,15 (incomplete set)
10 |  | SB13 | 1422458 SB |  | RUS AS |  | 240 | 1 | 1 | 1 | 1 | 240 | 03-03-03-21 | Repair of LPR-1 support bearing at the opened cylinder
[7 empty] | 67 | 1 | 1 | 1 | 1 | 67 | 03-05-35-01 | Repair of the bearing centrifugal throwers at the opened cylinder (1 ring)
[7 empty] | 60 | 1 | 1 | 1 | 1 | 60 | 03-05-29-03 | Assembly adjustment (tightening, gap, rotor starting and axial position) for HPR-1 bearing
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of rotor hydrolift system for turbines К-1000-60/1500-1, К-1000-60/1500-2 k=0,15 (incomplete set)
11 |  | SB14 | 1422458 SB |  | RUS AS |  | 240 | 1 | 1 | 1 | 1 | 240 | 03-03-03-21 | Repair of LPR-1 support bearing at the opened cylinder
[7 empty] | 67 | 1 | 1 | 1 | 1 | 67 | 03-05-35-01 | Repair of the bearing centrifugal throwers at the opened cylinder (1 ring)
[7 empty] | 60 | 1 | 1 | 1 | 1 | 60 | 03-05-29-03 | Assembly adjustment (tightening, gap, rotor starting and axial position) for HPR-1 bearing
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of rotor hydrolift system for turbines К-1000-60/1500-1, К-1000-60/1500-2 к=0,15 ((incomplete set)
12 |  | SB15 | 1422458 SB |  | RUS AS |  | 240 | 1 | 1 | 1 | 1 | 240 | 03-03-03-21 | Repair of LPR-1 support bearing at the opened cylinder
[7 empty] | 67 | 1 | 1 | 1 | 1 | 67 | 03-05-35-01 | Repair of the bearing centrifugal throwers at the opened cylinder (1 ring)
[7 empty] | 60 | 1 | 1 | 1 | 1 | 60 | 03-05-29-03 | Assembly adjustment (tightening, gap, rotor starting and axial position) for HPR-1 bearing
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of rotor hydrolift system for turbines К-1000-60/1500-1, К-1000-60/1500-2 к=0,15 ((incomplete set)
13 | BG | SB15D001 | 1309445SB | CR | RUS AS |  | 260 | 1 | 1 | 1 | 1 | 260 | 03-03-04-04 | Repair of turbine barring gears. Turbine K-1000
14 | TG and E bearings No. 6,7,8 | SQ11 |  | Inspection + defects removal | RUS AS |  | 270 | 1 | 1 | 1 | 1 | 270 | 03-03-05-19 | GR support repair without rotor removal
[7 empty] | 58 | 1 | 1 | 1 | 1 | 58 | 03-05-30-01 | Adjustment of GR bearing assembly (tightening, gap)
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of turbine K-1000 RHLS (1 support)
[7 empty] | 337 | 1 | 1 | 1 | 1 | 337 | 03-05-17-01 | GR journal repair by machining
15 |  | SQ12 |  | Inspection + defects removal | RUS AS |  | 270 | 1 | 1 | 1 | 1 | 270 | 03-03-05-19 | GR support repair without rotor withdrawal
[7 empty] | 58 | 1 | 1 | 1 | 1 | 58 | 03-05-30-01 | Adjustment of GR bearing assembly (tightening, gap)
[7 empty] | 39.6 | 1 | 1.15 | 1 | 1 | 45.54 | 03-03-14-03*0,15 | Repair of turbine K-1000 RHLS (1 support)
[7 empty] | 337 | 1 | 1 | 1 | 1 | 337 | 03-05-17-01 | GR journal repair by machining
[7 empty] | 301 | 1 | 1 | 1 | 1 | 301 | 03-05-17-03 | GR half-coupling repair by machining
16 |  | SQ13 |  | Inspection + defects removal | RUS AS |  | 102 | 1 | 1 | 1 | 1 | 102 | 03-03-05-20 | Repair of electrical unit rotors supports without ER rotor withdrawal
[7 empty] | 29 | 1 | 1 | 1 | 1 | 29 | 03-05-30-02 | Adjustment of ER bearing assembly (tightening, gap, rotor starting and axial position)
[7 empty] | 180 | 1 | 1 | 1 | 1 | 180 | 03-05-17-02 | GR journal repair
[7 empty] | 73 | 1 | 1 | 1 | 1 | 73 | 03-05-17-04 | GR half-coupling repair
17 | Low-pressure stop valve (LPSV) | SA22S010 | 1422944SB | OR | RUS AS |  | 198 | 1.1 | 1 | 1.1 | 1 | 239.58 | 03-03-07-16 | LPSV repair
| LPSV servomotor |  | 1309808 SB | OR | RUS AS |  | 100 | 1 | 1 | 1 | 1 | 100 | 03-04-21-10 | LPSV servomotor repair
18 | LPSV steam servomotor | SA22S011 | 1321064SB | OR | RUS AS |  | 100 | 1 | 1 | 1 | 1 | 100 | 03-04-21-10 | LPSV steam servomotor repair
19 | Steam servomotor hydraulic intensifier | SA22S012 | 1320072 SB | OR | RUS AS |  | 104 | 1 | 1 | 1 | 1 | 104 | 03-04-25-10 | Repair of steam servomotor intensifier
20 | Low-pressure control valve (LPCV) | SA22S020 | 1422944SB | OR | RUS AS |  | 198 | 1.1 | 1 | 1.1 | 1 | 239.58 | 03-03-07-16 | LPCV repair
| LPCV servomotor |  | 1320896 SB | OR | RUS AS |  | 100 | 1 | 1 | 1 | 1 | 100 | 03-04-21-10 | LPCV servomotor repair
21 | LPCV steam servomotor | SA22S021 | 1321064 SB | OR | RUS AS |  | 198 | 1.1 | 1 | 1.1 | 1 | 239.58 | 03-03-07-16 | LPCV steam servomotor repair
22 | Steam servomotor hydraulic actuator | SA22S022 | 1320072 SB | OR | RUS AS |  | 104 | 1 | 1 | 1 | 1 | 104 | 03-04-25-10 | Repair of steam servomotor intensifier
| TOTAL TC: | [10 empty] | 31425.585

## ОЭО
№ | Equipment description | AKZ/ ID of equipment | Type of equipment | List of scheduled works | Subdivision (company)– work executor | Labor inputs as per OESN | К=1,2 dust tightness + К=1,2 RCP-2ск. | К=1,15 RCP EM-journal bearing | К=1,15 EM of vertical version + К=1,02 RCP 750rev/min | К=1,15 (by cooling method) | Кspec=1,2 (RS ensuring) | К=1,15 (work in respirator) | К=1,1 to 1,5 (at the height) | К=1,15 (confined area) | К= 1,3 (work without HE m> 50 kg) | K=1,15 (High temperature conditions) | Total labor inputs, | №of position in standard (OESN book 81-26-…2003)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Department-owner: RC
EEMD
1 | Generator air-operated circuit-breaker | 10AQ01Q01 | VGV 27-160/20000TZ | MR | RUS AS | 528.3974 | 2.0279 | 1 | 1 | 1 | 1 | 1 | 1 | 1.15 | 1 | 1 | 1232.2676 | 07-05-01-01 with reducing coefficient. 0,613
RP&A
2 | RP&A |  | RP7A | К | RUS AS | 5200 | 1 | 1 | 1 | 1 | 1.05 | 1 | 1 | 1.05 | 1 | 1 | 5733
Rotating mechanisms
3 | Turbine-generator | 10SP10 | TBB-1000-2/27 | MR | RUS AS | 4246.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.15 | 1 | 1 | 5371.82 | 07-01-01-02
4 | Turbine-generator | 10SP10 | TBB-1000-2/27 | Search for abnormal noise source | RUS AS | 120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 120 | By experts
5 | Exciter BVD-3400-3000TZ | 10SR10 | BVD-3400-3000TZ | MR | RUS AS | 373.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 373.3 | 07-01-02-02
6 | RCPS motor | YD20D001 | DVDAZ-173/119-6-8АМ05 | CR | RUS AS | 776 | 1.44 | 1.15 | 1.15 | 1.15 | 1.2 | 1 | 1.1 | 1.05 | 1 | 1 | 2355.4884 | 26-07-02-06
7 | RCPS motor | YD40D001 | DVDAZ-173/119-6-8АМ05 | CR | RUS AS | 3386.4 | 1.44 | 1.15 | 1.15 | 1.15 | 1.2 | 1 | 1.1 | 1.05 | 1 | 1 | 10279.157 | 26-07-02-03
8 | Diesel-generator | GY40D001 | SBGD-3100-10,5-6TZ | OR | RUS AS | 950.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.05 | 1 | 1 | 998.025 | 07-01-04-01
| TOTAL EED: | [15 empty] | 26463.058

## МС
№ | Equipment description | AKZ/ equipment coding | Equipment type | List of planned works | Company – work executor | Ground of works | Labor inputs as per OESN | Кspec (RS ensuring) | К=1,15 (work in respirator) | К=1,1 to 1,5 (at height) | К=1,15 (confined area) | К= 1,3 (work without HE m> 50 kg) | К=1,15 (KWU equipment) | K=1,15 (High temperature conditions) | Total labor inputs | №of position in standard (OESN book 81-26-…2003) | Note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
MS
1 | Temperature, pressure, level and flow-rate detectors | ZSD | Metrological check 218 pcs. | CR | RUS AS | ARS | 10.69 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 699.9983 | 09-03-03-01
| Итого МС: | [13 empty] | 699.9983

## АСУТП
№ | Equipment description | AKZ/ ID of equipment | Type of equipment | List of scheduled works | Subdivision (company)– work executor | Ground of work | Labor inputs as per OESN | Kspec (ensuring of RS) | К=1,15 (work in respirator) | К=1,1 to 1,5 (at the height) | К=1,15 (confined area) | К= 1,3 (work without HE m> 50 kg) | К=1,15 (KWU equipment) | K=1,15 (High temperature conditions) | Total labor inputs | №of position in standard (OESN book 81-26-…2003) | Note
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
CPS
111 | CPS loops (206 pcs.) | CPS loops | BER loops | M | RUS AS | ARS | 704 | 1.2 | 1.15 | 1.2 | 1 | 1 | 1 | 1 | 1165.824 | 26-01-02-01-02, 26-01-02-01-21, 26-01-02-01-26, 26-01-02-11-25, 26-09-10-06
119 | Detecting units BDPN-31R installation | 11YC00X011A-B001, 11YC00X011B-B001,11YC00X011C-B001, 12YC00X012A-B001, 12YC00X012B-B001,12YC00X012C-B001, | Detecting units | M | RUS AS | CRS
120 | Detecting units BDPN-31R installation | 11YC00X011A-B001, 11YC00X011B-B001,11YC00X011C-B001, 12YC00X012A-B001, 12YC00X012B-B001,12YC00X012C-B001, | Detecting units | M | RUS AS | CRS
I&C
551 | thermal control sensors in ZA/B, ZC, ZC2, ZF, ZM2,4,5, ZM9, ZE, ZW, ZL4, ZL6, ZH.0, ZL2, ZX, ZY, ZG1, ZJ, ZU10, ZP12, ZR1.5, ZK1, ZK2, ZS1 | RA, RB, RD, RL, ZR, RM, RN, RQ, RG, SG, SH, SL, VC, VH, VN, |  | CR without metrological support (number 350pcs.) | РУСАС | ARS | 3.14 | 1.2 | 1 | 1 | 1 | 1 | 1 | 1 | 461.58 | 09-03-11-01
563 | PLR detectors in ZA/B,ZB9, ZC,ZC2 | YA,YB,YC,YD,YT,YP,TA,TU,TH,TF,TW,VE,RL,RQ,TD,TL,TS,RZ, GY,UV,UF | SAPHIRE-22М, MTK,1151DR4Е2252М3В1,URSV,DSP,F1760.1,F1762.4, | CR without metrological support (number 130pcs.) | RUS AS | ARS | 10.69 | 1.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1167.348 | 09-03-03-01
RCP THERMAL CONTROL
571 | I&C | 10YD10T017 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
572 | I&C | 10YD10T018 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
573 | I&C | 10YD10T010A | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
574 | I&C | 10YD10T010B | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
575 | I&C | 10YD10T010C | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
576 | I&C | 10YD10T011 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
577 | I&C | 10YD10T012 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
578 | I&C | 10YD10T013 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
579 | I&C | 10YD10T014 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
580 | I&C | 10YD10T015 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
581 | I&C | 10YD10T016 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
582 | I&C | 10YD10T019 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
583 | I&C | 10YD10T020 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
584 | I&C | 10YD10T021 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
585 | I&C | 10YD10T022 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-1 motor OR
586 | I&C | 10YD20T017 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
587 | I&C | 10YD20T018 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
588 | I&C | 10YD20T010A | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
589 | I&C | 10YD20T010B | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
590 | I&C | 10YD20T010C | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
591 | I&C | 10YD20T011 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
592 | I&C | 10YD20T012 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
593 | I&C | 10YD20T013 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
594 | I&C | 10YD20T014 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
595 | I&C | 10YD20T015 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
596 | I&C | 10YD20T016 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
597 | I&C | 10YD20T019 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
598 | I&C | 10YD20T020 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
599 | I&C | 10YD20T021 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
600 | I&C | 10YD20T022 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-2 motor OR
601 | I&C | 10YD30T017 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
602 | I&C | 10YD30T018 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
603 | I&C | 10YD30T010A | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
604 | I&C | 10YD30T010B | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
605 | I&C | 10YD30T010C | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
606 | I&C | 10YD30T011 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
607 | I&C | 10YD30T012 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
608 | I&C | 10YD30T013 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
609 | I&C | 10YD30T014 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
610 | I&C | 10YD30T015 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
611 | I&C | 10YD30T016 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
612 | I&C | 10YD30T019 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
613 | I&C | 10YD30T020 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
614 | I&C | 10YD30T021 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
615 | I&C | 10YD30T022 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-3 motor OR
616 | I&C | 10YD40T017 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
617 | I&C | 10YD40T018 | TSP-02-ТВ3 427.11-11 Кл.В L=100 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
618 | I&C | 10YD40T010A | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
619 | I&C | 10YD40T010B | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
620 | I&C | 10YD40T010C | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
621 | I&C | 10YD40T011 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
622 | I&C | 10YD40T012 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
623 | I&C | 10YD40T013 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
624 | I&C | 10YD40T014 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
625 | I&C | 10YD40T015 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
626 | I&C | 10YD40T016 | TSP-02-ТВ3 427.11-58 Кл.В L=34 | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
627 | I&C | 10YD40T019 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
628 | I&C | 10YD40T020 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
629 | I&C | 10YD40T021 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
630 | I&C | 10YD40T022 | TSP-02-ТВ3 427.11-64 Кл.В | CR | RUS AS | ARS | 3.14 | 1.2 | 1.15 | 1 | 1.15 | 1 | 1 | 1.15 | 5.7307 | 09-03-11-01 | Assuming RCP-4 motor OR
TURBINE SET THERMAL CONTROL
631 | I&C | 10SB11T011 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
632 | I&C | 10SB11T012 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
633 | I&C | 10SB11T021 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
634 | I&C | 10SB11T022 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
635 | I&C | 10SB11T023 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
636 | I&C | 10SB11T024 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
637 | I&C | 10SB11T025 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
638 | I&C | 10SB11T026 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
639 | I&C | 10SB11T027 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
640 | I&C | 10SB11T028 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
641 | I&C | 10SB11T029 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
642 | I&C | 10SB11T030 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
643 | I&C | 10SB11T031 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
644 | I&C | 10SB11T032 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
645 | I&C | 10SB11T033 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
646 | I&C | 10SB11T034 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
647 | I&C | 10SB11T035 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
648 | I&C | 10SB11T036 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
649 | I&C | 10SB11T037 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
650 | I&C | 10SB11T038 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
651 | I&C | 10SB11T039 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
652 | I&C | 10SB11T040 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
653 | I&C | 10SB11T041 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
654 | I&C | 10SB11T042 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
655 | I&C | 10SB11T043 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
656 | I&C | 10SB11T044 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
657 | I&C | 10SB12T011 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
658 | I&C | 10SB12T012 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
659 | I&C | 10SB13T011 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
660 | I&C | 10SB13T012 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
661 | I&C | 10SB14T011 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
662 | I&C | 10SB14T012 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
663 | I&C | 10SB15T011 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
664 | I&C | 10SB15T012 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
665 | I&C | 10SQ11T011 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
666 | I&C | 10SQ11T012 | TSP319M/Pt100/B/3/0.00391 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
667 | I&C | 10SQ12T001 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
668 | I&C | 10SQ12T002 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
669 | I&C | 10SQ12T003 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
670 | I&C | 10SQ12T004 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
671 | I&C | 10SQ13T001 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
672 | I&C | 10SQ13T002 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
673 | I&C | 10SQ13T003 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
674 | I&C | 10SQ13T004 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
675 | I&C | 10SP13T001 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
676 | I&C | 10SP13T002 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
677 | I&C | 10SP13T003 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
678 | I&C | 10SP13T004 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
679 | I&C | 10SP13T005 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
680 | I&C | 10SP13T006 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
681 | I&C | 10SP13T007 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
682 | I&C | 10SP13T008 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
683 | I&C | 10SP13T009 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
684 | I&C | 10SP13T010 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
685 | I&C | 10SP13T011 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
686 | I&C | 10SP13T012 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
687 | I&C | 10SP13T013 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
688 | I&C | 10SP13T014 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
689 | I&C | 10SP13T015 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
690 | I&C | 10SP13T016 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
691 | I&C | 10SP13T017 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
692 | I&C | 10SP13T018 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
693 | I&C | 10SP13T019 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
694 | I&C | 10SP13T020 | TSP 9203-29-100П | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
695 | I&C | 10SP15T001 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
696 | I&C | 10SP15T002 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
697 | I&C | 10SP15T003 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
698 | I&C | 10SP15T004 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
699 | I&C | 10SP15T005 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
700 | I&C | 10SP15T006 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
701 | I&C | 10SP15T007 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
702 | I&C | 10SP15T008 | TSP100 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
703 | I&C | 10SR30T001 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
704 | I&C | 10SR30T002 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
705 | I&C | 10SR30T003 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
706 | I&C | 10SR30T004 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
707 | I&C | 10SR30T005 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
708 | I&C | 10SR30T006 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
709 | I&C | 10SR30T007 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
710 | I&C | 10SR30T008 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
711 | I&C | 10SR30T101 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
712 | I&C | 10SR30T102 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
713 | I&C | 10SR30T103 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
714 | I&C | 10SR30T104 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
715 | I&C | 10SR30T105 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
716 | I&C | 10SR30T106 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
717 | I&C | 10SR30T107 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
718 | I&C | 10SR30T108 | TSP9203-29 100П-A3 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
719 | I&C | 10SA20T001 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
720 | I&C | 10SA20T002 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
721 | I&C | 10SA20T003 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
722 | I&C | 10SA20T004 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
723 | I&C | 10SA30T001 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
724 | I&C | 10SA30T002 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
725 | I&C | 10SA30T003 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
726 | I&C | 10SA30T004 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
727 | I&C | 10SA40T001 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
728 | I&C | 10SA40T002 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
729 | I&C | 10SA40T003 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
730 | I&C | 10SA40T004 | TSP-1088. 081-77 Кл.В L=200 | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
731 | I&C | 10SA10T001 | ТХА 2088 L=1000 гз | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
732 | I&C | 10SA10T002 | ТХА 2088 L=630 гз | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
733 | I&C | 10SA10T003 | ТХА 2088 L=630 гз | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
734 | I&C | 10SA10T004 | ТХА 2088 L=630 гз | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
735 | I&C | 10SA10T005 | ТХА 2088 L=630 гз | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
736 | I&C | 10SA10T011 | ТХА 2188 L=1000 of surface | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
737 | I&C | 10SA10T012 | ТХА 2188 L=1000 of surface | CR | RUS AS | ARS | 3.14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.14 | 09-03-11-01
MECHANICAL QUANTITIES
825 | I&C | 10SA10V008 | DVT-82-В-20 | CR | RUS AS | ARS | 9.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10.9 | 09-09-23-01
826 | I&C | 10SA40V008 | DVT-82-В-20 | CR | RUS AS | ARS | 9.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10.9 | 09-09-23-01
827 | I&C | 10SB11S001 | DVT-30+К22 | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
828 | I&C | 10SB11S002 | DVT-30+К22 | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
829 | I&C | 10SB11S003 | DVT-30+К22 | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
830 | I&C | 10SB11S003P01 | DVT-30+ИП36+БИ2 | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
831 | I&C | 10SB11V004 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
832 | I&C | 10SB11V005 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
833 | I&C | 10SB11V006 | DVT-20+ИП34 | CR | RUS AS | ARS | 35.99 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35.99 | 09-09-16-01
834 | I&C | 10SB11V016 | DVT-20+ИП34 | CR | RUS AS | ARS | 35.99 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35.99 | 09-09-16-01
835 | I&C | 10SB11V026 | DVT-20+ИП34 | CR | RUS AS | ARS | 35.99 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35.99 | 09-09-16-01
836 | I&C | 10SB12V004 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
837 | I&C | 10SB12V005 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
838 | I&C | 10SB12V007 | DVT-60.30+ИП34 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
839 | I&C | 10SB12V011 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
840 | I&C | 10SB12V012 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
841 | I&C | 10SB13V004 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
842 | I&C | 10SB13V005 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
843 | I&C | 10SB13V007 | DVT-40.20+ИП42 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
844 | I&C | 10SB13V011 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
845 | I&C | 10SB13V012 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
846 | I&C | 10SB14V004 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
847 | I&C | 10SB14V005 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
848 | I&C | 10SB14V007 | DVT-40.30+ИП42 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
849 | I&C | 10SB14V011 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
850 | I&C | 10SB14V012 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
851 | I&C | 10SB15V004 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
852 | I&C | 10SB15V005 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
853 | I&C | 10SB15V008 | DVT-40.30+ИП42 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
854 | I&C | 10SB15V011 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
855 | I&C | 10SB15V012 | DVT-10.160.7+ИП37 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
856 | I&C | 10SJ51V055 | DVT-20+К21 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
857 | I&C | 10SJ51V056 | DVT-20+К21 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
858 | I&C | 10SQ11V004 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
859 | I&C | 10SQ11V005 | DVT-10.160.7 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
860 | I&C | 10SQ11V011 | DVT-40.30+ИП42 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
861 | I&C | 10SQ11V012 | DVT-40.30+ИП42 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
862 | I&C | 10SB11V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
863 | I&C | 10SB11V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
864 | I&C | 10SB11V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
865 | I&C | 10SB12V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
866 | I&C | 10SB12V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
867 | I&C | 10SB12V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
868 | I&C | 10SB13V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
869 | I&C | 10SB13V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
870 | I&C | 10SB13V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
871 | I&C | 10SB14V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
872 | I&C | 10SB14V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
873 | I&C | 10SB14V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
874 | I&C | 10SB15V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
875 | I&C | 10SB15V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
876 | I&C | 10SB15V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
877 | I&C | 10SQ11V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
878 | I&C | 10SQ11V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
879 | I&C | 10SQ11V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
880 | I&C | 10SQ12V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
881 | I&C | 10SQ12V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
882 | I&C | 10SQ12V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
883 | I&C | 10SQ13V001 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
884 | I&C | 10SQ13V002 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
885 | I&C | 10SQ13V003 | DPE-23МВ-25 | CR | RUS AS | ARS | 23.47 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23.47 | 09-09-17-01
886 | I&C | 10SB11S004 | (A5S09 T048-5M) Brown | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
887 | I&C | 10SB11S005 | (A5S09 T048-5M) Brown | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
888 | I&C | 10SB11S006 | (A5S09 T048-5M) Brown | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
889 | I&C | 10SB11S007 | (A5S09 T048-5M) Brown | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
890 | I&C | 10SB11S008 | (A5S09 T048-5M) Brown | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
906 | I&C | 10SB11S009 | (A5S09 T048-5M) Brown | CR | RUS AS | ARS | 37.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37.75 | 09-09-15-01
IBN
907 | I&C |  | IBN-7, IBN-8, IBN-9 16 pcs. | ТО | RUS AS | ARS | 650 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 650 | By experts
ARS&RC
959 | Electric-driven valves -drive control circuits |  | ARS&RC | ТР (60 pcs.) | RUS AS | ARS | 18.78 | 1.2 | 1 | 1.1 | 1 | 1 | 1 | 1.1 | 1636.1136 | 09-04-01-02, 09-04-02-02, 09-04-03-02, 09-04-06-02=18,78
970 | Low pressure stop valve with servomotor | SA22S010 | ARS&RC | CR | RUS AS | ARS | 18.78 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18.78 | 09-04-01-02, 09-04-02-02, 09-04-03-02, 09-04-06-02=18,78
971 | Low pressure control valve with servomotor | SA22S020 | ARS&RC | CR | RUS AS | ARS | 18.78 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18.78 | 09-04-01-02, 09-04-02-02, 09-04-03-02, 09-04-06-02=18,78
MCDS
306 | ICIS software adjustment and introduction of necessary compensation factors in data base of CCUL, CAS, ICIS and MCDS equipment for PU work with the 5-th fuel cycle | 10JQB10, 10JQB20, 10JQB30 | ICIS | ТО | ZAO "FTTS" A.I. Kovel | ARS | 600 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 600 | By experts. Based on review of labor input for similar works performed during CR-2018
307 | Conduct of calibration test introducing necessary compensation factors in ICIS upper level | 10JQB10, 10JQB20, 10JQB30 | ICIS | ТО | ZAO "FTTS" A.I. Kovel | ARS | 600 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 600 | By experts. Based on review of labor input for similar works performed during CR-2018
| TOTAL APCS: | [13 empty] | 8725.955