## Sheet1
Type |  |  |  | Smart Differential Pressure Transmitter | Smart Pressure Sensor | Pressure Gauges | Differential Pressure Gauges | Rod Type Pressure Transmitter | Smart Temperature Sensor | Temperature Sensor (Resistance Thermocouple) | Thermoelectric Converter | Bimetallic Thermometer
Design |  |  |  | ТЖИУ406ДД-М100-АС | ТЖИУ406ДИ-М100-АС, ТЖИУ406ДА-М100-АС, ТЖИУ406ДИВ-М100-АС | МП3-У, МП4-У, МТИ | ДСП-УС | АИР-20А/М2/ДГ/530 | ТПУ 0304/-/М2-Н , ТПУ 0304/-/М2-СВ | ТС-1388/1, СБ210/СП-02 | КТК-01(ХА)с ИСХ | ТБ, ТБ-2, ТБ-2Р
Actual |  |  |  | DPT-DPz | PT-DPz | PG | DPG | PT-NSG, PT-NPz | RTD-PT100 | RTD-PT50 RTD-2PT100 | TC-K-01 | TG
Function |  |  |  | used for differential pressure control, e.g. om filters or pumps, volumetric or mass flow measurement and level measurement | Pressure Measurement | Pressure Measurement | Pressure Measurement | Pressure Measurement | Temperature Measurement | Temperature Measurement | Temperature Measurement | Temperature Measurement
1 | Safety class as per OPB-88-97 | design |  | 2, 3, 4 | 2, 3, 4 | 2, 3, 4 | 4 | 4 | 3, 4 | 2, 3, 4 | 2, 3, 4 | 2, 3, 4
|  | actual | accomplished1 | 4 | 4 | 4 | NS2 | NS | 4 | 4 | NS | 4
|  |  | executable3 | 2, 3 | 2, 3 | 2, 3 | 4 | 4 | 3 | 2, 3 | 2, 3, 4 | 2, 3
2 | Climatic version and category of placement GOST 15150-69 | design |  | Т / T; 2, 3 | Т / T; 3 / UHL ; 3 | Т / T; 3 / UHL ; 3 | Т / T; 3 | Т / T; 2 | Т / T; 3 | Т / T; 3 | Т / T; 3 | Т / T; 3
|  | actual | accomplished | TNP4 | TNP | TNP | NS | NS | TNP | TNP | NS | TNP
|  |  | executable | T; 1, 2, 3 | T; 1, 2, 3 | T; 2, 3 | T; 2, 3 | T; 2, 3 | T; 1, 2, 3 | T; 1, 2, 3 | T; 1, 2, 3 | T; 2, 3
3 | Resistance to mold fungi in accordance with GOST 9.048-89 | design |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | actual | accomplished | TNP | TNP | TNP | NS | NS | TNP | TNP | NS | TNP
|  |  | executable | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
4 | Operating conditions in premises according to SP AS-03 | design |  | II, III | II, III | II, III | II, III | II, III | III | I, II, III | I, II, III | II, III
|  | actual | accomplished | III | III | III | NS | NS | III | III | NS | III
|  |  | executable | II | II | II | II, III | II, III | III | I, II | I, II, III | II
5 | Operable when exposed to radiation | design |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | actual | accomplished | TNP | TNP | TNP | NS | NS | TNP | TNP | NS | TNP
|  |  | executable | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
6 | NPP usage reference | design |  | At least 5 years | At least 5 years | At least 5 years | At least 5 years | At least 5 years | At least 5 years | At least 5 years | At least 5 years | At least 5 years
|  | actual |  | 12 months | 20 months | 12 months | NS | NS | 0 month | 0 month (RTD-PT50) 12 months (RTD-2PT100) | NS | 10 months
7 | Seismic stability category as per NP-031 | design |  | I, II, III | I, II, III | I, II, III | I, II, III | I, II, III | I, II, III | II, III | --- | I, II, III
|  | actual | accomplished | III | III | III | NS | NS | III | III | --- | III
|  |  | executable | I, II | I, II | I, II | I, II, III | I, II, III | I, II | II | --- | I, II
8 | Equipment group as per PNAE G-7-008-89 | design |  | B, C | B, C | B, C | --- | --- | --- | B, C | --- | ---
|  | actual | accomplished | TNP | TNP | TNP | --- | --- | --- | TNP | --- | ---
|  |  | executable | B, C | B, C | B, C | --- | --- | --- | B, C | --- | ---
9 | Output Signal | design |  | 4-20 mA | 4-20 mA | --- | --- | 4-20 mA | 4-20 mA | --- | --- | ---
|  | actual |  | 4-20 mA | 4-20 mA | --- | --- | NS | 4-20 mA | --- | --- | ---
10 | Output settling time | design |  | 0.2-0.5 s | 0.2-0.5 s | --- | --- | --- | 30 s | --- | --- | ---
|  | actual |  | 0.12 s | 0.12 s | --- | --- | --- |  | --- | --- | ---
11 | Connecting thread | design |  | --- | --- | --- | --- | --- | M20×1.5 | M20×1.5 | M20×1.5 | M27×2
|  | actual | accomplished | --- | --- | --- | --- | --- | M20×1.5 | M20×1.5 | NS | M20×1.5 M18×1.5
|  |  | executable | --- | --- | --- | --- | --- | M20×1.5 | M20×1.5 | M20×1.5 | M27×2
12 | Mounting part length, mm | design |  | --- | --- | --- | --- | --- | 60, 80, 100, 120, 160, 200, 250, 320, 400, 500, 630 | 60, 80, 100, 120, 160, 200, 250, 320, 400, 500, 630 | 60, 80, 100, 120, 160, 200, 250, 320, 400, 500, 630, 800, 1000, 1250, 1600, 2000, 2500 | 80, 100, 125, 160, 200, 250, 315
|  | actual | accomplished | --- | --- | --- | --- | --- | 80 | 80, 160, 200, 320, 400 | NS | 100, 125, 160
|  |  | executable | --- | --- | --- | --- | --- | 60, 80, 100, 120, 160, 200, 250, 320, 400, 500, 630 | 60, 80, 100, 120, 160, 200, 250, 320, 400, 500, 630 | 60, 80, 100, 120, 160, 200, 250, 320, 400, 500, 630, 800, 1000, 1250, 1600, 2000, 2500 | 80, 100, 125, 160, 200, 250, 315
13 | The presence of a protective sleeve | design |  | --- | --- | --- | --- | --- | --- | --- | --- | ---
|  | actual |  | --- | --- | --- | --- | --- | Yes | Yes | Yes | Yes
14 | Measurement range | design |  | from 0,06 kPa to 16 MPa | from 0,06 kPa to 25 MPa | from 0 to 10, 100, 160, 250, 400 kPa, from 0 to 1, 1,6, 2,5, 4, 6, 10, 16, 25, 40 Mpa | from 0 - 100 kPa to 0 - 25 MPa | from 0 to 16, 250, 400, 600 kPa, from 0 to 1, 1,6, 2,5, 4, 6, 10, 16, 25, 40 MPa | from -50 °С to +400 °С | from -50 °С to +400 °С | from -50 °С to +400 °С | from -50 °С to +500 °С
|  | actual | accomplished | 0-1 kPa 0-10 MPa | 0-1 kPa 0-25 MPa | 2.5-60 kPa 0-160 MPa | NS | NS | 0-100 °С | 0-400 °С | NS | -30~200 °С
|  |  | executable | from 0,06 kPa to 16 MPa | from 0,06 kPa to 25 MPa | from 0 to 10, 100, 160, 250, 400 kPa, from 0 to 1, 1,6, 2,5, 4, 6, 10, 16, 25, 40 Mpa | from 0 - 100 kPa to 0 - 25 MPa | from 0 to 16, 250, 400, 600 kPa, from 0 to 1, 1,6, 2,5, 4, 6, 10, 16, 25, 40 MPa | from -30 °С to +400 °С | from -30 °С to +400 °С | from -30 °С to +400 °С | from -50 °С to +500 °С
15 | Measurement errors range | design |  | ±0,5%; ±0,25% for EP-CSSI | ±0,5%; ±0,25% for EP-CSSI | ±1,5% | ±0,5%; ±0,25% for EP-CSSI | ±0,5%; ±0,25% for EP-CSSI | +/-1%, for signaling +/-1,5% | ± (0,3 +0,005х¦t¦) °С for the range from -50 °С to +400 °С ± 0,2 °С for ACS | ± 2,5 °С for the range from -50 °С to +400 °С; ± 0,5% for EP-CSSI | ±1,5%
|  | actual | accomplished | ±0.075~±0.15% | ±0.075~±0.15% | ±1% | NS | NS | Class A | Class A | NS | ±1%
|  |  | executable | ±0.075~±0.15% | ±0.075~±0.15% | ±1% | ±0.5% | ±0.25% | Class A | Class A | Class 1 | ±1%
16 | Weight | design |  | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement | Compliance with analogues specified in the design requirement
|  | actual | accomplished | Yes | Yes | Yes | NS | NS | No | No | NS | No
|  |  | executable | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
17 | One-side maitenance | design |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | actual |  | Yes | Yes | Yes | NS | NS | Yes | Yes | NS | Yes
18 | IP rating | design |  | IP67 | IP67 | IP54, IP55 | IP55 | IP54, IP65 | IP54, IP65 | IP54, IP65, IP68 | --- | IP54, IP65
|  | actual | accomplished | IP68 | IP68 | IP65 | NS | NS | IP67 | IP67 | NS | IP65
|  |  | executable | IP68 | IP68 | IP65 | IP65 | IP65 | IP67 | IP68 | IP67 | IP65
19 | Performance under ambient conditions specified in ITR 40.BU2.0120.0.0.AK.EZ0001.B01 table 1 section BU2-EEZ00295 | design |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | actual | accomplished | TNP | TNP | TNP | NS | NS | TNP | TNP | NS | TNP
|  |  | executable | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
206 | Performance under ambient conditions specified in ITT 40.BU2.0120.0.0.AK.EZ0001.B01 table 1 section BU2-EEZ0029 | design |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | actual | accomplished
executable
NOTES:
1 Accomplished features for manufactured sensors and instruments (delivered to BNPP)
2 NS = Not Supplied
3 Features which can be executed and applied on the sensors to be manufactured (for BNPP applications)
4 TNP = Test Not Performed
5 Fields are completed according to Table 1, section BU2-EEZ0178 of ITR BU2.0120.0.0.AK.EZ0001.B01
6 Difference between rows 19 and 20 is not clear. So row 20 is not completed.
𝜏_0.9=1.02 𝑚
𝜏_0.5=19.6 𝑆