4. MAINTENANCE

4.1. Organization and functions

4.1.1. Functions and responsibilities

How are organizational structure, responsibilities, levels of authority and functions defined and communicated within the maintenance organization? Are they understood by personnel [SSR-2/2 Requirement 1; 3.2(b)(d), Requirement 2; 3.5, Requirement 3; 3.8, 3.9] [NS-G-2.4; 2.11] [NS-G-2.6; 3.8, 3.9, 4.11]

How are the goals, objectives and safety indicators related to maintenance developed and managed? How are outcomes checked and measured within the organization? [SSR-2/2 Requirement 9; 4.33-4.37] [NS-G-2.6; 2.7, 2.8, 3.3, 4.4,]

How are maintenance policies and programmes kept up-to-date? What internal process is put in place in this regard? [SSR-2/2 Requirement 31] [NS-G-2.4; 6.2, 6.3, 6.5-6.7, 6.36] [NS-G-2.6; 2.7, 3.1, 3.3] [NS-G-2.11; 7.2]

4.1.2. Personnel

What is the staffing level, including the use of contractors, in the maintenance area? How does the plant ensure that there is enough manpower to cover outage and operation workloads? [SSR-2/2 Requirement 4; 3.10, 3.11] [NS-G-2.6; 3.7, 4.6, 4.11, 4.12, 4.15] [GS-G-3.1; 4.1]

How are maintenance staff, including contractors, qualified for their assigned work? What measures have been taken to maintain adequate levels of experience, knowledge and proficiency? [SSR-2/2 Requirement 4; 3.10, Requirement 7; 4.16, 4.20, 4.21] [NS-G-2.6; 4.30-4.38] [NS-G-2.4; 7.18] [NS-G-2.8; 5.22-5.26, 5.30] [GS-G-3.1; 4.6, 4.17-4.19]

4.2. Maintenance facilities and equipment

How are maintenance facilities promoting safe and efficient completion of works? How does the plant establish that there are enough facilities for all maintenance work? [NS-G-2.6; 8.6-8.20] [NS-G-2.4; 7.19] [NS-G-2.7; 3.56]

What training facilities and mock-ups are available for major activities? [SSR-2/2 Requirement 7; 4.21, 4.24] [NS-G-2.6; 8.15] [NS-G-2.7; 5.4, 5.6]

How are tools and equipment maintained and controlled? Is the quantity of consumable supplies adequate and available when needed? Is there any history of extending the maintenance window for a safety related plant system - that has been taken out of operation - owing to lack of spare parts? [SSR-2/2 Requirement 31; 8.15, 8.16] [NS-G-2.6; 4.26, 8.19, 9.41-9.44, 10.21-10.23] [GS-G-3.5; 5.157, 5.160]

How is measurement and testing equipment calibrated and controlled to ensure accuracy and traceability? [NS-G-2.6; 9.41-9.44] [GS-G-3.1; 5.34] [GS-G-3.5; 5.29] [NS-G-2.4; 7.20]

How are decontamination facilities and remote controlled tools used to minimize radiation doses? [NS-G-2.6; 8.12-8.14, 8.16, 8.20] [NS-G-2.7; 3.11-3.13]

4.3. Maintenance programmes

How are different types of maintenance (preventive, corrective, predictive, etc.) balanced to optimize the maintenance programme? [SSR-2/2 Requirement 31; 8.1] [NS-G-2.6; 2.6, 5.36, 5.37, 8.2]

4.3.1. Preventive maintenance programme

How are the scope and frequencies of preventive maintenance activities determined? How does the plant ensure the completeness of the programme? [SSR-2/2 Requirement 31; 8.5] [NS-G-2.6; 4.5, 8.4]

How are preventive maintenance activities managed and controlled to ensure timely completion? [SSR-2/2 Requirement 31; 8.8] [NS-G-2.6; 2.3]

How is the effectiveness of the preventive maintenance programme evaluated in terms of improving equipment reliability and availability? [SSR-2/2 Requirement 3; 3.2(e)] [NS-G-2.6; 5.34, 5.36]

How is identified equipment degradation managed and corrected? How are priorities established for repairing degraded equipment? [SSR-2/2 Requirement 31; 8.12] [NS-G-2.6; 4.11] [NS-G-2.12; 4.11, 4.22, 4.26, 4.27]

What kinds of predictive maintenance techniques are used? How are new, proven practices incorporated? How are these inputs used for revising the maintenance programme? [SSR-2/2 Requirement 31; 8.5] [NS-G-2.6; 2.3, 2.7, 5.37]

How are risk assessment results used to determine maintenance and inspection requirements? [NS-G-2.12; 4.16]

4.3.2. Corrective maintenance

What process is in place to effectively identify deficiencies? [SSR-2/2 Requirement 31; 8.12] [NS-G-2.6; 8.46] [GS-G-3.1; 6.59-6.62] [NS-G-2.14; 4.34-4.42]

What are the objectives for uncompleted work (maintenance backlog) and how is the latter controlled? What is the current status, and how is its cumulative impact on plant safety assessed and communicated? [SSR-2/2 Requirement 31; 8.12-8.14] [NS-G-2.6; 5.19]

How is the effectiveness of the corrective maintenance programme reviewed? How are improvements made in response to review results? [SSR-2/2 Requirement 31; 8.14] [NS-G-2.6; 5.33, 5.34, 5.36-5.38]

4.3.3. Ageing management

How is equipment degradation identified? What process is in place for this purpose? [SSR-2/2 Requirement 14; 4.50, 4.51] [NS-G-2.12; 4.11, 4.22, 4.23, 4.29, 4.31, 4.32] [NS-G-2.6; 2.12, 7.8, 9.37]

How is information on components susceptible to age-related failures processed and used? [SSR-2/2 Requirement 14; 4.50, 4.51] [NS-G-2.6; 6.12, 9.20] [NS-G-2.12; 4.14-4.17]

How is monitoring of ageing undertaken, and how are corrective actions taken for different inspection results? [SSR-2/2 Requirement 14; 4.50, 4.51] [NS-G-2.12; 4.22-4.45]

4.3.4. In-service inspection

How does the plant ensure that in-service inspection (ISI) inspectors are qualified and knowledgeable of specific ISI techniques? [SSR-2/2 Requirement 4; 3.11] [NS-G-2.4; 7.23] [NS-G-2.6; 10.24-10.34]

How are ISI results being reviewed and analysed in the plant? How are corrective actions being taken? What actions does the plant take based on the output from its reviews of in-service inspections? [SSR-2/2 Requirement 31; 8.4] [NS-G-2.6; 6.7-6.9]

4.4. Procedures, records and maintenance history

How are historical records and files periodically reviewed and analysed to identify the root causes of problems? How are these results used to improve maintenance performance? [SSR-2/2 Requirement 15; 4.52] [SSR-2/2 Requirement 31; 8.4] [NS-G-2.6; 3.3, 6.12, 6.13]

What process is in place to trend safety performance and to analyse the causes of adverse trends in the maintenance area? [SSR-2/2 Requirement 31, 8.4, 8.6] [NS-G-2.11; 6.4, 6.5]

4.5. Conduct of maintenance work

How is maintenance work properly authorized, controlled and documented? [SSR-2/2 Requirement 31; 8.8-8.10] [NS-G-2.6; 4.23, 5.1-5.19, 5.23-5.32] [GS-G-3.1; 2.21]

How is the safety of personnel and equipment ensured when conducting maintenance field activities? [SSR-2/2 Requirement 31; 8.8, 8.9] [NS-G-2.6; 5.15-5.17]

How does the plant guarantee that adequate resources are made available for maintenance activities? Are there any examples of cases where a lack of resources caused unnecessary delays in the completion of maintenance activities? If so, which examples best illustrate this? [SSR-2/2 Requirement 31; 8.12, 8.14, 8.20] [GS-G-3.1; 4.1, 4.2] [NS-G-2.6; 3.7, 4.11, 4.12, 4.15, 5.23, 5.36, 5.37]

How is it confirmed that procedures are followed in the field as prescribed by plant requirements? [SSR-2/2 Requirement 31] [NS-G-2.6; 3.8, 3.9, 5.6, 5.14]

What schemes are in place for monitoring plant conditions, activities and personnel attitudes through systematic walkdowns by managers? How are deviations managed? [SSR-2/2 Requirement 9; 4.35, 4.37] [GS-G-3.5; 6.3]

How are human performance tools used in the field? How are aspects of the working environment, that are impacting human performance, identified and controlled? [SSR-2/2 Requirement 8; 4.28, 4.29, Requirement 31; 8.9] [NS-G-2.6; 2.11, 4.30, 5.36]

How are managers and supervisors effectively coaching and observing field workers to reinforce correct behaviours and plant expectations? [SSR-2/2 Requirement 9; 4.34, 4.35] [GS-G-3.1; 6.19]

How is the work of contractors controlled and monitored? [SSR-2/2 Requirement 5; 4.3, Requirement 7; 4.20] [NS-G-2.6; 3.8, 3.9]

How is post maintenance/modification testing carried out? [SSR-2/2 Requirement 31; 8.10] [NS-G-2.6; 8.50, 8.53-8.55, 9.4] [NS-G-2.14; 5.14]

4.6. Material condition

What standards are in place to promote good material condition? How is plant material condition maintained to a high standard? [SSR-2/2 Requirement 28; 7.10-7.12] [NS-G-2.6; 4.26, 4.29, 8.32-8.37, 10.1]

How is degradation of material condition identified in a timely manner? How are corrective actions taken? [SSR-2/2 Requirement 28; 7.10] [NS-G-2.14; 7.33]

What is the extent of the plant’s foreign material exclusion (FME) programme? How is the FME programme implemented, controlled and optimized in the field? [SSR-2/2 Requirement 28; 7.11] [NS-G-2.5; 3.9, 3.19, 4.2, 4.19, 5.19, 6.8]

4.7. Work control

Describe the work control process in place at the plant. How is the effectiveness of the work control process monitored?  [SSR-2/2 Requirement 31; 8.8-8.10] [NS-G-2.6; 5.14-5.19, 5.23-5.26]

What approved work authorization documents are in place? [SSR-2/2 Requirement 31; 8.9, 8.10] [NS-G-2.6; 5.1, 5.6, 5.9, 5.14]

How are works being prioritized and how effective is the process in addressing safety-significant issues? [SSR-2/2 Requirement 31; 8.14] [NS-G-2.6; 8.1-8.5] [NS-G-2.14; 7.10] [GS-G-3.1; 5.2]

How are material and manpower requirements considered during work planning? [GS-R-3; 4.1] [GS-G-3.5; 4.8-4.25]  [NS-G-2.6; 4.6, 4.11, 4.12, 8.23]

How are temporary modifications minimized? How is the maintenance backlog controlled and analysed? Are there any safety indicators to monitor this backlog? [SSR-2/2 Requirement 9; 4.34, Requirement 11; 4.41, 4.42, Requirement 31; 8.1, 8.12, 8.14] [NS-G-2.3; 6.3]

How is outage planning integrated into the work control process? [SSR-2/2 Requirement 32; 8.18] [NS-G-2.6; 5.20-5.22]

How is it confirmed that interfaces between maintenance and other groups in the plant are effective? [SSR-2/2 Requirement 31; 8.11] [NS-G-2.6; 3.12]

How is the ALARA principle incorporated into the planning and implementation of work activities? [SSR-2/2 Requirement 8; 4.25, Requirement 20; 5.16] [NS-G-2.6; 4.23] [NS-G-2.7; 3.39]

4.8. Spare parts and materials

Who is responsible for procurement and goods-receipt inspections? How are spare parts procured and then inspected upon receipt? What procedures govern the process? [SSR-2/2 Requirement 31; 8.15, 8.16] [NS-G-2.6; 8.21-8.23]

How are the quality and technical specifications of spare parts and materials maintained consistent with plant design? [SSR-2/2 Requirement 31; 8.16] [NS-G-2.6; 8.24-8.26, 8.29]

What controls has the plant implemented regarding the use of commercial-grade spare parts? [SSR-2/2 Requirement 31; 8.16] [GS-G-3.5; 5.35-5.37]

How does the plant guarantee that there are adequate spare parts and material management facilities to meet its needs? [SSR-2/2 Requirement 31; 8.17] [NS-G-2.6; 8.32]

How are appropriate environmental conditions maintained within storage facilities? [SSR-2/2 Requirement 31; 8.15, 8.17] [NS-G-2.6; 8.33]

How are stock levels defined, and what particular attention is paid to critical components? [SSR-2/2 Requirement 31; 8.15, 8.16] [NS-G-2.6; 8.24-8.29]

How are CSFIs (counterfeit, suspect and fraudulent items) prevented from entering the plant for use in systems and components? How are certificates of spare parts from outside-suppliers checked and confirmed? [SSR-2/2 Requirement 31; 8.15, 8.16] [NS-G-2.6; 8.24, 8.27, 8.29] [GS-G-3.5; 5.161, 5.162]

How does the plant guarantee that safety related spare parts and materials are traceable? [NS-G-2.6; 8.39]

How is preventive maintenance performed on spare parts? [GS-G-3.5; 5.153]

What process is in place to deal with repairs and returns of spare parts, and surplus spare parts? [SSR-2/2 Requirement 31; 8.15] [GS-G-3.5; 5.154] [NS-G-2.6; 8.21-8.23, 8.39]

How are obsolete, non-conforming and damaged spare parts controlled? [SSR-2/2 Requirement 31; 8.15] [NS-G-2.6; 8.42, 8.49, 8.50]

Are periodic QA audits and self-assessments performed and, if so, at what frequency?  [SSR-2/2 Requirement 9; 4.33-4.35] [GS-G-3.1; 6.12] [NS-G-2.6; 5.33-5.38]

4.9. Outage management

How are the outage organization and associated responsibilities defined? [SSR-2/2 Requirement 32; 8.20-8.22] [NS-G-2.6; 5.20, 5.22]

What continuous outage improvement process is in place to optimize outage performance? [SSR-2/2 Requirement 32; 8.18, 8.24, 5.21]

How is outage preparation conducted? How does this effectively control the milestones of outage preparation and the outage scope freeze date? How does outage preparation take into account past lessons learned as well as external lessons? [SSR-2/2 Requirement 32; 8.24] [NS-G-2.6; 5.21] [NS-G-2.11; 7.2]

How is nuclear safety reviewed during the outage? How is defence-in-depth maintained throughout the outage? What process is in place to review changes to the outage in terms of their implications for outage safety? [SSR-2/2 Requirement 32; 8.19, 8.20] [NS-G-2.6; 5.22]

How is outage execution monitored in terms of safety, quality and schedule adherence? [SSR-2/2 Requirement 32; 8.19] [NS-G-2.6; 5.22, 7.3]

How are contractors managed during the outage? What attention is given to the experience level of contractors present during the outage? [SSR-2/2 Requirement 32; 8.21, 8.23] [NS-G-2.6; 3.8, 3.9] [GS-G-3.5; 5.79-5.83]

How are radiation protection, waste reduction and control of chemical hazards considered in the outage programme? [SSR-2/2 Requirement 32; 8.23] [NS-G-2.6; 4.23] [NS-G-2.7; 4.2, 4.4, 4.6, 4.8]

How are personnel trained in specific aspects related to the outage, such as any infrequently performed activities, specific configurations during the outage, high-risk time windows for the outage, etc.? [SSR-2/2 Requirement 7; 4.16, 4.17, 4.19, 4.20, Requirement 32; 8.20] [NS-G-2.8; 4.1]

What long-term planning and scheduling is undertaken for plant outages? [SSR-2/2 Requirement 32; 8.18] [NS-G-2.6; 4.21]

4.10. Configuration control

How is control of plant configuration ensured during maintenance and prior to the return-to-service of plant equipment? [SSR-2/2 Requirement 10; 4.38, Requirement 11; 4.39, Requirement 31; 8.10] [NS-G-2.6; 5.17, 5.28]

What kinds of administrative procedures and controls are implemented to ensure control of plant configuration during maintenance and surveillance activities? [SSR-2/2 Requirement 31; 8.3] [NS-G-2.3; 7.1-7.3] [NS-G-2.6; 4.26, 9.9]

What system is in place for informing control room operators of all maintenance activities before they are commenced in order to maintain configuration control and ensure safe operation of the plant? [NS-G-2.6; 4.9]

4.11. Use of PSA, PSR and OEF

How does the maintenance department use PSA applications in order to optimize maintenance activities? [SSR-2/2 Requirement 31; 8.5, 8.6, 8.13] [NS-G-2.6; 7.2-7.5] [SSG-3; 10.36, 10.37, 10.52]

How are the results of periodic safety reviews utilized to identify any necessary modifications, with a view to enhancing the maintenance programme? [SSR-2/2 Requirement 12; 4.44, Requirement 31; 8.13]  [SSG-25; 3.8, 5.29, 5.41, 5.47, 5.86] [NS-G-2.3; 2.2, 3.8] [NS-G-2.6; 7.7, 7.9] [NS-G-2.12; 5.5, 7.1, 7.9-7.11]

How does the maintenance department use OEF for continuous improvement of its maintenance activities? [SSR-2/2 Requirement 24; 5.27] [NS-G-2.6; 6.11-6.14]

FACTs Requirements:

September 2016

Format

- Date format: 8 June 2016 (DD MM YYYY)

- Use The Plant instead of The Station

- Do not include procedure number , but the name of the procedure, such as the Working instruction to calibrate the pressure transmitter 1XXX

- Numbering (no numbering, use – as in this format

- Spell out all the abbreviations, such as: Main Control Room (MCR), and consistent throughout the report

- Use English words in the report, no local language words in the report

Exchange with the Counterpart

- Every night, write the facts in the format as specified (refer to the examples below)

- Save it on the last page of your Working Notes Outline

- You will have a printed out copy of the facts in your tray before lunch and you can give the facts to your counterpart for verification

- Revise the facts with the inputs from discussions with your counterpart, and finalize the facts.

- Make sure your counterparts understand the potential safety consequence of your facts (ask yourself so what)

- When you have enough facts for a theme, develop the issue per the example of issue and give it to team leader and deputy team leader early

Facts (for reference only, please delete it and add you own)

Maintenance Work Practices

- Work on Essential Service Water (ESW) pump C outlet venting Valve (1EF-V0054)

  - Floor grates at the worksite were not covered with canvas to prevent small items from falling through to the floor below.

  - Wrenches, spanner, bolts and nuts in plastic bags and lubricants for bolts were placed on the Pump inlet pipe with the potential to slip off.

  - The plastic bag containing bolts and nuts was broken during the work, and the bolts and nuts fell through the floor grates down to the floor below.

  - A soft Foreign Material Exclusion (FME) cover was used as bag for used bolts and nuts.

  - The worksite was not fenced off.

  - The above situations were not challenged by the three workers within the group.

- The pre-job brief for the test of the Load Shedding Sequencer logic check for 3.3kV essential electrical board 3 was not conducted in a structured manner as outlined in the Green Card Brief. Although most of the elements were covered, key points were not emphasized in a concise manner.

- Three way communication was not used as intended during the test of Load Shedding Sequencer logic check for the 3.3kV essential electrical board 3. The worker and the team lead did not challenge each other for not using three way communication.

- On 16 September 2015 during the leak testing on the condensate system, the test equipment used for this activity had been connected to the incorrect Condenser Extraction Pump (CEP). Not using human error prevention tools (such as pre-job briefing, point touch verbalize, peer check, and three way communication) has been identified as the main cause.

- On 4 August 2014, when working on the controller (1AB-PC0277) for the loop 2 steam generator Power Operated Relief Valve (PORV) (1AB-PV0277), an unauthorized parameter setting was used. This caused the manual close button to open the PORV and the open button to close the PORV. This condition was not identified from 4 August to 26 September 2014 as the automatic control worked correctly.