NUCLEAR POWER PRODUCTION AND DEVELOPMENT COMPANY OF IRAN

BUSHEHR NUCLEAR POWER PLANT (BNPP-2)

UNITS 2, 3

Seismic Hazard Analysis

of Bushehr NPP-2 (Final Report)

BU2/ES-OCE/ES-0-RPT/SUM-0-134/1-00/0

Revision B01

2016

Ofogh Consulting Engineers

BUSHEHR NUCLEAR POWER PLANT (BNPP-2)

UNITS 2, 3

Seismic Hazard Analysis

of Bushehr NPP-2 (Final Report)

BU2/ES-OCE/ES-0-RPT/SUM-0-134/1-00/0

Revision B01

2016

CONTENT

Introduction	2

1	Final Result of seismic hazard analysis of Bushehr nuclear plant power (phase II)	3

1.1	Earthquake catalog	3

1.2	Seismic source models and corresponding seismicity parameters	7

1.2.1 Development of seismic source model	7

1.2.2 Determination of the maximum magnitude of seismic sources	11

1.2.3 Determination of the seismicity parameters of seismic sources	12

1.3	Selection and ranking of GMPEs	13

1.4	Treatment of uncertainty	13

1.5	Final results of PSHA	15

1.6	Final results of DSHA	18

1.7	Result of Disaggregation	20

References	26

Revision list	27

Introduction

This is the final report of Bushehr Nuclear Power Plant-2 which is prepared after several meeting of an expert panel from IIEES, RIES, IPE and OCE.

After several discussions the expert panel reaches the agreement in following items to consolidate the results of PSHA and DSHA.

- Earthquake catalog

- Historical and Instrumental catalog

- Homogenizing the earthquake catalog and completeness of catalog

- Deculstering of catalog

- Delineation of seismic sources

- Geometry of 4 seismic source models

- The maximum magnitude and depth of near field sources

- The value of upper and lower seismogenic depth

- Estimation of Seismicity parameters

- The approach of estimation and value of seismicity parameters in cases there is not enough data

- The approach to evaluate maximum magnitude of sources

- The selection and weights of GMPEs

- The general form of Logic Tree and corresponding weights of each branch

It should be mentioned that this document is the final report based on the opinion of the expert panel.

# Final Result of seismic hazard analysis of Bushehr nuclear plant power (phase II)

## Earthquake catalog

The earthquake catalog is one of prerequisite and fundamental steps in any seismic hazard assessment. Such a robust earthquake catalog can undoubtedly help to have an accurate estimation of hazard at site. This step is one the challenging issues of expert panel. After several analysis and discussion the expert panel agreed to use historical catalog provided by Dr. Tatevossian and the instrumental catalog of Shahvar et al. (2013) from 1900 to 2011 with substitution of relocated events provided by Dr. Tatar in this catalog. It is also agreed to use relocated events provided by Dr. Tatar from 2011 to 2014. Regarding the magnitudes of Dr. Tatar, it is agreed to use the conversion relationships of Shahvar et al. (2013).

Based on the above agreement, the final is composed of 2576 events which 1467 events with magnitude greater than 4.0 is extracted from Shahvar catalog for the duration of (1900- 2012) and 1109 events is added to final catalog which dominantly have magnitude less than 4.0 and belongs to the 2012-2015.  In Figure 1.1 the distribution of events in the final catalog in the 300 Km around the site has been represented.

Figure ‎1.1- Distribution of events in final catalog around the 300 Km of the site

As it was mentioned the relation of Shahvar et al (2013) is used for unifying the magnitude scale of the final catalog. In Table 1.1 the magnitude scale relation of Shahvar et al (2013) which is used for homogenizing of the final catalog have been represented. In this report we use the red relation which has the lower value of standard deviation.

Table ‎1.1- Magnitude scale relation of Shahvar et al (2013)

| Relationships | R2 | rms* Error |
| --- | --- | --- |
| Regression relation between MS and MW (MS<6.1) |  |  |
| SR*: Mw=0.589 MS +2.420 | 0.872 | 0.145 |
| ISR**: MS=1.483 MW -2.996 | 0.678 | 0.230 |
| OR***: Mw=0.611 MS +2.314 | 0.871 | 0.124 |
| Regression relation between MS and MW (MS>6.1) |  |  |
| SR: Mw=0.887 MS +0.656 | 0.862 | 0.171 |
| ISR: MS=1.004 MW +0.072 | 0.848 | 0.179 |
| OR: Mw=0.949 MS +0.243 | 0.858 | 0.126 |
| Regression relation between mb and MW (Zagros) |  |  |
| SR: Mw=0.917 mb +0.507 | 0.796 | 0.341 |
| ISR: mb=0.869 MW +0.568 | 0.806 | 0.274 |
| OR: Mw=1.030 mb -0.057 | 0.784 | 0.223 |
| Regression relation between ML and MW |  |  |
| SR: Mw=0.701 ML +1.656 | 0.793 | 0.190 |
| ISR: ML=1.138 MW -0.904 | 0.664 | 0.242 |
| OR: Mw=0.763 ML +1.355 | 0.787 | 0.153 |
| Regression relation between MN and MW |  |  |
| SR: Mw=0.768 MN +1.272 | 0.816 | 0.197 |
| ISR: MN=1.067 MW -0.430 | 0.745 | 0.233 |
| OR: Mw=0.834 MN +0.932 | 0.810 | 0.154 |

*: Standard least-square (linear) regression

**: Inverted (Inverse) Standard least-square regression

***: Orthogonal Regression

In Figure 1.2 the completeness of the final catalog based on the approach of maximum curvature approach has been represented. As it is clear the final catalog for the period of 2000-2015 is nearly complete for the magnitude of 4.0. In Table 1.2 the completeness value which is taken into account for analysis has been represented.

Figure ‎1.2- Completeness of the catalog based on the approach of Maximum curveture

Table ‎1.2- The completeness value of catalog

| Period | Completeness magnitude | Magnitude uncertainty |
| --- | --- | --- |
| 1900-1920 | 5.7 | 0.4 |
| 1920-1964 | 5.4 | 0.4 |
| 1964-1980 | 4.7 | 0.3 |
| 1980-2000 | 4.1 | 0.2 |
| 2000-2015 | 3.9 | 0.1 |

For declustering of the catalog it was agreed to use the approach of Reasenberg (1985). Based on this approach the final deculstered catalog is composed of 2348 independent events which is shown in Figure 1.3.

Figure ‎1.3- Distribution of declustered events in the final catalog around the 300 Km of the site

## Seismic source models and corresponding seismicity parameters

### Development of seismic source model

One of the critical steps of PSHA is definition of seismic sources. In this regard the expert panel reaches to the agreement to use the four different seismic models with different weights. However, it was agreed that each team modified the geometry of their seismic sources in a way that an area source covers the Bushehr peninsula. In Table 1.3 the fourth seismic source models with their corresponding weight in calculation has been represented.

Table ‎1.3- The seismic source model and corresponding weight in calculation

| The seismic source models with corresponding weight in calculation |  |  |
| --- | --- | --- |
| Seismic source model | Specification | Weight |
| SM1-BNPP1 | 25 area source (Figure 1.4) | 0.111 |
| SM2-IIEES | 27 Area source and 50 line source (Figure 1.5) | 0.308 |
| SM3-RIES | 20 Area source (Figure 1.6) | 0.328 |
| SM4-IPE | 15 Area source (Figure 1.7) | 0.253 |

Figure ‎1.4- Geometry of the first seismic source (SM1-BNPP1)

Figure ‎1.5- Geometry of the second seismic source model by considering two line sources (Bushehr and KharkMish-1) near the site

Figure ‎1.6- Geometry of the third seismic source model by considering of an area source model under the site (SM3-RIES)

Figure ‎1.7- Geometry of the fourth seismic source model by considering an area source under the site (SM4-IPE)

It should be mentioned in modeling of seismic sources the following value of depth which is determined by the expert is used (Table 1.4).

Table ‎1.4- Depth of seismic source models with corresponding weights

| Source Name | D=6.0 Km | D=9.0 Km | D=13.5 Km | D=18.5 Km |
| --- | --- | --- | --- | --- |
| Bushehr Peninsula | 0.12 | 0.275 | 0.24 | 0.365 |
| Mond | 0.085 | 0.295 | 0.33 | 0.29 |
| Borazjan | 0.175 | 0.335 | 0.31 | 0.18 |
| Other sources | 0.135 | 0.335 | 0.345 | 0.185 |

### Determination of the maximum magnitude of seismic sources

The maximum magnitude of seismic sources is determined by the relation of Wells and Coppersmith (1994) with following criteria.

- Using relationships of strike-slip fault for North-South trends

- Using relationships of reverse fault for North West-South East trends

- Using SRL (Surface Rupture Length) relationship with following branches:

  - Total length of the fault length on the map   (0.325)

  - 0.75 length of the fault length on the map    (0.53)

  - 0.50 length of the fault length on the map     (0.145)

It should be mentioned in the fourth seismic source model (SM4-IPE) the following procedure is adopted for estimation of maximum magnitude of sources.

- Total length of the fault length on the map   (0.282)

- 0.75 length of the fault length on the map    (0.341)

- 0.50 length of the fault length on the map     (0.100)

- Max obs+delta				(0.279)

Considering Mmax of areal sources with no fault inside it (or crossing a fault from several areal sources) it is agreed:

- For IPE sources, the border of areal sources 6 and 7 was revised in order to completely include Borazjan Fault in source 6. The following Mmax are assigned to areal sources:

| Areal Source No (IPE) | Mmax |
| --- | --- |
| 7 | 6.2 |
| 9 | 6.2 |
| 12 | 6.1 |
| 6 (Borazjan) | 7.5 |

- For BNPP1 model, the following Mmax are assigned to areal sources:

| Areal Source No (BNPP1) | Mmax |
| --- | --- |
| CG | 5.0 |
| FC | 5.0 |
| ZA | 5.0 |
| KHII | 5.0 |
| KHI | 5.7 |
| B | 5.7 |
| DA | 5.7 |

The value of maximum magnitude of sources (Mmax) with their corresponding weight is represented in an electric file which is attached to report.

### Determination of the seismicity parameters of seismic sources

Determination of seismicity parameters is another challenging issue in performing PSHA. In this report the procedure which is agreed by expert panel is adopted for calculating of seismic parameters.

For estimation of seismicity parameter (β, λ) two approaches of Kijko (2012) and slip rate is implemented with following procedure.

- The approach of Kijko (2012) is used for calculation of b value.

- All the events located inside each source are used for calculation of b value. However, the minimum number of events for calculation shall be 30.

- In sources where number of events inside the source is less than 30, it is agreed to use regional b value equal to 1.15

- In sources that the value of slip rate is available, it is agreed to use both Kijko (2012) and slip rate method of Dr. Talebian with following weights:

- Kijko (2012) 		(0.47)

- Slip rate method	(0.53)

The values of slip rates which are accepted by expert panel.

- It is agreed to set Mmin of integration as 4.5

The value of seismicity parameters of seismic sources with their corresponding weight is represented in an electric file which is attached to report.

## Selection and ranking of GMPEs

Selection of appropriate GMPEs and ranking of them is another challenging issue in conducting the seismic hazard analysis of Bushehr Nuclear Power Plan- 2. In this regard the expert panel decided to use 5 different GMPEs as follow with equal weights (Table 1.5). Also the truncation level of PDF of GMPEs was chosen to be 3.0 sigma.

Table ‎1.5- The final selected GMPEs with their corresponding weights

| Ground Motion Parameter Equation | Weight |
| --- | --- |
| Ghasemi et al (2009) | 0.20 |
| Kale et al (2015) | 0.20 |
| West II Abrahamson and Silva (2014) | 0.20 |
| West II Chiu and Youngs (2014) | 0.20 |
| West II Idriss (2014) | 0.20 |

Also, the expert panel agreed to use Sinaean05 GMPE for PGA in combination with Ghasemi09 for PSA in other periods.

## Treatment of uncertainty

In this study, the analysis of Logic Tree is performed as it is illustrated in Figure 1.8. As it is clear, in this study four seismic source models are included in calculation. In the first branch of logic tree four different depths have been considered. Also, for estimation of seismicity parameters two approaches of Kijko (2012) and slip rate with equal different weights are considered in calculation. The maximum magnitude of each source is estimated by physical dimension of each source (for the fourth seismic source model another branch which is maximum magnitude + delta is added). Five different GMPEs with equal weights are incorporated in calculation.

The final logic tree in this study includes 520 branches. Figure 1.8 represents the final logic tree and corresponding weights of each branch.

Figure ‎1.8- The structure of logic tree for capturing uncertainty in PSHA

## Final results of PSHA

In this section the result of PSHA for Bushehr Nuclear Power Plan will be represented. It should be mentioned this analysis has been done with considering of VS30=600 m/s and with considering of areal sources for all seismic models (IIEES, RIES and IPE seismic models).

In Figure 1.9 and Table 1.6 the mean, median, 16th and 84th percentile of the hazard curve for PGA for seismic source models has been represented.

Figure ‎1.9- The mean, median, 16th and 84th percentile of the hazard curve PGA

Table ‎1.6- The mean, median, 16th and 84th percentile of the acceleration in different return period for the first scenario with VS30=600 m/s

| Return Period (year) | Mean | 16th percentile | 50th percentile | 85th percentile |
| --- | --- | --- | --- | --- |
| 475 | 0.251 | 0.162 | 0.235 | 0.316 |
| 1000 | 0.322 | 0.209 | 0.299 | 0.402 |
| 2475 | 0.421 | 0.280 | 0.394 | 0.504 |
| 10000 | 0.604 | 0.403 | 0.568 | 0.680 |

In Figure 1.10 to Figure 1.12 the uniform hazard spectrum for different return period (1000, 10000 and 100000 years) with mean and 16th, 50th and 84th percentile have been represented.

Figure ‎1.10- Uniform hazard spectrum with mean and 16th, 50th and 84th percentile for return period of 1000 year

Figure ‎1.11- Uniform hazard spectrum with mean and 16th, 50th and 84th percentile for return period of 10000 year for

Figure ‎1.12- Uniform hazard spectrum with mean and 16th, 50th and 84th percentile for return period of 100000 year for

## Final results of DSHA

In this section the result of DSHA for Bushehr Nuclear Power Plant will be represented. It should be mentioned in this section we use the input parameter of linear sources in IIEES seismic source model with following exception which is represented by expert panel.

“Considering DSHA, it is agreed to use all the methods, relationships and weights for all the sources except Bushehr Peninsula based on expert panel opinion. For the sources inside Bushehr Peninsula (Bushehr and Khargmish faults), it is agreed by voting to use Mmax=6.0 with the location of the faults”

In Figure 1.13 the mean, mean plus one sigma and mean plus two sigma of deterministic spectrum has been represented. In Table 1.7 the value of acceleration for near seismic sources has been represented. As it is clear the event with magnitude Mw=6.0 under the site, Bushehr, Kharkmish and longer segment of east Mond fault represent the highest values of acceleration, respectively.

Figure ‎1.13- The mean, mean+1sigma and mean+2sigma of deterministic spectrum

Table ‎1.7- Value of acceleration for PGA for near seismic sources

| Source Name | Mean | Mean+1sigma | Mean+2sigma |
| --- | --- | --- | --- |
| KharkMish1 | 0.25 | 0.48 | 0.94 |
| Bushehr | 0.25 | 0.48 | 0.94 |
| Mond-W1 | 0.15 | 0.28 | 0.52 |
| Mond-W2 | 0.19 | 0.35 | 0.63 |
| Mond-E1 | 0.11 | 0.21 | 0.38 |
| Mond-E2 | 0.23 | 0.41 | 0.74 |
| Event with M=6.0 under site | 0.26 | 0.51 | 0.99 |

In Table 1.8 the value of acceleration for one branch of Logic Tree for calculation of DSHA has been represented. In this branch the depth of fault is considered equal to 9.0, magnitude is obtained based on the relation of wells and coppersmith (1994) with assumption that total length of fault has been ruptured.

Table ‎1.8- Distance, magnitude and acceleration of near field sources with considering of depth equal to 9.0 and assume that total length of fault is ruptured

| Source Name | Mw | Rjb | Rrup | Rhyp | Ketal2015 | Ghetal2009 | I2015 | CY2015 | AS2015 | LogicTree |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| KharkMish1 | 6.0 | 2.35 | 5.27 | 10.99 | 0.477 | 0.345 | 0.627 | 0.728 | 0.710 | 0.577 |
| Bushehr | 6.0 | 1.91 | 4.81 | 10.99 | 0.483 | 0.345 | 0.660 | 0.767 | 0.738 | 0.599 |
| Mond-W1 | 6.8 | 14.16 | 14.22 | 22.49 | 0.327 | 0.345 | 0.476 | 0.514 | 0.484 | 0.429 |
| Mond-W2 | 7.1 | 1.53 | 1.87 | 33.29 | 0.745 | 0.302 | 1.468 | 1.325 | 0.936 | 0.955 |
| Mond-E1 | 6.8 | 23.36 | 23.40 | 31.36 | 0.214 | 0.252 | 0.292 | 0.322 | 0.325 | 0.281 |
| Mond-E2 | 7.1 | 19.40 | 24.15 | 38.85 | 0.295 | 0.261 | 0.326 | 0.360 | 0.321 | 0.313 |
| Event with M=6.0 under site | 6.0 | 0.00 | 4.43 | 9.0 | 0.497 | 0.409 | 0.689 | 0.801 | 0.763 | 0.632 |

## Result of Disaggregation

Once the PSHA computations are complete, a critical question is “which earthquake scenario contributes the most hazard to the site” Because we have aggregated all scenarios together in the PSHA calculations. The deaggregation of the mean probabilistic seismic hazard analysis (PSHA) results determines the contribution of individual magnitude and distance ranges to the overall seismic hazard. Information from the deaggregation is useful to both review the PSHA and understand the seismic sources that contribute most to hazard at the site.

In this report for determining the controlling earthquake the approach of NUREG 1.208 is adopted. In this approach, the controlling earthquakes are developed from the deaggregation of the PSHA results at ground motion levels corresponding to the annual frequencies of 1 E-04 and 1 E-05 and are based on the magnitude and distance values that contribute most to hazard at the average of 1 and 2.5 Hz and the average of 5 and 10 Hz. More detail about the procedure and formulation can be found in reference (NUREG 1.208).

In Figure 1.14 to Figure 1.21 the results of deaggregation analysis in different period for return period of 10000 and 100000 years have been represented.

Figure ‎1.14- Deaggregation analysis for return period of 10000 year for period of 0.1 sec

Figure ‎1.15- Deaggregation analysis for return period of 10000 year for period of 0.2 sec

Figure ‎1.16- Deaggregation analysis for return period of 10000 year for period of 0.4 sec

Figure ‎1.17- Deaggregation analysis for return period of 10000 year for period of 1.0 sec

Figure ‎1.18- Deaggregation analysis for return period of 100000 year for period of 0.1 sec

Figure ‎1.19- Deaggregation analysis for return period of 100000 year for period of 0.2 sec

Figure ‎1.20- Deaggregation analysis for return period of 100000 year for period of 0.4 sec

Figure ‎1.21- Deaggregation analysis for return period of 100000 year for period of 1.0 sec

In Table 1.9 the high and low frequency controlling earthquakes for different annual probability based on the approach of NUREG 1.208 have been represented.

Table ‎1.9- High- and Low-Frequency controlling earthquakes

| Hazard | Magnitude (Mw) | Distance (Km) |
| --- | --- | --- |
| Mean 1 E-03 High-Frequency (5 and 10 Hz) | 5.6 | 12.16 |
| Mean 1 E-03 Low-Frequency (1 and 2.5 Hz) | 6.7 | 34.27 |
| Mean 1 E-04 High-Frequency (5 and 10 Hz) | 5.8 | 11.10 |
| Mean 1 E-04 Low-Frequency (1 and 2.5 Hz) | 6.9 | 26.64 |
| Mean 1 E-05 High-Frequency (5 and 10 Hz) | 6.1 | 9.80 |
| Mean 1 E-05 Low-Frequency (1 and 2.5 Hz) | 7.1 | 18.75 |

# References

Abrahamson N, SilvaW (2008) Summary of the Abrahamson & Silva NGA ground motion relations. Earthq Spectra 24:67–97

Abrahamson, N. and Silva, W. [2008] “Summary of the Abrahamson & Silva NGA ground motion relations,” Earthquake Spectra 24(1), 67–97.

Chiou, B. S. J., & Youngs, R. R. (2014). Update of the Chiou and Youngs NGA model for the average horizontal component of peak ground motion and response spectra. Earthquake Spectra, 30(3), 1117-1153.

Ghasemi, H., Zare, M., Fukushima, Y., and Koketsu, K. [2009] “An empirical spectral ground-motion model for Iran,” Journal of Seismology 13, 499–515.

Idriss, I. M. (2014). An NGA-West2 empirical model for estimating the horizontal spectral values generated by shallow crustal earthquakes.Earthquake Spectra, 30(3), 1155-1177.

Kijko, A. (2012). On Bayesian procedure for maximum earthquake magnitude estimation. Research in Geophysics, 2(1), e7.

Reasenberg, P. (1985), Second-order moment of central California seismicity, 1969-82, J. Geophys. Res., 90, 5479-5495.

Shahvar M P, Zare M, Castellaro S (2013) A Unified Seismic Catalog for the Iranian Plateau (1900–2011). Seismological Research Letters 84:233-249

Wells, D. L., and K. J. Coppersmith (1994). New empirical relationships among magnitude, rupture zength, rupture width, rupture area, and surface displacement, Bull. Seism. Soc. Am. 84, 974-1002.

Revision list

| Rev. | Numbers of sheets |  |  |  | Total number of sheets in the document | Docu-ment № | Signature | Date |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | changed | replaced | new | deleted |  |  |  |  |