Начало формы

| WANO Event Report WANO Moscow Centre, 2014-0113 | Main Steam Isolation Valve (MSIV) failed to close when tested Bushehr 1, 05.02.2014 | Revision Number 00 - Posted date 08.08.2014 |
| --- | --- | --- |

None

| Unit (Year) :; Bushehr 1 (2012). Additional Units :. Reactor Type :; PWR. Reactor Manufacturer :; Framatome. Plant Designer :; TO BE DONE. Event Date :; 05.02.2014. INES :; 0. | OE Station Information Contact WANO Information Contact |
| --- | --- |

| Reference : |  |
| --- | --- |

OECT Information

Summary
N/A 

Causes
N/A 

Keywords
N/A 

References
N/A

Summary

Steam pipeline MSIVs were inspected per program during the outage.

These valves were checked for their closed position by opening the control valves under the supervision and on command of the Main Control Room (MCR) crew.

RA10S004 and RA20S004 MSIVs were operating as requested.

With the attempts made to close RA30S004 MSIV through closing the control valves, the MSIV failed to close.

Direct Cause: Detached parts

Root Cause: Deficient original design

Contributor: The equipment installed does not meet the requirements

Description

Steam pipeline MSIVs were inspected per program during the outage.

These valves were checked for their closed position by opening the control valves under the supervision and on command of the Main Control Room (MCR) crew.

RA10S004 and RA20S004 MSIVs were operating as requested.

RA30S004 MSIV testing results

With the attempts made to close RA30S004 MSIV through closing the control valves 13RA30S041, 042, the MSIV failed to close.

The following defects were found:

13RA30S041 valve demonstrated higher opening time, while 13RA30S042 valve had a defective actuator limit switch.

When using 12RA30S043, 044 and RA30S004 control valves, the MSIV also failed to close, although the valves were operating as requested.

Consequences

Main Steam Isolation Valve (MSIV) failed to close when tested

Analysis/Comments

Working, operating, design and other documents were studied to identify the causes of the MSIV failure to close and a potential human factor effect on the MSIV failure.

The following conclusions were made once all the aforesaid documents had been studied:

A connecting sleeve supplying steam to control the MSIV had a loose connection with the MSIV.

MSIV closing position control was impossible as there was no way of supplying control steam.

Direct Cause: Detached parts

Root Cause: Deficient original design

Contributor: The equipment installed does not meet the requirements.

Corrective Actions

The following actions will be taken to repair the equipment:

The MSIV will be repaired and inspected thereafter.

Control valve defects will be disposed of.

All the other MSIV control valves will be inspected.

The MSIV operation and connecting sleeve-to-MSIV connection change will be discussed with the supplier.

Attachments

Coded Fields

| Field | Code | Description |
| --- | --- | --- |
| Category | 03 | Major equipment damage |
| Consequences | 03 | Equipment damage, Fires, Steam Generator Tube Leak |
| Systems | 510 | Main Steam and auxiliaries (including auxiliary steam) |
| Components | 230 | Valves (including safety, check, relief & solenoid), valve operators, controllers, dampers (including fire dampers), seals and packing, flanges, Orifices, Drain Traps, Diaphragm Rupture Disks |
| Status | 150 | Hot shutdown - sub critical and coolant temperature < normal operating temperature |
| Activity | 25 | Routine Testing (of existing equipment) with existing procedures/documents |
| Group | 170 210 | Work Planning or Scheduling Shift - Control Room Operators |
| Direct Cause | 0101 | Deformation, distortion, spurious movement, loosening, displacement |
| Root Cause | 2001 | Original design inadequate |
| Causal Factor | 2108 | Equipment installed does not meet all codes / requirements |

CONFIDENTIALITY NOTICE: Copyright © 1987-2014 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale or commercial use. This document is protected as an unpublished work under the copyright laws of all countries which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. This document and its contents are confidential and shall be treated in strictest confidence. In particular, except with the prior written consent of the WANO Coordinating Centre, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations.

LIABILITY DISCLAIMER NOTICE: This information was prepared in connection with work sponsored by the WANO. Neither WANO, WANO members, nor any person acting on the behalf of them (a) makes warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that use of any information, apparatus, method or process disclosed in this document may not infringe on privately owned rights, or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of any information, apparatus, method, or process disclosed in this document.

Конец формы