## Sheet
Significance | INES | Event Number | Event Date | Station | Reference Unit | Title | OECT Description | OECT Causes | Keywords | OECT Reference | PO&Cs
Trending | 0 | WER ATL 15-1097 | 2015-09-10 | Bruce A | Bruce A 4 | Unit Taken Offline Due to Deteriorating Generator Stator Cooling | During normal operation, the turbine generator stator cooling system was found degraded. The unit was shutdown to rectify the problem. | The cause was blockage of the system strainer which was single point vulnerability. Another cause was not implementing the modification done for the stator cooling system design on units 1 and 2. | cooling,modification,reactor shutdown,single point vulnerability,stator,strainer |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS IMPLEMENTATION (PI.3);
Other | 0 | WER ATL 15-1095 | 2015-09-05 | Bruce A | Bruce A 1 | Lessons Learned From Problem Solving Exercise – Improving Preventative Maintenance Task Planning and Scheduling Survival | See summary below. | See causes below.
Other | 0 | WER ATL 15-1093 | 2015-08-14 | Bruce A | Bruce A 4 | Lessons Learned From Unposted Radiation Hazard Incident | See summary below. | See causes below.
Trending | 0 | WER ATL 15-1091 | 2015-07-24 | Bruce A | Bruce A 4 | Lessons Learned From Incident Involving Worker Entering Reactor Vault Without Required Dosimetry | During an outage, a supplemental worker entered the reactor vault and stayed there for 10 minutes without wearing an electronic personal dosimeter. There was a potential for the worker to be exposed to radiation without a method to alert or track the amount of exposure received. | The cause was failure to apply human performance tools, inadequate peer check and pre-job brief. | contractor,human error,prejob brief,radiation exposure |  | RADIOLOGICAL SAFETY (RS.1);
Trending | N | WER ATL 15-1089 | 2015-07-06 | Darlington | Darlington 3 | Missed Opportunity to Force Cool Turbine Results in 2-day Extension to Forced Outage | While shutting down to address a generator hydrogen seal oil leak, forced cooling of the turbine was not conducted. This resulted in a 2-day extension to the outage critical path. | The cause was inadequate procedures as it did not provide flexibility and criteria to allow forced cooling of the turbine. | cooling,procedure inadequacy,turbine |  | CONDUCT OF OPERATIONS (OP.2);
Other | N | WER ATL 15-1087 | 2015-09-01 | Cernavoda | Cernavoda 1 | Imprint errors found in Computer Software Change for Fuel Handling Driving Program | See summary below. | See causes below.
Trending | N | WER ATL 15-1085 | 2015-08-20 | Cernavoda | Cernavoda 1 | Containment Hydrogen Monitoring System Stalled due to Momentary Power Interruption during Performance of Mandatory Testing | During normal operation and while performing a test, the hydrogen and containment atmosphere monitoring system stalled and became unavailable until manually reset by the operator. | The cause was brief interruption of the 220 V power supply during the test as the system did not have uninterruptible power supply. | containment monitor,gas monitor,hydrogen,power supply |  | EQUIPMENT PERFORMANCE (ER.1);
Other | N | WER ATL 15-1083 | 2015-08-10 | Laguna Verde | Laguna Verde 1 | Radiation area identified on control building roof top | See summary below. | See causes below.
Other | N | WER ATL 15-1081 | 2015-08-06 | Laguna Verde | Laguna Verde 2 | Turbine Service Water Pump trip due to phase C overload | See summary below. | See causes below.
Trending | 0 | WER MOW 15-0199 | 2015-09-25 | Khmelnitsky | Khmelnitsky 1 | #PRELIMINARY# Low pressure and hi humidity observed inside the containment during Reactor Pressurizer Pilot Operated Relief Valves (PORVs) Testing | During startup in hot shutdown and while testing pressuriser pilot operated relief valves, primary coolant pressure and pressuriser level was observed dropping with increase in humidity, temperature and pressure in containment. The reactor was brought to cold shutdown to rectify the problem. | The direct cause was leak from the stem of a valve. The root cause is under investigation. | containment pressure,leak,pilot operated relief valve,pressuriser level,pressuriser relief valve,reactor coolant,reactor pressure |  | EQUIPMENT PERFORMANCE (ER.1);
Trending |  | WER MOW 15-0133 | 2015-07-06 | Smolensk | Smolensk 1 | The unit 1 shut down due to leakage detection inside the Reinforced Leaktight Compartment (RLC) | During normal operation, primary coolant leakage was detected inside a reinforced leak tight compartment. The reactor was scrammed manually with a reactor setback switch. The event resulted in a 7-days outage. | The direct cause was leakage from a check valve body-bonnet flange joint on a pipe due to non-uniform nut tightening. The root cause was deficient maintenance and deficient maintenance documentation as tightening torque check intervals were not specified. | check valve,flange,leak,manual scram,nut,procedure inadequacy,reactor coolant,torque |  | EQUIPMENT FAILURE PREVENTION (ER.2); MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
Trending | N | WER TYO 15-0209 | 2014-08-04 | Fuqing | Fuqing 1 | KIC (Plant Computer Information & Control System) operator station shortly unavailability | During commissioning at 0.95% reactor power, plant computer information and control system (KIC) was unavailable. KIC lost its functions, station monitoring and control switched to back up panel (BUP) and control rods switched to auto mode. | The direct cause was incorrect configuration of KIC. The root cause was that I and C personnel failed to comprehensively verify the parameter data during modification. Another root cause was inadequate risk awareness of I and C personnel on the essential equipment related to DCS. | human error,modification,monitor |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER TYO 15-0130 | 2015-07-17 | Hamaoka | Hamaoka 4 | Entering LCO resulting from the automatic shutdown of an emergency diesel generator | During a periodic inspection, the limit switch for the mechanical overspeed shutdown system of an emergency diesel generator (EDG) was turned on accidentally resulting in the EDG being unavailable. A limiting condition of operations was entered. | The direct cause was a human error by a contractor. The noncompliance was identified in the absence of a supervisor, a gap in work recognition between the supervisor and the workers and lack of consideration for non-experience contractors. | communication,contractor,diesel generator,human error,limiting condition of operation,supervisory oversight,switch,work control |  | MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
Other | N | WER TYO 15-0049 | 2015-03-11 | Hamaoka | Hamaoka 5 | Wash water leakage during inspection of high conductivity waste system components | See summary below. | See causes below.
Trending | N | WER ATL 15-1079 | 2015-04-20 | Watts Bar | Watts Bar 1 | Vital Power System Malfunction Due To Shorted Test Leads | During normal operation and while troubleshooting on the power supply fuses to 48 V AC power supply, the test leads were shorted resulting in a solid state protection system breaker trip and unexpected annunciator for vital power and reactor vessel level instrumentation system. | The direct cause was human error. The apparent cause was inadequate communication between departments. The contributing cause was failure to use procedure. | breaker,human error,reactor protection system,short circuit |  | MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
Trending | N | WER ATL 15-1077 | 2015-02-04 | Summer (Virgil C.) | Virgil C. Summer 1 | Reactor Building Spray Isolation Valve Failure | During normal operation and while performing charging pump and diesel generator slave relay test, the reactor building spray sump isolation valve did not show fully open at the main control board and the engineered safety features status light for the valve position also remained dim. This resulted in entry into a 72-hour shutdown limiting condition of operation. | The apparent cause was degraded tolerances in the springpack and open torque switch settings due to normal wear. | ageing,containment spray,isolation valve,limiting condition of operation,torque switch |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | N | WER ATL 15-1075 | 2015-03-18 | Oconee | Oconee 1 | Onsite Emergency AC Power Supply Unavailable Due To High Generator Bearing Oil Level | During normal operation, an on-site emergency hydroelectric generator became inoperable for emergency start when a level switch in the generator bearing oil actuated upon high oil level and opened a permissive contact in the emergency start circuit. A 72-hour action statement was entered for units 1, 2 and 3. | The direct cause was inadequate level switch set point tolerance as it did not consider system changes such as thermal expansion of the oil upon shutdown combined with the maximum cold oil fill level. | bearing,emergency power,level switch,limiting condition of operation,oil level,setpoint |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); ENGINEERING FUNDAMENTALS (EN.1);
Trending | N | WER ATL 15-1073 | 2015-06-10 | North Anna | North Anna 1 | Turbine Driven Auxiliary Feed Water Pump Steam Supply Trip Valve Inadvertently Tripped Closed | During normal operation, the main steam trip valve to the turbine driven auxiliary feedwater (AFW) pump was inadvertently tripped closed resulting in unavailability of the AFW pump. | The cause was that a security officer unknowingly bumped the trip valve during routine round. | auxiliary feedwater pump turbine driven,human error,valve |  | OPERATION CONFIGURATION CONTROL (CM.2); HUMAN PERFORMANCE (HU.1);
Trending | N | WER ATL 15-1071 | 2015-05-23 | Summer (Virgil C.) | Virgil C. Summer 1 | Main Steam Header "B" Power Relief Valve Found In "Manual" Position | During normal operation, a main steam header power relief valve station was found in manual position and could not be placed in auto position. | The apparent cause was failure of a tracking driver card due to normal ageing. | ageing,circuit card,safety relief valve |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Other | N | WER ATL 15-1069 | 2015-03-16 | River Bend | River Bend 1 | Detection of Pipe Wall Thinning Attributed to Flow Accelerated Corrosion (FAC) | See summary below. | See causes below.
Other | N | WER ATL 15-1067 | 2015-05-05 | Hope Creek | Hope Creek 1 | High Pressure Coolant Injection Exhaust Trip During Overspeed Testing | See summary below. | See causes below.
Trending | N | WER ATL 15-1065 | 2015-05-28 | Byron | Byron 1 | Auxiliary Feedwater Pump Inboard Bearing Oil Leak Discovered During Monthly Surveillance Run | During normal operation and while testing a diesel driven auxiliary feedwater (AFW) pump, oil leakage resulted in declaring the AFW pump inoperable and consequently entry into a limiting condition of operation. | The apparent cause was that the deflector ring moved out of position due to loss of engagement of the set screws with the pump shaft. This was due to inadequate torque for set screws which was not specified by the manufacturer and thread locking compound was also not used. | auxiliary feedwater pump,leak,limiting condition of operation,oil,procedure inadequacy,setscrew,torque |  | CONDUCT OF MAINTENANCE (MA.2);
Other | N | WER ATL 15-1063 | 2015-06-04 | Wolf Creek | Wolf Creek 1 | Radiation Monitor System Inverter Damage due to Electrical Overheating | See summary below. | See causes below.
Trending | 0 | WER ATL 15-1061 | 2015-01-07 | Beaver Valley | Beaver Valley 2 | Emergency Diesel Generator Jacket Water Leak During Operations Surveillance Test | During normal operation and while performing an emergency diesel generator (EDG) test, a jacket water leak was identified at a flanged connection in the turbocharger loop section, resulting in the EDG inoperability and entering into a limited condition of operation (LCO). | The cause was a failed gasket in the turbocharger due to untimely performance of appropriate corrective maintenance. An inadequate perception of the risk existed within the organization. Contributors were weak adherence of operation process, inadequate corrective action program implementation and inadequate post-maintenance test. | diesel generator,gasket,leak,limiting condition of operation,procedure adherence |  | CONDUCT OF MAINTENANCE (MA.2); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
Other | N | WER ATL 15-1060 | 2015-05-02 | Wolf Creek | Wolf Creek 1 | Error During Physics Testing Restoration Causes Alarm | Summary see below. | See causes below.
Trending | N | WER ATL 15-1059 | 2015-03-26 | Arkansas Nuclear One | Arkansas Nuclear One 2 | High Pressure Injection Check Valve Failed Testing | During normal operation and while performing a valve closure test, a high pressure injection check valve was found leaking. This condition resulted in isolating a train for the high pressure safety injection system. The leak was a recurring issue. | The apparent cause was inadequate spring design and piping/installation. | check valve,design,high pressure coolant injection,leak,piping,spring |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Other | N | WER ATL 15-1058 | 2015-03-05 | Perry | Perry 1 | Small Fire in the Unit 1 Heater Bay on a 6” Flexible Ventilation Hose During Welding | See summary below. | See causes below.
Trending | N | WER ATL 15-1057 | 2015-08-18 | Darlington | Darlington 4 | Standby Digital Control Computer Stalled without Restart | During normal operation, digital control computer (DCC) stalled without restart. This occurred again a week later. Without a Standby, a stall on the other DCC will result in unit shutdown and loss of generation. | The direct cause was an intermittent loss of power to a digital output (DO) chassis. The apparent cause was age-related degradation/deterioration of +5VDC I/O power supplies of the DO chassis. | ageing,degradation,power supply |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Other | N | WER ATL 15-1056 | 2015-08-05 | Darlington | Darlington 1 | Elevated Chlorine Result in Condenser Cooling Water during Follow up Sampling | See summary below. | See causes below.
Other | N | WER ATL 15-1055 | 2015-07-02 | Cernavoda | Cernavoda 2 | Contamination of the demineralized water in the feedwater supply tank 2-4322-TK99 | See summary below. | See causes below.
Trending | 0 | WER ATL 15-1054 | 2015-07-16 | Barakah | Barakah 1 | Meteorological Tower Instrument Sensors Fall from 60 Meters | During construction and following maintenance on the meteorological tower instruments, an instrument package fell from approximately 60 meters high while being raised to the respective locations on the tower. Instruments on the tower were struck and damaged. There was the potential of serious personal injury. | The cause was inadequate periodic maintenance programme on the winch equipment by contractors. Contributing cause was ageing due to the extreme environmental conditions. | ageing,contractor,fall,industrial safety,instrument cable,preventive maintenance | SOER 2008-1 Rec 3 | EQUIPMENT FAILURE PREVENTION (ER.2); INDUSTRIAL SAFETY (IS.1);
Trending | N | WER ATL 15-1053 | 2015-08-05 | Laguna Verde | Laguna Verde 1 | Reactor power increase due to heater drain system oscillations | During operation at 87.5% power and while searching main condenser air leak, level in a feed water heater increased unexpectedly and the heater alternate drain opened causing a flow decrease in heater drain system. Consequently, reactor water level decreased and feed water flow increased, resulting in increasing reactor power to 2030 MWt (vs licensed 2027 MWt). | The apparent cause was inattention to detail. Operator did not identify that changes in the feed water heater would cause the perturbation in the control of the heater level and that this would finally affect the reactor water level control causing a reactivity management event. Other causes were inadequate procedure and lack of communication among all operations personnel. | communication,heater,heater drain,power ascension,procedure inadequacy,reactivity management | SOER 2007-1 Rev.1 Rec 3 and 4, SOER 2013-1 Rec 4 | OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);
Other | N | WER ATL 15-1052 | 2015-07-09 | Cernavoda | Cernavoda 2 | Chemical alert declared due to oil spill during filling operations to spare transformer in 110 kV station | See summary below. | See causes below.
Other | 0 | WER MOW 15-0198 | 2015-02-23 | Leningrad | Leningrad 2 | A motor of the ventilation facility associated with the exhaust ventilation system (V-74/6) failed. | See summary below. | See causes below.
Other | 0 | WER MOW 15-0197 | 2015-03-27 | Smolensk | Smolensk 2 | A Second Stage Condensate Pump Tripped from a Stator Winding Fault | See summary below. | See causes below.
Trending | 0 | WER MOW 15-0196 | 2015-07-11 | Leningrad | Leningrad 4 | Unit 4 emergency diesel generators started | During an outage, an emergency startup transformer tripped on the phase-to- phase cutoff of the 110 kV switchyard overhead line with a subsequent deenergization of standby busducts. An automatic reactor scram occurred on loss of voltage on all 6 kV non-vital buses with a subsequent start-up of emergency diesel generators. | The direct cause was failure to detect heating of the associated transformer stub from a through wall defect. The root causes were terminal fabrication defect and missing requirement for using mobile thermal imagers in the operating documentation. | crack,emergency power,procedure inadequacy,automatic scram,temperature,transformer,vendor | SOER 2011-1 Rev 1 Rec 4 and 5 | LONG-TERM EQUIPMENT RELIABILITY (ER.3); CONDUCT OF MAINTENANCE (MA.2);