## Sheet1
[8 empty] | Current Date : | 2017-10-22
|  |  | R.1 | AFI LF.1-1 Corrective Measures - Corrective measures in the field of Management and Leadership | Responsible entity Manager of management system and supervision | Deadline | STATUS | Change DATE : | 2017-10-22 15:42
1LF.1-1 | 1 | LF.1-1 | 1.1 | Categorizing the plant events according to the type of event and system of equipment which is defective | Manager of management system and supervision / Head of Operating experiences group | 2015-10-22 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.2 | Drawing up the order for re-evaluating all of the events in terms of effectiveness of corrective measures and their repetition and the measures which were taken | Manager of management system and supervision | 2015-10-31 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.3 | Analyzing the evaluation of events on the basis of notification issued and developing the report | Manager of management system and supervision / Chairman of evaluation committees | April 31, 2016 | AI
1LF.1-1 | 1 | LF.1-1 | 1.4 | Developing procedure for evaluation of effectiveness of corrective measures in the area of events | Manager of management system and supervision / Head of Operating experiences group | 2015-11-21 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.5 | Analysis of events annually and submitting report to high committee of safety | Manager of management system and supervision / chairman of nuclear safety self-assessment committee | Permanent one-year periods | SAT
1LF.1-1 | 1 | LF.1-1 | 1.6 | Sending letter to NPPD as for performing independent analysis of events related to BNPP and taking necessary measures for improvement | Manager of management system and supervision | 2015-10-22 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.7 | Revising the procedure of orders and notifications and determining the strict and cautionary requirements in decision-taking | Manager of management system and supervision | 2015-03-10 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.8 | Pursuing the approval and ratifying the procedure of technical decisions by NNSD and NPPD | Manager of management system and supervision / Planning and Technical Documents manager | 2015-07-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.9 | Revising or developing the new procedure (including technical, managerial decisions) in BNPP (procedure in the level of plant) and receiving the necessary approvals. | Manager of management system and supervision / Planning and Technical Documents manager | 2016-03-19 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.1 | Sending letter to NPPD for establishing an independent and high supervision committee in order to analyze and evaluate event investigation reports and the adequacy of corrective measures taken and technical decisions which were taken. | Manager of management system and supervision | 2016-03-19 | AI
1LF.1-1 | 1 | LF.1-1 | 1.11 | Establishing the methodology of ASSET and HPES in the investigation of events and incidents in plant by using the capacities of technical support contracts. | Manager of management system and supervision | 2016-09-20 | FAR
1LF.1-1 | 1 | LF.1-1 | 1.12 | Using the principle of similar equipment in drawing up the corrective measures and making necessary changes in the procedure of investigating events and receiving necessary approvals: (drawing up correcting measures based on the principle of corrective and preventive measures in similar equipment ). | Manager of management system and supervision / chairman of events and accidents investigation committee | 2016-03-19 | AI
1LF.1-1 | 1 | LF.1-1 | 1.13 | Adding the requirement of comparison of technical decisions and notification orders with FSAR (NPP Final Safety Assessment Report) in the procedure of technical decisions | Manager of management system and supervision / Planning and technical documents manager | 2016-03-19 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.14 | Adding the requirement of comparison of notification orders with FSAR in the procedure of notifications and orders | Manager of management system and supervision | 2016-03-19 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.15 | Pursuing the establishment of the risk analysis system and executing PSA level 1 and 2 in the plant | Manager of management system and supervision / Deputy for Safety | 2016-03-19 | AI
1LF.1-1 | 1 | LF.1-1 | 1.16 | Performing the analysis trend of reliability of safety channels and safety equipment in terms of safety based on a list approved by chief engineer , safety deputy. | Manager of management system and supervision | 10/22/2015 Permanently(every quarter) | SAT
1LF.1-1 | 1 | LF.1-1 | 1.17 | сравнения показателей блока с наилучшей отраслевой практикой (бенчмаркинг) |  |  | SAT
1LF.1-1 | 1 | LF.1-1 | 1.18 | Developing procedure and executing the supervision on all of processes which are important in terms of safety | Manager of management system and supervision / Fuel and nuclear safety manager | 2015-11-21 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.19 | Preparing order for performing corrective measures in due time and taking necessary measures for more control on corrective measures and necessary solutions for more accountability of managements as for corrective measures. | Manager of management system and supervision | 2015-08-10 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.2 | Preparing software of event investigation and corrective measures bank. | Manager of management system and supervision / ICT manager | 2016-05-21 | AI
1LF.1-1 | 1 | LF.1-1 | 1.21 | Making it possible to record significant events on this software 1.20 | Manager of management system and supervision / ICT manager | 2017-06-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.22 | Preparing and executing the procedure of trending the analysis of defects on all the equipment and corrective measures for improvement. | Manager of management system and supervision / M&R planning manager | 2016-03-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.23 | Improvement in the managers monitoring system ( in three managerial levels) from working locations (equipment and staff) and also continuous monitoring how to remove the comments obtained from the visits ( including the development of checklist , qualitative analysis of the managers and evaluation of the precision and speed in executing the corrective measures). | Manager of management system and supervision / Head of Operating experiences group | 2016-03-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.24 | Developing and preparing the comprehensive program for decreasing the human error in NPPs ( methods of training and using the consultants). | Manager of management system and supervision / Head of Human resources and Training center | 2016-02-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.25 | Improvement in the maintenance and repairs system ( including developing the strategies and maintenance and repairs policy related to all the equipment and systems, record sustem related to monitoring the scheduled activities of the maintenance and repairs, improbement and simplification of the methods for the repairing the equipment, supervision and control on the performance of the contractors). | Manager of management system and supervision / Deputy for M&R | 2016-03-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.26 | Developing the exectuitve program of modernization for those equipment which udergo defect continuously in BNPP operation | Manager of management system and supervision / Deputy for engineering and technical support | 2016-03-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.27 | Improvement in the program of controlling the documents (revising and editing the working document). | Manager of management system and supervision / Deputy for engineering and technical support | 2016-01-20 | SAT
1LF.1-1 | 1 | LF.1-1 | 1 | Participation especially NPP managerial positions on bench marking and scientific visit in this area to other plants regarding 2016-17 interaction plan with WANO-MC. | Manager of management system and supervision / NPP Management | According to the program of interaction with WANO-MC for 2016-17 | SAT
1LF.1-1 | 1 | LF.1-1 | 1.29 | Holding Tchnical Support Missions about AFIs and organizing for formulating the corrective measures in relevant areas: methods for decision making, conservative decision-making). | Manager of management system and supervision / NPP Management | According to the program of interaction with WANO-MC for 2016-17 | SAT
|  |  | R.2 | AFI ОР.2-1 corrective measures - Corrective measures in the field of Operation area | Responsible entity Deputy for production | Deadline
2ОР.2-1 | 2 | ОР.2-1 | 2.1 | Performing technical training of all of the operator s in the field of operators communication, controlling the working parameters of equipment, switching , controlling each other’s work during switchings. | Head of Human Resources and Training Center | 2016-09-20 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.2 | Making changes in the job description of NPP shift supervisor , unit shift supervisor and shift supervisors of the managements in the issue of realizing a unitary management during technical working on the equipment including switchings in NPP MCR | Deputy for production, Turbine manager, Reactor manager, electricity manager, I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-03-19 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.3 | Providing technical briefing of operators of Reactor managerment and ventilation for using switching cards , checklists and operation procedures, receiving permit , reporting and control request by a superior official ( operation, technical –administrative management). (OP-06-OD-06) | Reactor manager, chiller and ventilation manager | 2016-03-19 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.4 | Technical training of emergency diesel operators (operation of diesel and related procedures). OP-06-OD-06 | Reactor manager / Head of Human resources and Training center | 2016-06-19 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.5 | Determining the working modes of ventilators UV61(62,63,64)D(002A, 002В,001А, 0015), UF61(62,63,64)S(002, 013, 007) (when putting them in a manual mode) and other ventilation equipment of buildings ZK1,2,3 and their valve ware. Developing technical order and making necessary changes in operating procedures. OP-06-OD-06 | Ventilation manager | 2016-03-19 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.6 | Durung exercise and training in simulator, it should be analyzed how to do operator communication , control of working parameters of equipment and control of each other’s work by instructors and they should be included in the report and evaluation of exerices and results. (OP-06-OD-06) | Head of Human resources and Training center / simulator manager | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.7 | Checklist of controlling condition of equipment of channels of safety system of emergency diesels buildings for using during visits and during periodical tests and after repairs. OP-06-OD-06 | Reactor manager | 2016-03-19 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.8 | In themes of periodical briefings of reactor operators, it should be added how to work under supervisor. OP-04-VG-02 | Reactor manager | 2016-03-19 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.9 | In the periodical briefing themes of Unit shift supervisor and NPP shift supervisor, it should be included how to work under supervisor. | Deputy for production | 2016-02-19 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.1 | In the monthly and periodical briefing themes of operators, it should be included how to do switching and operator’s communication. OP-04-VG-02 | Turbine manager, Reactor manager, Deputy for production, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-03-19 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.11 | Providing technical training of operators of production division, Reactor managerment, Turbine , electrical power, I&C , common systems, radiation safety and waste treatment workshop in the field of working with schedule , switchings and manner of work supervision. OP-04-VG-02 | Head of Human resources and Training center | 2016-09-20 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.12 | In the periodical briefing program of shift supervisors of plant and Unit , it should be included how to submit order for performing step-by-step operation during technological operation in accordance with working program. OP-04-VG-01 | Turbine manager, Reactor manager, production manager, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager | 2016-03-19 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.13 | Reviewing the existence of necessary requirements in technical ocuments which were producedin the field of presence of technical-administrative staff of managements during important switchnings and if necessary, making changes in documents. OP-04-VG-01 | Deputy for production | 2016-02-19 | FAR
2ОР.2-1 | 2 | ОР.2-1 | 2.14 | Developing the list of managements present in different switching. OP-04-VG-01 | Deputy for production | 2016-03-19 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.15 | In the periodical briefing program of operators of emergency diesels , it should be included how to do switching under supervision of a controller or by obtaining the permit of above-mentioed operator. OP-04-OD-07 | Reactor manager | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.16 | In the list of monthly briefing program of all the operators , it should be included how to do switching and how the communication of operators is done. OP-04-OD-07 | Deputy for production, Turbine manager, Reactor manager, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-03-09 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.17 | Technical training for all of the operators bout switching and operator’s communication should be held. OP-01-OD-02 | Head of Human resources and Training center | 2016-03-10 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.18 | Revising the list of necessary switching cards of all of managements ( an operation for which more than 3 switchnings should be done ). OP-01-OD-04 | Deputy for production, Turbine manager, Reactor manager, electricity manager , chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-06-19
2ОР.2-1 | 2 | ОР.2-1 | 2.19 | Giving technical briefing to executor of when technical service is done and also observing the requirements of switching cards and working programs. OP-01-OD-04 | Deputy for M&R | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.2 | Correcting the reulation of performing technical services of equipment about all of the articles of regulations of technical service and its checklist should be done step by step and also any step should be specified after being done. OP-04-OD-05 | Deputy for M&R | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.21 | Analyzing the working program of effiency test of permanent power feeding supply of emergency channels 1 to 4 of safety systems and in case of non-complinace with requirements of procedure 69.BU.1 0.0.FB.PRO.BNPP1338 , developing again the program. OP-04-OD-05 | I&C manager | 2016-02-09 | SAI
2ОР.2-1 | 2 | ОР.2-1 | 2.22 | Performing unplanned briefings of all staff of I&C management about not using the unapproved and invalid programs during works. OP-03-OD-04 | I&C manager | 2016-02-09 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.23 | Submitting letter to the designer AEP and posing the problem of lack of flow rate sensors in the outlet of pumps of middle cooling water system TF of safety channels 2 and 3 | Reactor managerment | 2016-03-10 | AI
2ОР.2-1 | 2 | ОР.2-1 | 2.24 | Preparing the method of calculating the total flow rate of systems TF in order to submit it in СВБУ. OP-03-OD-04 | I&C manager | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 |  |  | Reactor manager |  | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.25 | Making changes in operation procedure of system TF in issue: method of controlling flow rate in TF system , mentioning permissible flow rate in system and explanations about necessary measures when permissible values are deviated. OP-01-VG-06 | Reactor manager | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.26 | Briefing (issuing technical order) of the reactor shift supervisor, Turbine control engineer, Turbine supervisor , uint shift supervisor, and NPP shift supervisor about necessity of performing operator communications in Russian language in MCR. OP-01-VG-03 | Deputy for production / Reactor manager / Turbine manager | 2016-03-10 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.27 | Performing technical training of operator СЭ-production division, РО-Reactor managerment, ТО-Turbine management, ОВиК-chiller and ventilation management, АСУ-ТП-I&C management, ЭТО-electricity management, ООО-common systems management, ХС-chemistry manager, РБ-radiation safety management and СДРАО-waste treatment management about how to do operator communications and switchings and incuding this issue in the list of monthly briefings of these staff. OP-01-VG-05 | Deputy for production, Turbine manager, Reactor manager, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-05-09 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.28 | Briefing the operators of Reactor managerment (reactor shift supervisor and control engineer) during performing works simultaneously. OP-01-VG-05 | Reactor manager | 2016-05-09 | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.29 | Including the issue of how to switch during performing simultaneous works in the list of issues of monthly briefing and technical training of operators СЭ, РО, ТО, ОВиК, АСУ-ТП, ЭТО, ООО, ХС, РБ and СДРАО. OP-01-VG-05 | Turbine manager, Reactor manager, Deputy for production, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-05-09 | SAT
2ОР.2-1 | 2 | ОР.2-1 |  |  | Head of Human resources and Training center
|  |  | R. | AFI OF.1-1 corrective measures - Corrective measures in the field of Operation area | Responsible entity Deputy for production | Deadline
2OF.1-1 | 2 | OF.1-1 | 2.33 | Preparing notebook and order for reviewing all videocadres of working locations, РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО,ОРБ, ОЭО, in main control room and recording all of the defects and non-compliances. | I&C manager | 2016-02-08 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.34 | Reviewing all the videocadres of working locations РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО ,ОРБ, ОЭО in MCR and recording all the defects and non-complinaces including conditions of mechanisms, valves, violet color of parameters, lack of emergency and warning setpoints, inaccuracy of parameters shown, lack of compliance of warning signal and emergency signal with real value of parameter will be done in a separate notebook which will be prepared by I&C management. | Turbine manager, Reactor manager, electricity manager , I&C manager, chiller and ventilation manager | 2016-05-09 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.35 |  | I&C manager | 2016-06-09
2OF.1-1 | 2 | OF.1-1 | 2.36 | Holding a mutual meeting with I&C and equipment-owning manager in order to take decision about the remaining matters | Deputy for production | 2016-07-09 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.37 | Revising the setpoint of changing the color of hexagon sof fuel assemblies during increase of temperature in their outlet (currently when the temperature of water coming out of assemblies is more than 327 degree, the color of assemblies changes inro red considering the fact that the maximum outlet temperature of fuel assemblies is 335 ˚C when four pumps of primary circuit are operating. | I&C manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.38 | Revising the color change of setpoint color change of DNBR into red. Currently DNBR changes into less than 50 to red during reducing it. According to the operation regulation, reserve value of DNBR is at least 1.0 including its measurement error with reliability rate of 95% with the error of measurement parameters. | I&C manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.39 | reviewing whether it is possible to provide signal in videocadres СВРК during increase of parameters Nакз, QL, Кq, КL from permissible values by specifying the increase rate of every parameters for which relevant signal will be provided. OP-04-VG-04 | I&C manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.4 | It should be included in the program of briefing the personnel to monitor parameters ( in fragments of working locations) , record the defects and moving them. OP-03-VG-01 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , | 2016-04-08 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.41 | Reviewing all of the videocadres of working locations РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО in MCR and recording all the defects and non-compliances including the condition of mechanisms, valves , violet color of parameters, setpoints of announcing warning and emergency, inaccuracy of parameters, non-compliance of warning signal and emergency signal with actual value of parameters in a separate logbook which will be prepared by I&C management for it. | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-09 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.42 | Holding a mutual meeting with I&C after gathering and analysis in order to divide the defects. OP-03-VG-01 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.43 | Providing technical training and completing the issues of briefing the personnel about the performance of personnel when they receive signals and recording them and measures taken in operator logbook. OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-04-18 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.44 | Considering the procedure of staff reaction when they receive signal and checking the card for measures of personnel for all of the sign boards of MCR . OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.45 | Preparing logbook of signal boards which are constantly “on” and preparing technical order for addressing these signals in shift in order to remove the cause for the related boards which are “on” .OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.46 | Preparing technical order for making it obligatory to record the signals which are “on” during shift change in the operator logbook. OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.47 | Revising the shift acceptance and deliverychecklist of operating logbook in the field of adding item of signal boards which are “on” | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-04-18 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.48 | The issue of checking the parameters ( in fragments of working locations) , and recording the defects and removing them should be included in the program of briefing the staff. | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-02-09 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.49
2OF.1-1 | 2 | OF.1-1 | 2.5
2OF.1-1 | 2 | OF.1-1 | 2.51 | Considering whether it is possible or not to separate the tonality of warning sound signals from emergency ones and realizing it. OP-04-VG-03 | I&C manager | 2016-03-10 | AI
2OF.1-1 | 2 | OF.1-1 | 2.52 | Considering wheher it is possible to stabilize the blinking state of optical diods of pumps and valves in mimicking the MCR panel which comes into being when their power feeding circuit is in a separate condition . OP-03-OD-03 | I&C manager | 2016-03-10 | AI
2OF.1-1 | 2 | OF.1-1 | 2.53 | Considering whether it is possible to install placard ( with a text) on the button of valves and pumps in mimic panel . OP-03-OD-03 | I&C manager | 2016-05-19
2OF.1-1 | 2 | OF.1-1 | 2.54 | Checking all the boards and panels of MCR in terms of having Russian translation for all of the titles of signals (in case of existence of only English text, Russian translation should also be near the English text). OP-03-OD-05 | I&C manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.55 | Providing technical training and completing the issues of briefing personnel anbout what personnel should do during receiving signal and recording the signals and measures taken in operaroe logbook. OP-01-VG -10،OP-04-OD-01،OP-01-VG-09 | Reactor manager / Electricity manager / Turbine manager / Head of Human resources and Training center | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.56 | Reviewing the procedure of the staff reaction during receiving signal and checking the existence of card for measures taken by staff for all of the signal boards of MCR . OP-01-VG-10 ،OP-04-OD-01،OP-01-VG-09 | Reactor manager / Electricity manager / Turbine manager | 2016-03-10 | AI
2OF.1-1 | 2 | OF.1-1 | 2.57 | Preparing a logbook for signal boards which are constantly “on” and preparing technical order for addressing these signals in shift in order to remove the cause for related boards which are “on” . OP-01-VG-10،OP-04-OD-01، OP-01-VG-09 | Deputy for production | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.58 | Revising checklist of shift supervisor and delivery of operator logbook in the field of adding item of signal boards which are on,. OP-01-VG-10،OP-04-OD-01،OP-01-VG-09 | Deputy for production / Reactor manager / Electricity manager / Turbine manager | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.59 | Checking the manner of interaction among managements in order to remove the defects of equipment which are monitored from local panels. If the interactions are not cleartechnical order is developed to remove the defects of local panels , defects of equipment and necessary measures during receiving signal. OP-06-OD-07 | Reactor manager / Electricity manager / I&C manager / Deputy for engineering and technical support | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.6 | Determimning the interactions among all managements which have equipment which are monitored by local panels. OP-06-OD-07 | Deputy for engineering and technical support | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.61 | Providing the technical training for staff of reactor , electricity and I&C managements about how to remove defects in safety channels of emergency power supply. OP-06-OD-07 | Head of Human resources and Training center | 2016-03-20 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.62 | Preparing the procedure of measures of staff for the received signals in local panels of safety channels of emergency power. OP-06-OD-07 | Reactor manager, electricity manager , I&C manager, manager of process engineering | 2016-09-20 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.63 | Preparing the reaction card of staff for the received signals in local panels of safety channels of emergency power supply. OP-06-OD-07 | Reactor manager, electricity manager , I&C manager, manager of process engineering | 2016-10-21 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.64 | Preparing the defect logbook during scheduled repairs in different managements . | Equipment-owning managers | 2015-11-11 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.65 | .Revising the defect logbook in working lications in order to identify defects which cannot be identified for different reasons and should be transferred to defect logbook in order to remove them during scheduled repairs. | Equipment-owning managers | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.66 | Preparing the visit logbook with equal format in accordance with the requirements of management of planning and technical documents in all the equipment-owning with the following contents: ordinal No. of visit, date, time, shift, dfects observed, name and surname and signature, visitor and and initials of related manager. OP-02-OD-04 | Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.67 | Providing the manual of completing visit logbook . OP-02-OD-04 | Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.68 | Making changes in the document 90.BU.10.0.QAPOP.BNPP021 OP-02-OD-04 | manager of Process engineering | 2016-04-18 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.69 | Briefing all the operators with the issue of how to complete the visit logbooks and the logbooks for recording defect . | Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-04-18 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.7 | make visit to equipment and locations by operators such as exact visit to equipment of defect analysis , submitting and transferring defects to equipment-owning management and recording the defect in the subjects of periodic briefing of personnel which is repeated every three months. OP-03-OD-10 | Turbine manager, Reactor manager, Deputy for production, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.71 | In the program of preparing the local operators in training center , the issue of paying visit to equipment and locations should be included. OP-03-OD-10 | Head of Human resources and Training center | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.72 | Revising the switching cards and preparing them in accordance with the procedure 69.BU.1 0.00.AB.WI.ATEX.002. OP-01-VG-12 | Reactor manager | 2016-06-19 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.73 | Performing unplanned technical briefings by the reactor control engineer and reactor shift supervisor for recording the parameters of safety pumps during test in the logbook of safety-related important systems LGB-1300-1017 . | Reactor manager, electricity manager , I&C manager, Turbine manager, Chillness and ventilation manager , chemistry manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.74 | Making necessary changes in technical specifications related to controlling the level of oil of diesel generator bearings, making necessary changes in the visit checklist of emergency diesel by the local operator. OP-01-OD-13 | Reactor manager |  | SAT
2OF.1-1 | 2 | OF.1-1 | 2.75 | Investigating the necessity and possibility of controlling working parameters of equipment of all safety systems in locations. OP-03-OD-13 | Reactor managerr, Turbine manager, chiller and ventilation manager , | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.76 | Investigating the necessity and possibility of controlling working parameters of safety systems pumps in their locations. OP-03-OD-13 | Reactor manager | 2016-03-10 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.77 | Determining the controller who accompany diesel operator during performing the tests of emergency power channel . | Reactor manager | 2015-12-31 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.78 | Providing the technical training of reactor operator ( diesel operator ) with the subject of checking the working parameters of diesel in the monitors . OP-04-OD-08 | Reactor manager | 2015-12-31 | SAT
2OF.1-1 | 2 | OF.1-1 | 2.79 | Oil level in the volume of technical service of emergency diesel is checked via glass openings. | Reactor manager | 2015-12-31 | SAT
2OF.1-1 | 2 | OF.1-1 |  | Marking the glass openings which measure oil in order to monitor the amount of oil in crankcases of bearing.
2OF.1-1 | 2 | OF.1-1 |  | Recording the defect of openings which measure the oil of diesel of safety chaneel No. 3 . OP-01-OD-12
|  |  | R. | AFI OP.1-1 corrective measures - Corrective measures in the field of Operation area | Responsible entity Deputy for production | Deadline
2OP.1-1 | 2 | OP.1-1 | 2.8 | It is necessary for superior technical administrative staff to be present during important switching and managers should check the basic skills of operators which were mentioned in SOER 2013. | Equipment-owning managers | Permanently | SAT
2OP.1-1 | 2 | OP.1-1 | 2.81 | Preparing the list of important switchings in which the presence of superior technical administrative staff is necessary and submitting it to the senior process engineering management. | Reactor manager, Turbine manager, chemistry manager, ventilation manager, I&C manager | 2016-02-19 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.82 | Summing up and preparing the general switchings of BNPP and ordering it by the chief engineer to the sections of NPP. | Management of senior engineering of process | 2016-03-19 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.83 | Pursuing the preparation and approval of second revision ИЛА РУ,ТО, ЭО.(ИЛА: Instructions for Emergency Response, РУ-Reactor, ТО-Turbine, ЭО-Electricity, Equipments). | Deputy for engineering and technical support | 2016-09-20 | AI
2OP.1-1 | 2 | OP.1-1 | 2.84 | Updating ИЛА РУ,ТО, ЭО in accordance with the structure of documents which is used in Russian NPPs. ( provided in the technical support contract) | Deputy for engineering and technical support | 2017-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.85 | Determining the strategy of how to use the existing documents during accidents and disruptions . | Deputy for engineering and technical support | 2017-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.86 | Training personnel for how to use documents, providing training for how to exchange information, switching, and operators conversation. | Simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 |  |  |  | permanently | SAT
2OP.1-1 | 2 | OP.1-1 | 2.87 | Developing the controlling procedure of control physics. | Fuel and nuclear Safety manager | 2016-01-20 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.88 | Providing training for MCR personnel in tems of requirements mentioned in SOER 2013-2 “ cautionary decision making , reactivity management, permanent monitoring og parameters and regimes in MCR and work in the group”. | Head of Human resources and Training center | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 |  |  |  | Periodically in qualification maintenance programs | SAT
2OP.1-1 | 2 | OP.1-1 | 2.89 | Pursuing the establishment of SAM and procedures related to beyond-design and design-basis accidents . | Deputy for engineering and technical support | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.9 | Preparing procedure for making personnel use the fragment related to the amount of reserve water until the saturation temperature during heating and cooling the circuit and also in the cases which there is leakage in primary circuit. СРО-02-VGWTSV-01-01 | Reactor manager | 2016-02-20 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.91 | Providing training as for leakage from primary circuit to secondary circuit | Simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.92 | Providing training as for the performance of staff during radiation accidents in emergency drills related to organization of works should be evaluated. СРО-02-VGWTSV-01-03 | Head of Human resources and Training center / simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.93 | Reviewing the possibility of making sound signals for disconnecting the equipment of primary and secondary circuits and electrical equipment. | I&C manager | 2015-09-22 | SAT
2OP.1-1 | 2 | OP.1-1 |  | СРО-02-VGWTSV-01-04 |  |  | SAT
2OP.1-1 | 2 | OP.1-1 | 2.94 | Providng the list of equipment of primary and secondary circuits and electrical equipment in order to make sound signals. | Equipment-owning managers | 2015-10-23 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.95 | Providing training about the leakage from primary to secondary circuit ( deenergizingthe heaters КД. СРО-02-VGWTSV-05 | Simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.96 | Providing training in the field of sfaff performance after emergency outage. СРО-02-VGWTSV-01-06 | Simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.97 | Providing changes in the document instructions for emergency response ИЛА РУ и instructions for emergency response ИЛА ЭО as for the performance of staff in case of disconnection of 10-Kv busbars in normal operation. | Reactor manager / Electricity manager | 2016-01-01 | AI
2OP.1-1 | 2 | OP.1-1 | 2.98 | Preparing the scenario and tprviding training after making the changes . CPO-04-VGWTSV-11-06 | Simulator manager | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.99 | Making changes in the documents instructions for emergency response ИЛА TО related to the performance of staff in case of leakage or breakage of internal consumption collectors of NPP. | Turbine manager | 2016-01-01 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.1 | Preparing the scenario and tprviding training after making the change .CPO-04-VGWTSV-11-09 | Simulator manager | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.101 | -Providing the training for MCR staff for performing properly the requirements of procedure for donnecting and disconnecting . | Head of Human resources and Training center | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.102 | -Sending the connection and disconnection blanks to training center. | Equipment-owning managers | permanently | SAT
2OP.1-1 | 2 | OP.1-1 | 2.103 | -Using the connection and disconnection in the process of training with simulator. | Simulator manager | permanently | AI
2OP.1-1 | 2 | OP.1-1 | 2.104 | Providing training to Turbine shift staff about the performance of operator when the power of the Unit is decreasing . CPO-04-VGWTSV-11-11 | Simulator manager | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.105 | Providing the training for MCR staff for performing properly the requirements of procedure for donnecting and disconnecting during performing scenarios in simulator. | Simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.106 | sending the connection and disconnection to the training center. | Equipment-owning managers | permanently | SAT
2OP.1-1 | 2 | OP.1-1 | 2.107 | Using the connection and disconnection blanks in the process of training with simulator. СРО-02-VGWTSV-13 | Simulator manager | permanently | SAT
2OP.1-1 | 2 | OP.1-1 | 2.108 | Making changes in ИЛА РУ as for function of reactor operator after falling of control rod in the core, and also the performance of staff during bringing up the control rod from the core , | Reactor manager | 2016-03-01 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.109 | Preparing the scenario and providing training after making changes СРО-02-VGWTSV-07-1 | Simulator manager | 2016-07-01 | AI
2OP.1-1 | 2 | OP.1-1 | 2.11 | Providing training for evaluations of ОР СУЗ . СРО-02-VGWTSV-07-03 | Simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.111 | Briefing the MCR staff aas for using the proceures during changing reactivity , | Deputy for production | 2015-10-23 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.112 | Providing training for how to use АНФХ (album neutron physical characteristics). СРО-02-VGWTSV-07-04 | Fuel and nuclear safety manager / simulator manager | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.113 | Making changes ТРБЭ as for the prohibition of increasing the reactor power if the working position of reactor control rods is not in the position specified in Technical Specifications and in case of inefieciency of РОМ, ПЗ-1. СРО-02-VGWTSV-04-01 | Management of senior engineering of process | 2016-04-01 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.114 | Making change in ИЛА РУ as for performance of reactor operator after falling of control rod in the core and also the performance of staff during bringing up the control rod from the core CPO-04-VGWTSV-11-08 | Reactor manager | 2016-03-01 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.115 | making change in the procedure ТРБЭ for how should POM of the power of Y=Unit be limited in case of inefieciency. СРО-02-VGWTSV-03 | Management of senior engineering of process / Reactor manager | 2016-04-01 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.116 | Making change in the procedure ИЭ РУ as for how to decrease power on the siede of reactor ( injection of noron to primary circuit and shutting down APM and launching the Turbine monitoring system in РД mode.) СРО-02-VGWTSV-11 | Reactor manager | 2016-03-30 | AI
2OP.1-1 | 2 | OP.1-1 | 2.117 | Making changes in the procedure ИЛА РУ as for the description of small leakage grom primary circuit and impossibility of normally injecting water into primary circuit and performance of the staff in this condition | Reactor manager | 2016-03-30 | AI
2OP.1-1 | 2 | OP.1-1 | 2.118 | Making changes in the procedure ИЭ РУ about how to decrease the power from the reactor . | Management of senior engineering of process / Reactor manager | 2016-03-30 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.119 | Making change in the procedure ИЭ РУ as for decreasing the power on the side of reactor ( injecting boron to primary circuit and launching the Turbine monitoring system in the РД mode. CPO-04-VGWTSV-11-04 | Reactor manager | 2016-03-30 | AI
2OP.1-1 | 2 | OP.1-1 | 2.12 | Making change in the procedure ИЛА ЭО as for the performance of staff during disconnection of transformers and lack of performance of ABP busbars 10Kv and therefore losing the main equipment CPO-04-VGWTSV-11-07 | Reactor manager / electricity manager | 2016-06-01 | AI
2OP.1-1 | 2 | OP.1-1 | 2.121 | Making change in the procedure ТРБЭ, ИЭ РУ, ИЛА РУ as for explaining how to bring up the group УПЗ, CPO-04-VGWTSV-11-08. | Reactor manager / fuel and nuclear safety manager / Management of senior engineering of process | 2016-03-30 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.122 | Making changes ТРБЭ as for the prohibition of increasing the reactor power if the working position of reactor control rods is not in the position specified in Technical Specifications and in case of inefieciency of РОМ, ПЗ-1. | Management of senior engineering of process | 2016-04-01 | AI
2OP.1-1 | 2 | OP.1-1 |  | Training in simulator СРО-02-VGWTSV-04-03 | Simulator manager |  | SAT
2OP.1-1 | 2 | OP.1-1 | 2.123 | Providing training about taking the cautionary decisions СРО-02-VGWTSV-04-04 | Head of Human resources and Training center | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.124 | Providing training for Unit shift supervisor,Providing training about how to control the feeding condition of internal consumption CPO-04-VGWTSV-05 | Head of Human resources and Training center | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.125 | Providing traing for the staff about the necessaity of requirements of the operation conversation CPO-04-VGWTSV-01 | Head of Human resources and Training center | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.126 | Briefing the Unit shift supervisor as for how to perform operators conversation and submitting information to dispatcher of power grid in case of lack of presence of NPP shift supervisor. CPO-04-VGWTSV-01 | Head of Human resources and Training center | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 |  | Preparing a note about performance of the Unit shift supervisor about the operation conversations and submitting information to dispatcher of power grid in case of lack of presence of NPP shift supervisor, | Head of Human resources and Training center / Deputy for production | 2016-05-21 | AI
2OP.1-1 | 2 | OP.1-1 |  | Applying changes in the procedure of the manner of the operators conversations | Management of senior engineering of process | 2016-05-21 | AI
2OP.1-1 | 2 | OP.1-1 | 2.127 | Briefing the Unit shift supervisor as for how to perform operators conversation and submitting information to dispatcher of power grid in case of lack of presence of NPP shift supervisor. СРО-02-VGWTSV-09-03 | Deputy for production | 2016-03-10 | SAT
2OP.1-1 | 2 | OP.1-1 | 2.128 | Briefing the MCR staff as for necessity of providing proper and accurate information to superior managers ( operation and administration managers) СРО-02-VGWTSV-09-05 | Deputy for production / Reactor manager / Turbine manager |  | SAT
2OP.1-1 | 2 | OP.1-1 | 2.129 | Revising the requirements related to how to do purposeful briefings and also adding the requirement about the matter that Unit shift supervisor should brief all the staff in case of event of the Unit and especially in case of accident . CPO-04-VGWTSV-07 | Management of senior engineering of process | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.13 | Briefing the staff of MCR about the matter that issuing the order for opening the electrical schema of equipment rests with the Unit shift supervisor and the shift supervisors of managements can do it with the permit of the unit shift supervisor. CPO-04-VGWTSV-09 | Management of senior engineering of process | 2016-03-10 | AI
2OP.1-1 | 2 | OP.1-1 | 2.131 | Take into account both internal and external operating experience in the development of plans for training of operator personnel of control room in the FSS. | Deputy for production / Head of Human Resources and Training Center /Manager of management system and supervision (Head of Operating experiences group) | Done. 12/30/2015 | AI
|  |  | R.3 | AFI MA.2-1 Corrective measure - Corrective measures in the field of Maintenance and Repairs | Responsible entity Deputy for M&R | Deadline
3MA.2-1 | 3 | MA.2-1 | 3.1 | Submitting monthly report about development and execution of mechanical repair documents from contractor to manager of plant and M&R division. | Deputy for M&R / Planning and technical documents manager | September 17, 2015Permanently in every month | SAT
3MA.2-1 | 3 | MA.2-1 | 3.2 | Correspondence with NPPD about condition of M&R documents and pursuing unitl reaching the result. | Deputy for M&R / M&R manager | 2015-10-12 | SAT
3MA.2-1 | 3 | MA.2-1 |  |  | Deputy for M&R / / Electricity manager / I&C manager |  | SAT
3MA.2-1 | 3 | MA.2-1 | 3.3 | Preparing sechdeule of revising repair documents and submitting the program to M&R division. | Deputy for M&R / Manager of planning and technical documentataions | 2015-09-11 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.4 | Preparing the procedure of categorizing the repairs workers. | Deputy for M&R / Mechanical repairs manager | 2016-02-19 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.5 | Executimg the procedure of categorizing the repairs workers. | Deputy for M&R / | 2016-04-21 | AI
3MA.2-1 | 3 | MA.2-1 | 3.6 | Preparing, approving and executing checklist of technical service of rotary equipment based on the type of equipment. | Deputy for M&R / TAPNA rotary equipment repair manager | 2016-03-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.7 | Preparing, approving and executing checklist of technical service of static equipment based on the type of equipment. | Deputy for M&R / TAPNA static equipment repair manager | 2016-03-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.8 | Preparing, approving and executing checklist of technical service of ventilation equipment based on the type of equipment. | Deputy for M&R / TAPNA ventilation equipment repair manager | 2016-03-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.9 | Preparing, approving, and executing the checkislts of repairs which have nuclear hazard. | Deputy for M&R / Head of primary circuit equipment displacement | 2016-01-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.1 | Preparing, approving, and executing the checklists of technical services of electrical equipment. | Electricity manager | 2016-03-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.11 | Preparing, approving, and executing checklist of technical services of I&C equipment. | I&C manager | 2016-03-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.12 | Revising the M&R repair document based on the experiences reached during 3-year repairs. | Deputy for M&R / M&R manager / electricity manager / I&C manager | 2016-03-10 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.13 | Adding the article related to unplanned emergency repairs in the daily chart. МА-01-GI-02 | Deputy for M&R / M&R programming manager | 2015-09-11 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.14 | Cleaning the place of installing the equipment ZF.02.12-ZF.02.58, existence of metal covr of thermal insulation beside the repair people. | Turbine manager Ventilation manager | 2015-09-11 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.15 | Equipping the repair groups, preparing the containers particular for keeping alcohol, acetone, oil et cetra. (Facts: МА-02-GI-02 , MA-02-SP-04 , MA-01-SP-10) | Deputy for M&R | 2015-11-06 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.16 | Training the staff of repairs and observing the technical requirements of repair documents – job was not done in accordance with checklist of repairs. Valve was not manually assembled and disassembled according to the repair documents because of working mode of the system. МА-02-GI-03 | Deputy for M&R / TAPNA static equipments repairs manager | 2016-01-20 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.17 |  | Deputy for M&R / TAPNA rotary equipments repairs manager |  | SAT
3MA.2-1 | 3 | MA.2-1 | 3.18 |  | Reactor manager |  | SAT
3MA.2-1 | 3 | MA.2-1 | 3.19 | Revising and correcting the permits, briefing the staff . MA-01-SP-03 | Ventilation manager | 2016-01-20 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.2 | Revising how the permits are prepared- recording the conditions of safew work and personal protection equipment , briefing the staff. MA-01-SP-04 | Ventilation manager | 2016-01-20 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.21 | Training about how to fill the permits properly , there was no signature of ventilation shift supervisor in the permit 195, not briefing the staff.MA-01-SP-05 | Ventilation manager | 2016-01-20 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.22 | Providing technical training of ventilation repair group about how to use technical repair docuemnts. MA-01-SP-11 , MA-01-SP-07 | Head of ventilation repairs group | 2015-08-06 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.23 | Organizing and planning for performing simultaneously the current technical services of equipment ( electrical-mechanical). MA-01-SP-08 | M&R programming group | implemented | SAT
3MA.2-1 | 3 | MA.2-1 | 3.24 | Revising and correcting the forms and checklists related to repais of ventilation equipment. | Head of ventilation repairs group | 2015-10-07 | AI
3MA.2-1 | 3 | MA.2-1 | 3.25 | Providing training og operation experiences to repairman in order to prevent the defect of GY50D001 again , records of equipment in a management should be given to the repairs group at the beginning og repairs of one equipment. MA-03-SP-01 | Reactor manager | 2016-01-20 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.26 | Briefing the head of diesel repair group about organizing the repair activities in proportion with the volume of activities. | Deputy for M&R | 2015-09-11 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.27 | Revising and correcting the program of job planning СМ-78 about technicians passing practical training after finishing theoretical training – datek program and at the moment the comment has been removed.Updating the repair documents is the attachment of the table. МА-04- SP -04 | Head of human resources and training center | implemented | SAT
3MA.2-1 | 3 | MA.2-1 | 3.28 | Revising , root-finding and correcting the schedules of repair volumes – from 3331 activities scheduled , 1733 activity was performed and about %52 are nor yet done. Meanwhile, 576 unplanned activities have been done during repairs. On the basis of the grid request, the Unit was disconnected before the due time . The definite time of announcing the outage was not announced to TAPNA company until the last working operational day and this was because of lack of providing кд and lack of response of contractor in due time. The process of repair is a common process which includes spare parts for technical support and performing repairs and the implementation of program is depends on complete execution of all mentioned processes including preparation of conditions of equipment and systems for performing repairs, issuing repair permits, providing suitable spare parts, providing drawings and working documentset cetra. МА-04- SP -05 | Deputy for M&R | implemented | SAT
3MA.2-1 | 3 | MA.2-1 | 3.29 | Reviewing repair documents – results of analyzing the documents Руководстве при ремонте (68.BU.1.0.0.ABR.RTO.ETS033, 68.BU.1.0.0.ABR.RTO.ETS265, 68.BU.1.0.0.ABR. RTO.ETS079) shows that mentioned documents do not meet the requirements of procedure PRO-3150-04. MA-05-SP-01 | TAPNA engineering and technical manager | 2015-09-11 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.3 | periodically revise the M&R documents, the validity period was envisaged three years for M&R documentsand the first document should be revised periodically in Iranian year 1395. | TAPNA engineering and technical manager | Implemented under control | SAT
3MA.2-1 | 3 | MA.2-1 | 3.31 |  | Electricity manager / Commercial and equipment manager |  | AI
3MA.2-1 | 3 | MA.2-1 | 3.32 | Developing, revising, and registering the working documents , list of activities at the hand of execting personnel of repairs шкафа0,4кВ 10NN01H lack registration Number , are not approvedand their activity description is not relevant to mentioned equipment. Two different activites were recorded in the article 12. MA-02-SP-02 | Electricity manager | 2015-10-12 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.33 | Updating the working documents. In the attached drawing and inside the tableau шкафа, 0,4кВ 10NN01H and drawing of repair-executing people do not agree with each other. There are some crossed out items and corrections with pencil and pen and the documents have not been approved yet. MA-02-SP-03 | Electricity manager | 2015-10-12 | SAT
3MA.2-1 | 3 | MA.2-1 | 3.34 | Revising and updating rhe defect logbook of shift staff АСУ ТП. The review of logbook shows that there are 9 defects remaining from 2013. 34 defects remaining from 2014 have not been removed yet. ( All of the defects of 2013 were removed and considering the statement of contractor regarding the provision of spare parts for removing the mentioned defects until the end of overhaul 2015, the deadline for removing the remaining defects from 2014 is announced as 6 Dec. 2015 and 26 defects of the year 2014 (out of 34 defects ) has not been removed yet. | I&C manager | 2015-12-06 | SAT
|  |  | R.4 | AFI EN.1-1 Corrective measure - Corrective measures in the Technical Support and Engineering area | Responsible entity Deputy for technical and engineering | Deadline
4EN.1-1 | 4 | EN.1-1 | 4.1 | Preparing the procedure of visit and tend of analysis of system engineers from the related equipment and systems along with requirements ( including aim of the visit, period of visits, visit of deputies of management, and manager ; it is a requirement to consider the human resources, logbooks, requirement of preparing the checklist , information form, process of the defect report and pursuing them, checklist format, general checklist for visits, process of recording the results of visits, et cetera. ) | Deputy for technical and engineering / Manager of management system and supervision | 2016-04-22 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.2 4.3 4.4 4.5 4.6 | Preparing the exclusive procedure of visit and tend of analysis of system engineers from the equipment and system in the area of reactor equipments, Turbine equipments, chemistry equipments, common facilities equipments, ventilation equipments and | Reactor manager / Turbine manager / Chemistry manager / Manager of common facilities / Ventilation manager | 2016-02-29 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.7 | Preparing the procedure of visit and tend of analysis of system engineers from the equipment and system of I&C. | I&C manager | 2016-02-29 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.8 | Preparing the procedure of visit and tend of analysis of system engineers from the electrical equipment and systems. 4.8 | Electricity manager | 2016-02-29 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.9 | Preparing the format of data bank of monitoring equipment , systems and parameters , providing the conditions in order to record them in the internal network of NPP. 4.9 | Deputy for technical and engineering / ITC manager | 2016-03-19 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.10 4.11 4.12 4.13 4.14 | Preparing the list of parameters from reactor, Turbine, chemistry, common facilities, system which are needed to be monitored constantly and recording them in data bank and analyzing trend of changes and time period of trend analysis. | Turbine manager / Chemistry manager / Reactor manager / Ventilation manager / Common facilities manager | 2016-02-20 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.15 | Preparing the list of parameters from electrical system which are needed to be monitored constantly and recording them in data bank and analyzing trend of changes and time period of trend analysis. | Electricity manager | 2016-02-20 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.16 | Preparing the list of parameters from I&C system which are needed to be monitored constantly and recording them in data bank and analyzing trend of changes and time period of trend analysis. | I&C manager | 2016-02-20 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.17 | Preparing the procedure of evaluation of corrective measures and reviewing their effectiveness. | Head of operating experiences group | 2015-12-06 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.18 | Monitoring and analysis of effectiveness of corrective measures in order to evaluate corrective measures and avoiding the recurrence of accidents. | Manager of management system and supervision / Relevant managers | 3/19/2016 For the accidents which have occurred and after that permanently | AI
4EN.1-1 | 4 | EN.1-1 | 4.19 | In order to find root cause of accidents and determine exactly the root causes , also it is necessary to have specialist for methodology of investigate the accidents. | Head of Human resources and training center / Manager of management system and supervision | 2016-08-21 | FAR
4EN.1-1 | 4 | EN.1-1 | 4.12 | Organizing and executing the general training of methods of investigating the accidents for the staff who are involved in the analysis of defects and accidents. 4.20 | Head of Human resources and training center | 2016-12-21 | AI
4EN.1-1 | 4 | EN.1-1 | 4.14 | When choosing the operational control key parameters, consider requirements of Technological regulations, equipment certificates, technical conditions for the operation of the equipment and also operational experience. | Deputy for engineering and technical support | 2016-01-30 | SAT
4EN.1-1 | 4 | EN.1-1 | 4.15 | Develop a schedule for implementation of a unified database of equipment defects, defining milestones and specific timelines for each stage. | Deputy for engineering and technical support | Q3, 2016 | SAT
4EN.1-1 | 4 | EN.1-1 |  | • Сделать запрос через ВАО АЭС-МЦ о применяемых на других АЭС методах анализа состояния оборудования, анализа тенденций изменения ключевых эксплуатационных параметров, а также анализа дефектов оборудования. | Deputy for engineering and technical support | During 2016 | SAT
4EN.1-1 | 4 | EN.1-1 |  | · При выборе контролируемых ключевых эксплуатационных параметров руководствоваться требованиями Технологического Регламента, паспортов оборудования, технических условий на работу оборудования, а также эксплуатационным опытом. | Deputy for engineering and technical support | During 2016
4EN.1-1 | 4 | EN.1-1 |  | • Разработать план-график внедрения единой базы данных дефектов оборудования, определяющий основные этапы и конкретные сроки реализации каждого этапа. | Deputy for engineering and technical support | During 2016
|  |  | 4.17 | AFI CM.3-1 Corrective measure - Corrective measures in the Technical Support and Engineering area | Responsible entity Deputy for technical and engineering | Deadline
4CM.3-1 | 4 | CM.3-1 | 4.18 | Revising and making changes in the procedure of investigating the accidents in a way that the compliance of corrective measures before execution should be checked with requirements of FSAR and Technical Specification. It should not be written generally that the corrective measures do not agree with the requirement. The text and article of the given documents about the related system should be mentioned and then it should be concluded that the corrective measure has no non-compliance. 4.21 | Manager of management system and supervision | 2015-10-23 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.19 | Revising and making changes in the procedure of correction and improvement in equipment and systems in a way that before temporary or permanent improvement, the requesting management should submit the report which shows that the safety of plant is not affected and safety margin is protected. The basis of report is FSAR and Technical Specifications. 4.22 | Manager of the equipment and systems performance analysis | 2015-11-22 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.2 | Preparing the format of concentrated data bank of modernizations and obtaining the approval of deputies and chief engineer. 4.23 | Manager of the equipment and systems performance analysis | 2015-10-27 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.21 | Preparing the order for the process of registering, accounting the temporary changes in data bank and access of staff to the data bank. 4.24 | Manager of the equipment and systems performance analysis | 2016-01-20 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.22 | Completing the concentrated data bank of permanent modernizations including the corrections on the equipment and technical orders in a way that it would be the reference for all plant units in terms of temporary modernizations. 4.25 | Manager of the equipment and systems performance analysis / Manager of senior engineering of process / Equipment -owning managers | 2016-10-22 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.23 | Completing the concentrated data bank of improvements (modernizations) which are temporary including performing the corrections on the equipment and technical orders in a way that it would be a reference for all of the NPPs Units in terms of temporary modernizations . | Manager of the equipment and systems performance analysis | 2016-10-22 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.24 | TSM through the WANO-MC about applied at other plants about management practices and techniques for temporary modifications. | Deputy for engineering and technical support / Manager of the equipment and systems performance analysis | Done | SAT
4CM.3-1 | 4 | CM.3-1 | 4.25 | Identify and document the requirement for the maximum duration of temporary modifications - not more than 1 year or a fuel company. | Deputy for engineering and technical support / Manager of the equipment and systems performance analysis | Q1, 2016 | SAT
4CM.3-1 | 4 | CM.3-1 | 4.26 | Identify the persons responsible for the inclusion in the schedule of repairs, measures to eliminate temporary modifications. oblige responsibles to document the removal of temporary modifications after repairs. | Deputy for engineering and technical support / Manager of the equipment and systems performance analysis | 2016 | SAT
R.5
|  |  | 5.1 | AFI CY.1-1 Corrective Measures - Corrective measures in the field of Chemistry | Responsible Entity Chemistry manager | deadline
5CY.1-1 | 5 | CY.1-1 | 5.2 | Unplanned training was performed for Chemistry laboratory technicians in the field of main regulations of BNPP operation and the logbook of training with registration number LGB-1442-1951 should be registered and signed in the room of chemistry shift supervisor. | Chemistry manager / Chemistry Lab. Manager | 2015-10-12 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.3 | Locating three tables in places where it was necessary to put oxygen gauge in building ZF. They were designed and the requisites for manufacturing were provided and were delivered to workshop section. They have been manufactured and are transferred to the related places. | Chemistry manager | 2015-10-12 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.4 | Comparing the results of automatic and manual analysis for two months and submitting the report along with suggestions given to BNPP chief engineer in order to taking necessary decision | Chemistry manager | 2015-11-11 | AI
5CY.1-1 | 5 | CY.1-1 | 5.5 | Pursuing the removal of defects of automatic monitoring system of chemistry regimes of BNPP main circuits water. | I&C manager / Chemistry manager | 2016-09-10 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.6 | On the basis of analysis measurement procedure before sampling of secondary circuit for analyzing iron and copper , the route should be blown and drain completely. Manual and automatic sampling was performed for providing the blowing and draining the route in 6 separation points of line. | Chemistry manager | 2015-11-11 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.7 | The suitable table should be provided for correctly reading the graduated burette by operator of ZG.01. | Chemistry manager | 2015-09-21 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.8 | In order to provide clock in the location of sampling, purchase request should be given to logistic support management and the issue should be pursued. | Chemistry manager | 2015-09-21 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.9 | Additional cooler was requested for providing the temperature 250 C Celsius in laboratory environment and the issue should be pursued. | Chemistry manager | implemented | SAT
5CY.1-1 | 5 | CY.1-1 | 5.1 | In the program of the staff competence maintenance in the Iranian year ( beginning March 21, 2015), a training session about the defects raised in WANO peer review should be taken into account for day workers and shift workers and all of the staff should be briefed in this regard. | Chemistry manager | 2016-03-10 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.11 | Submission of request for complementary training in the area of chemistry and also determining the training subjects. | Chemistry manager | 2015-12-11 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.12 | Performing complementary training based on the requirements for chemistry staff with cooperation of chemistry management. | Head of Human resources and training center | 2016-09-10 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.13 | Preparing the briefing plan as for updating laboratory equipment and approving and enacting it in BNPP. | Chemistry manager | 2015-11-11 | AI
5CY.1-1 | 5 | CY.1-1 | 5.14 | Submission of list of necessary equipment to logistic support management based on the plan which has already been briefed and approved. | Chemistry manager | 2015-11-16 | AI
5CY.1-1 | 5 | CY.1-1 | 5.15 | Provision of equipment necessary for chemistry laboratory based on the required. | Commercial and equipment manager | 2016-09-10 | AI
5CY.1-1 | 5 | CY.1-1 | 5.16 | Developing explanatory note and approval of chemistry manager and installation in the related locations (laboratories). | Chemistry manager | 2016-03-10 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.17 | Provision of power switch and plug of laboratory hood in building ZC, room CO-844 with coordination with (power section) and was included in execution list. CY-01-SA-01 | Chemistry manager / Electricity manager | 2015-09-21 | SAT
5CY.1-1 | 5 | CY.1-1 | 5.18 | Safety label should be installed on all of the laboratory dishes. CY-01-SA-02 | Chemistry manager | implemeted | SAT
5CY.1-1 | 5 | CY.1-1 | 5.19 | The container of distilled water in ZC analysis laboratory was labeled.. CY-01-SA-03 | Chemistry manager | Implemented | SAT
5CY.1-1 | 5 | CY.1-1 | 5.2 | Registering the expiry date of chemical materials on chemical packages . CY-01-SA-04 | Chemistry manager | Permanently | SAT
5CY.1-1 | 5 | CY.1-1 | 5.21 | Procedure of determining the validity date of chemical materials was developed and approval of procedure. CY-01-SA-05. CY-01-SA-06 | Chemistry manager | 2015-12-21 | SAT
R.6
|  |  | 6.1 | AFI EP.2-1 Corrective Measures - Corrective Measures in the Field of Emergency Planning | Responsible Entity Manager of emergency planning | Deadline
6EP.2-1 | 6 | EP.2-1 | 6.2 | Issuing notification by the managing director for the responsible entity for severe accident management SAM in BNPP. | managing director/ Manager of management system and supervision | 2016-02-04 | SAT
6EP.2-1 | 6 | EP.2-1 | 6.3 | Preparing a plan for establishing SAM system with cooperation of the contractor and in accordance with technical support contract with contractor. | Manager of management system and supervision / Deputy for engineering and technical support | 2016-05-19 | AI
6EP.2-1 | 6 | EP.2-1 | 6.4 | Pursuing the provision of equipment related to SAM and emergency planning according to the plan which has already been approved by NPPD. | Deputy for engineering and technical support | 2016-05-19 | AI
6EP.2-1 | 6 | EP.2-1 | 6.5 | Pursuing the design and modernization necessary for using the provided equipment. | Deputy for engineering and technical support | 2016-06-19 | AI
6EP.2-1 | 6 | EP.2-1 | 6.6 | Pursuing the preparation of operation procedures, repairs and technical services for the equipment provided by NPPD. | Deputy for engineering and technical support | 2016-08-20 | AI
6EP.2-1 | 6 | EP.2-1 | 6.7 | Determining the responsible entities and owners of the equipment provided for mergency situations to be kept in ready-to-work mode. | Deputy for Safety / managing director | 2016-07-20 | SAT
6EP.2-1 | 6 | EP.2-1 |  | Preparing the requirements of reliable information system in emergnency. | ICT manager | 2016-03-10 | FAR
6EP.2-1 | 6 | EP.2-1 | 6.8 |  | Deputy for Safety / Managing director |  | FAR
6EP.2-1 | 6 | EP.2-1 | 6.9 | Pursuing and inquiring from nuclear protection and security office for permit and provision of reliable communication system in emergency. | ICT manager, Managing director | 2016-06-09 | FAR
6EP.2-1 | 6 | EP.2-1 | 6.1 | Pursuing for preparing and establishing reliable communication system during accident. | ICT manager | 2016-03-10 | FAR
6EP.2-1 | 6 | EP.2-1 |  | Preparing the plan of performing emergency drills especial for operational teams. | Deputy for M&R / M&R manager / TAPNA company | 2016-02-09 | SAT
6EP.2-1 | 6 | EP.2-1 | 6.11 |  | Manager of emergency planning |  | SAT
6EP.2-1 | 6 | EP.2-1 |  | Designating the training subjects of specialized teams of emergency operation. | M&R manager, TAPNA company, | 2016-10-21 | AI
6EP.2-1 | 6 | EP.2-1 |  |  | Manager of emergency planning, Head of Human resources and Training center |  | AI
6EP.2-1 | 6 | EP.2-1 | 6.12 |  | Head of Training and human resources center |  | AI
6EP.2-1 | 6 | EP.2-1 |  | Organizing and executing the training of specialized teams of emergency operation. | M&R manager, TAPNA company, | 2016-11-20 | AI
6EP.2-1 | 6 | EP.2-1 |  |  | Manager of emergency planning |  | AI
6EP.2-1 | 6 | EP.2-1 | 6.13 |  | Head of Training and human resources center |  | AI
6EP.2-1 | 6 | EP.2-1 | 6.14 | Revising the list of emergency equipment necessary in emergency and familiarity of personnel about how to use them. | Deputy for M&R | 2016-03-10 | AI
6EP.2-1 | 6 | EP.2-1 | 6.15 | Preparing the graph of inspection and technical service and checking the availability of equipment and instruments related to emergency operations teams. | Deputy for M&R | 2016-05-09 | SAT
6EP.2-1 | 6 | EP.2-1 | 6.16 | Inspecting Plan | Manager of management system and supervision | 2016-03-20 | AI
R.7
|  |  | 7.1 | AFI PI.2-1 Corrective measure - Corrective measures in the field of Performance Improvement | Responsible entity Head of Operating Experiences Group | Deadline
7PI.2-1 | 7 | PI.2-1 |  | Developing a complete software and the database to register all the domestic and foreign events and corrective measures. | Manager of management system and supervision | 2016-12-21 | AI
7PI.2-1 | 7 | PI.2-1 | 7.2 |  | ICT manager |  | AI
7PI.2-1 | 7 | PI.2-1 | 7.3 | Developing procedure for assessing corrective measures of reports of accident investigation. | Manager of management system and supervision / (Head of Operating experiences group) | 2015-09-21 | SAT
7PI.2-1 | 7 | PI.2-1 | 7.4 | Pursuing specialized training in the field of methods of investigating the accidents, the causes of accidents (direct and root cause) and training the correct method of developing and preparing reports of accident investigation for operation experiences group and the group for supervising the equipment and operation of management of supervision and management system and human resources and training center. | Manager of management system and supervision / Head of Human resources and training center | 2016-03-11 | FAR
7PI.2-1 | 7 | PI.2-1 |  | Analyzing the trending of near misses every 6 months. | Manager of management system and supervision / Head of Operating experiences group | From October 13, 2015 | SAT
7PI.2-1 | 7 | PI.2-1 | 7.5 |  |  | Permanently | SAT
7PI.2-1 | 7 | PI.2-1 | 7.6 | The proposed corrective measures and conclusion at the end of every self-assessment report and annual report was provided. | Manager of management system and supervision / Head of Operating experiences group | Permanently | SAT
7PI.2-1 | 7 | PI.2-1 | 7.7 | Developing procedure in the field of methods of analyzing and trending the reports of accident investigation ( Accidents, deviations, low level events, near miss) in NPP and also mentioning the details, format of report and how to develop it). | Manager of management system and supervision / Head of Operating experiences group | 2016-02-04 | SAT
7PI.2-1 | 7 | PI.2-1 | 7.8 | Making it possible to use psychological services in the committee of accidents investigation ( in all the cases which human error is the main cause of the accident) | Head of Human resources and training center | Permanently | AI
7PI.2-1 | 7 | PI.2-1 | 7.9 | In case of need to extend corrective measures of accident investigation reports in NPP in accordance with the procedure of accident investigation report in NPP (ATEX 863), submitting the causes of extending the time of performing corrective measures along with the approval of chief engineer of NPP one day before deadline for doing it for Operating experiences group. | Head of Operating experiences group / All of the managements of NPP | December 21, 2015 and Permanently control | AI
7PI.2-1 | 7 | PI.2-1 |  | Making it possible to record the backlog in the software of managing personnel performance by NPP relevant managers. | Head of Human resources and training center / ICT management | 2016-01-21 | SAT
7PI.2-1 | 7 | PI.2-1 | 7.1 | Performing corrective measures of accident investigation report (disruption, deviation, low level) which were not performed in due time or need time extension for different causes but nothing has been done for them yet . | Managers specified in the report | 2015-07-23 | AI
7PI.2-1 | 7 | PI.2-1 | 7.11 |  | Manager of management system and supervision (Head of Operating experiences group) | Q1 2016 | SAT
7PI.2-1 | 7 | PI.2-1 | 7.12
R.8
|  |  | 8.1 | AFI RP.3-1 Corrective measure - Corrective measures in the field of Radiation Safety | Responsible entity Radiation safety manager | Deadline
8RP.3-1 | 8 | RP.3-1 | 8.2 | Repair and necessary setting of КИД installed on the rooms and also preparing the chart of technical service and checking their efficiency. | Ventilation manager | July 20, 2016 and periodically according to the graff | SAT
8RP.3-1 | 8 | RP.3-1 | 8.3 | Preparing the checklist of visits of inspectors and radiation safety dosimeters and taking into account the monitoring of КИД hatches. In case of defect, informing the ventilation management and registering in operation logbook of radiation safety shift. | Radiation safety manager | 2015-09-21 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.4 | Inspecting the direction of air in locations and correcting cases in which the direction of air is from contaminated area to clean area. In order to prevent dissemination of radioactive material to cleaner areas, ventilation management should always take measures so that air direction would always be from radiation contaminated area to more contaminated area. | Ventilation manager | 2016-03-05 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.5 | Considering the direction of air movement in the checklist of dosimeter visits and staff of radiation safety management. In case of movement of air vice versa , the shifts should be informed and it should be recorded in the operation logbook of radiation safety shift. | Radiation safety manager | Permanently | SAT
8RP.3-1 | 8 | RP.3-1 | 8.6 | Briefing all the personnel about how to use СИЗ properly in controlled access area also taking necessary for using safety helmet in controlled access area and marking the necessary tools in controlled access area measures in order to prevent them from being removed from controlled access area. | Radiation safety manager / Occupational health and industrial safety manager / All BNPP managers | 2015-08-22 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.7 | Marking and coding all the repair tools used in the radiation controlled access area. | TAPNA company | 2015-09-21 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.8 | Optimizing the process of radiation monitoring of personnel and tools in in the exits of controlled access area and also equipping the radiation monitoring machines РЗБ-04-04 to entrance door in order to prevent the unauthorized exit of people and installing a set of UIM2-21 with its guidebook in the room 1ZC-09.22 in order to measure the arms and sides of people and also safety helmet. | Radiation safety manager | 2016-03-10 | AI
8RP.3-1 | 8 | RP.3-1 |  | Providing and installing the reserve sensor of radiation measurement of exit door of NPP , | Radiation safety manager | Done | SAT
8RP.3-1 | 8 | RP.3-1 | 8.9 | Installing the monitor which shows theses sensors are sound. |  |  | SAT
8RP.3-1 | 8 | RP.3-1 | 8.10 | Briefing the personnel about the monitoring radiation monitoring sensors in the exit of NPP | Radiation safety manager | Done | SAT
8RP.3-1 | 8 | RP.3-1 | 8.11 | Removing the defect of sensors which measure the radiation in exit door | Radiation safety manager | Done | SAT
8RP.3-1 | 8 | RP.3-1 | 8.12 | Sending letter to NPPD about the necessity of optimization (updating) the radiation contamination monitoring machines in the exit of controlled access area. In this letter, the suggestions of BNPP about removing the problems were also submitted to NPPD. | Radiation safety manager | 2015-09-21 | AI
8RP.3-1 | 8 | RP.3-1 | 8.13 | Preparing report from current status of radiation monitoring equipment existing in the system and equipment and sending to NPPD in order to [pursue the removal of defects. | Radiation safety manager | 2015-09-21 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.14 | Registering the equipment and spare parts necessary in the area of radiation safety from equipment and commercial management. | Radiation safety manager | 2015-09-21 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.15 | Providing the necessary spare parts and equipment in the area of radiation safety , submission of report of provision condition in a monthly basis to safety division and chief engineer of NPP about the provision of necessary equipment and spare parts. | Commercial and equipment manager | February 19, 2016 unitl the time of provision | FAR
8RP.3-1 | 8 | RP.3-1 | 8.16 | Briefing all the staff about how to use СИЗ properly , providing necessary measures for using the safety helmet by all the staff and making the tools which are used in the accidents. | Environmental monitoring laboratory manager | 2015-10-22 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.17 | Revising the training documents, time of training and reviewing the effectiveness of training in the area of radiation safety. | Head of Human resources and training center | 2016-06-19 | AI
8RP.3-1 | 8 | RP.3-1 | 8.18 | Briefing the managers and deputy managers in the area of radiation safety examinations. | Manager of management system and supervision | 2015-11-21 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.19 | Monitoring more the information in the field of radiation safety especially for staff who have toing and froing to controlled access area. | Head of Human resources and training center / Training committees | Permanently | AI
8RP.3-1 | 8 | RP.3-1 | 8.20 | Requesting and receiving the spare parts which are used more in the area of repairing the equipment of radiation monitoring and minimum maintenance in locations in order to repair the equipment in less time duration. | Radiation safety manager | 2016-05-19 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.21 | Preparing the requirements traning Sending letter to Manager of human resources and training center. | Radiation safety manager | 2016-01-20 | SAT
8RP.3-1 | 8 | RP.3-1 | 8.3 | Taking into account the radiation safety in the order issued by the manager of NPP in the area of program of staff competence. | Head of Human resources and training center | 2016-03-19 | SAT
R.
|  |  | 8.22 | AFI RP.4-1 Corrective measure - Corrective measures in the field of Radiation Safety | Responsible entity Radiation safety manager | Deadline
8RP.4-1 | 8 | RP.4-1 | 8.23 | Determining the location and suitable equipment of temporary sanitary path in Control Access Area of NPP in a way that it would be possible to separate clean and contaminated СИЗ with complete guide about how to use radiation contamination monitoring machine and two containers for clean and contaminated tools. | Radiation safety manager / Waste treatment workshop manager | 2016-03-19 | SAT
8RP.4-1 | 8 | RP.4-1 | 8.24 | Provision of rubbish bags in different colors for clean and contaminated wastes and preparing a guidebook how to use them and also briefing the staff as for separation of wastes and decreasing solid waste. | Waste treatment workshop manager / All of managers | 2015-08-22 | SAT
8RP.4-1 | 8 | RP.4-1 | 8.25 | Installing contamination monitoring machine in the exit of ZA in order to separate clean and contaminated СИЗ in the exit of reactor building in order to decrease solid waste. | Radiation safety manager | 2015-08-22 | SAT
8RP.4-1 | 8 | RP.4-1 |  | Determining the responsible entity for collecting the wastes in control access area and determining a clear procedure for collecting wastes in a way that no waste would be abandoned uncontrolled in the control access area. | Radiation safety manager, | 2016-02-19 | SAT
8RP.4-1 | 8 | RP.4-1 | 8.26 |  | Waste treatment workshop manager |  | SAT
8RP.4-1 | 8 | RP.4-1 | 8.27 | Checking the condition of radiation safety labels in control access area and removing the defects related to radiation safety labels. | Radiation safety manager | 2016-01-20 | SAT
8RP.4-1 | 8 | RP.4-1 |  | Preparing a manual about separating radioactive and non-radioactive wastes from wastes with different reactivity. | Waste treatment workshop manager | 2016-02-19 | SAT
8RP.4-1 | 8 | RP.4-1 | 8.28 |  | Radiation safety manager |  | SAT
8RP.4-1 | 8 | RP.4-1 | 8.29 | Preparing order for the location for collection rubbish and waste in control access area and receiving the approval of safety deputy and notification of chief engineer. | Waste treatment workshop manager / Radiation safety manager | 2016-02-14 | SAT
8RP.4-1 | 8 | RP.4-1 |  | Organizing the place of collecting according to the notification of chief engineer. | Waste treatment workshop manager | 2016-02-19 | SAT
R.9
|  |  | 9.1 | AFI HU.1-1 Corrective measures - Corrective measures in the field of Human Resources and Training | Responsible entity Head of Human resources and Training center | Deadline
9HU.1-1 | 9 | HU.1-1 | 9.2 | Preparing and submitting the draft of project called “prevention of incorrect performance of the staff” for independent deputies and managers. | Head of Human resources and training center | 2016-01-10 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.3 | Reviewing the draft of project and evaluating the activities and submitting the viewpoints related to this project (9.1) on each area. | All deputies and All Independent managers | 2016-02-10 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.4 | Reviewing the project, evaluating the activities and submitting the viewpoints related to services compensation, payment and welfare affairs to human resources and training center. | Deputy for support and development | 2016-02-10 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.5 | Reviewing and summing up the viewpoints of deputies and managers. | Head of Human resources and training center / Manager of management system and supervision | 2016-02-20 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.6 | Finalizing the order of the project “ prevention from the incorrect performance of staff”. | Head of Human resources and training center / Manager of management system and supervision | 2016-03-10 | AI
9HU.1-1 | 9 | HU.1-1 | 9.7 | Preparing and notifying the guide paper of managers in order to prevent the wrong performance of the staff. | Head of Human resources and training center | 2016-01-10 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.8 | Preparing and notifying the guide paper of staff in order to prevent the wrong performance of the staff. | Head of Human resources and training center | 2016-01-10 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.9 | Preparing training material for preventing the wrong performance of staff. | Head of Human resources and training center | 2016-01-20 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.1 | Including the method “prevention from wrong performance of staff” in the standard training program of jobs and executing it. | Head of Human resources and training center / training planning manager | 2016-06-19 | SAT
9HU.1-1 | 9 | HU.1-1 | 9.11 | Preparing the procedure “ instruments for decreasing the error of staff”. | Head of Human resources and training center | 2016-08-20 | AI
9HU.1-1 | 9 | HU.1-1 | 9.12 | Submitting the report of establishing and using the methods of decreasing error to human resources development management. | All of the executing managers of BNPP | 2016-09-20 | AI
9HU.1-1 | 9 | HU.1-1 | 9.13 | Including the supervision on using methods of decreasing error in inspection and supervision programs. | Manager of supervision and management system | 2015-10-21 | FAR
9HU.1-1 | 9 | HU.1-1 | 9.14 | Organizing and executing self-assessment in the field of using methods for decreasing error. | Head of Human resources and training center | 2016-12-20 | AI
R.
|  |  | 9.15 | AFI TR.1-1 Corrective measures - Corrective measures in the field of Human Resources and Training | Responsible entity Head of Human resources and Training center | Deadline
9TR.1-1 | 9 | TR.1-1 |  | List of all the non-complinces of MCR with FSS existing until mid-life repairs ( video-cadres, protection panels and blockings … ) were prepared and the process of modernization will be carried out according to plan. | BNPP Construction Project Manager / Operating Company / Human resources and Training center | 2016-09-20 | SAT
R0
توضیحات: رنگ سبز در ستون وضعیت: اقدام اصلاحی به نحو رضایتبخش انجام شده است. رنگ زرد در ستون وضعیت: اقدام اصلاحی کامل انجام نشده و در حال پیگیری است. رنگ قرمز در ستون وضعیت: اقدام اصلاحی بموقع یا بطور کامل انجام نشده یا نتایج اجرا رضایتبخش نبوده است و نیاز به توجه مجدد دارد. رنگ سفید یا بدون رنگ: موعد انجام اقدام و یا موعد بررسی وضعیت فرا نرسیده است.