Synopsis

This report consists of 91 pages with 38 tables.

Keywords: SPND; SPND sensitivity coefficients (changeover function coefficients); SPND current; fuel linear power; neutronic constants; transuranium elements.

This report provides: brief basic information on self-powered neutron detectors; computational technique applied to show how the neutron detector current correlates with power levels in the six fuel rods adjacent to the SPND; tables of sensitivity coefficients calculated proceeding from actual technical parameters of the ICID batch currently in operation; and tables of neutronic constants and transuranium elements for fuel assemblies operating within the 3nd fuel cycle at Unit 1 of the Bushehr NPP.

CONTENTS

Introduction	Error: Reference source not found

1Coefficients for the detector-indications-to-fuel-power changeover function	6

2 Neutronic constants	8

3 Transuranium concentration tables	9

Conclusion	10

Abbreviations	11

Referenses	12

Annex 1. Bushehr NPP fuel: Description of types and parameters	13

Annex 2. ICID structural data for the Bushehr NPP	17

Annex 3.Coefficients for SPND sensitivity computation functions	21

Annex 4. Neutronic constants for trhe ICIS	31

Annex 5. Tables of transuranium elements for the ICIS	85

Sheet registration changes	90

- Introduction

The 3 fuel cycle of Bushehr-1 implements the following types of fuel assemblies:

- 24 – unprofiled assemblies with 2.4% enrichment;

- 24_В36 – unprofiled assemblies with 2.4% enrichment that in the first cycle have burnt up with BARs – 0.036;

- 36 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%);

- 36В20 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%) with BARs – 0.020;

- 36В_20 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%) have burnt up with BARs – 0.020;

- 36В_36 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%) have burnt up with BARs – 0.036;

- 40 – assemblies with 4.1% enrichment profiled with 66 rods enriched to 3.7% (average enrichment 4%);

- 40 В20 – assemblies with 4.1% enrichment profiled with 66 rods enriched to 3.7% (average enrichment 4%) with BARs – 0.020;

- 16 – unprofiled assemblies with 1.6% enrichment.

Types and parameters of fuel assemblies are described in Annex 1.

For proper operation, the ICIS requires neutronic constants for the computational model of the reactor core and constants converting in-core neutron detector signals into linear power of fuel assemblies; the ICIS-M also requires tabulated data on transuranium concentrations depending on fuel burnup.

The Hortitsa-M software reconstructs in-core power – using fine and coarse meshes to interpolate neutron fields in assemblies with SPNDs and without SPNDs, respectively – on the basis of SPND indications only. Hence the correct interpretation of SPND indications (specifically the changeover function converting SPND current into linear power of fuel assemblies adjacent to this SPND) is critical for proper reconstruction of in-core power. Reliability degree of this information largely determines safe and economic reactor operation.

Table 1 and 2 of Annex 2 lists updated information on ICID structural components for Bushehr-1. Annex 3 contains tables of sensitivity coefficients. Annexes 4 and 5 respectively provide tables of neutronic constants and transuranium elements.

- coefficients for the detector-indications-to-fuel-power changeover function

At the Bushehr NPP, the VVER-1000 reactor core is monitored by 54 neutron detector assemblies containing 7 beta emission detectors (also known as self-powered neutron detectors or SPNDs) each. In functional terms, these detectors are transducers that include a sensitive part and a communication line. The sensitive part consists of a cylindrical emitter and a jacket that are insulated from each other. The emitter is made of rhodium, which is neutron-sensitive. In the rhodium emitter irradiated by neutrons, the neutron radiation capture reaction produces radioactive isotopes that decay and emit beta particles, or electrons. These electrons pass through the insulator and reach the jacket, thus producing electric current (activation component) proportional to the neutron flux density in the emitter circuit. Interaction of gamma rays (yielded by neutron radiation capture) with the emitter produces Compton and photo electrons. The current produced by this process (i.e. its instantaneous component) is also proportional to the neutron flux density. The detector current depends on in-core detector operation time (due to burnup of the neutron-sensitive material – rhodium) and on the neutron spectrum. On the detector positioning spot, the neutron spectrum depends on: fuel assembly type and burnup; water density; boron concentration in water; and specific power.

In the improved ICIS-M of the Bushehr NPP, the linear power of fuel assemblies on SPND positioning spots is calculated as follows:

Ql=S⋅MF(Y)⋅Je

where:

Ql – linear power of fuel assembly;

S – function describing the changeover from the detector emitter current to the average power of 6 rods surrounding the detector;

M – amount of rods per assembly;

F(Y) – the function which describes SPND burnup;

Y – integral emitter current over the detector operation period;

Je – emitter current.

The changeover function, S, depends on SPND and fuel assembly parameters, as well as on core status parameters, and is presented as a function with coefficients yielded by respective approximation of a set of changeover function values associated with different parameters of fuel assemblies and reactor core. For the ICIS-M of VVER-1000 operating at the Bushehr NPP, the changeover function has the following form:

S=P1⋅1+P2 W+P3 W2+P4 W3+P5 W4⋅1+P61+P7 W⋅G−Gо×1+P8 1+P9 W⋅C−Cо⋅1+P10+P11 WQQ0−1⋅1+P12N−4×1+P13 Wp+P14W−WpWpL0Kc+1+P15+P16 Wp+P17 Wp2⋅LBKcB+1+P18+P19 Wp+P20 Wp2⋅LDyKcDy

where P1...P20	– approximation coefficients;

W     	 – current fuel burnup;

– fuel burnup with absorber (CPS control assembly) introduced;

G, 	– current and reference water density;

C, 	 – current and reference concentration of natural boron in water;

Q,  	– current and reference specific power;

N 		– assembly-lengthwise detector number,

L0 		– detector section uncovered by the absorber (CPS assembly);

LB		– detector section covered by the boron part of the CPS assembly;

LDy  	–  detector section covered by the dysprosium part of the CPS assembly;

– load factor for rods surrounding the detector tube in an assembly (without accounting for CPS assembly insertion); is calculated by fine-mesh code with account of actual surroundings of this assembly in the reactor core;

– load factor for rods surrounding the detector tube in an assembly; is calculated with account of CPS assembly’s boron part insertion;

– load factor for rods surrounding the detector tube in an assembly; is calculated with account of CPS assembly’s dysprosium part insertion.

Reference values of water density, boron concentration and specific power correspond to those used in computations of approximation coefficients.

Power computations based on SPND indications currently use – for rods surrounding the ICID – the load factors calculated without accounting for ICID presence in the instrumentation tube. In such a case, proceeding from the equality

S(for Kc with NFMC)/Kc(with NFMC) = S(for Kc with Н2О)/Kc(with Н2О),

the changeover function can be calculated as follows:

S(for Kc with Н2О) = S(for Kc with NFMC)Kc(with Н2О)/Kc(with NFMC).

Tables 1–10 of Annex 3 list the changeover function coefficients to be used together with load factors for rods surrounding the SPND (both with and without the ICID). Arrays of changeover function values associated with various fuel assembly and core parameters were calculated by the TVS-M [1] – a spectral code intended for computation of neutronic parameters of fuel assembly cells.

It should be noted that, besides specific technical parameters of each ICID batch, computations of sensitivity factors also accounted for the history of BAR presence in fuel assemblies. Consequently – in contrast to neutronic constants that are divided into two groups and to transuranium elements that do not depend on BARs – each type of fuel assemblies within a given core is actually divided into three groups (fuel assemblies that has contained BARs before; fuel assemblies that has never contained BARs; and fuel assemblies that are containing BARs in the current cycle).

The SPND burnup is accounted for by the following function:

F(Y) =1-ET*Y + ET2*Y ^2

For d = 0.0481 cm, Ldpz = 25.4 cm:   ET  =   2.698E-03, ET2  =  -3.709E-06,

where d and Ldpz are the diameter and the length (the neutron-sensitive part of SPND).

# neutronic constants

To reconstruct the in-core power field, the ICIS uses the discrete solution of the neutron diffusion equation and also neutronic constants same as those used in the BIPR-7A – a 3D / two-group / coarse-mesh / neutron diffusion software code. These neutronic constants were calculated by the TVS-M [1] – a spectral code intended for computation of neutronic parameters of fuel assembly cells.

To reduce the neutronic constant approximation error, the current ICIS software version uses the maximum array of fuel burnup points.

Fuel mass in the ICIS software should be preset in accordance with the grade of fuel loaded into the core.

Tables 1–2 list: reference coolant parameters the computations of neutronic constants were based on, and fuel temperatures depending on specific power in the computational prism, respectively. Reference parameters of each type of fuel assemblies can differ from each other. The coolant density of the heat carrier is given without regard to boric acid.

Table 1 - Reference coolant parameters for neutronic constants

| Parameter | Value |
| --- | --- |
| Coolant temperature, K | 579 |
| Coolant density, g/cm3 | 0.7161 |

Table 2 - Fuel temperatures depending on specific power in the computational prism

| Specific power, kW/cm3 | Fuel temperature, K |
| --- | --- |
| 0 | 575 |
| 50 | 756 |
| 100 | 924 |
| 150 | 1084 |
| 200 | 1236 |
| 250 | 1379 |
| 300 | 1511 |
| 350 | 1627 |

Tables 1–14 of Annex 4 list neutronic constants in standard form required for their input in the ICIS.

# transuranium concentration tables

For proper operation, the ICIS requires tables of concentrations of transuranium elements depending on fuel burnup.

Tables 1–4 of Annex 5 contain concentrations (in atomic density units, 1024 cm-3) of transuranium elements in fuel assembly depending on fuel burnup (MWd/kgU).

The concentrations of transuranic elements in fuel assembly are calculated taking into account lack of gaps between a fuel tablet and a cover, without the central opening in tablets and gaps between them.

- conclusion

The ICIS constants library was prepared for the following types of fuel assemblies operating within the 3 fuel cycle at Bushehr-1:

- 24 – unprofiled assemblies with 2.4% enrichment;

- 24_В36 – unprofiled assemblies with 2.4% enrichment that in the first cycle have burnt up with BARs – 0.036;

- 36 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%);

- 36В20 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%) with BARs – 0.020;

- 36В_20 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%) have burnt up with BARs – 0.020;

- 36В_36 – assemblies with 3.7% enrichment profiled with 66 rods enriched to 3.3% (average enrichment 3.62%) have burnt up with BARs – 0.036;

- 40 – assemblies with 4.1% enrichment profiled with 66 rods enriched to 3.7% (average enrichment 4%);

- 40 В20 – assemblies with 4.1% enrichment profiled with 66 rods enriched to 3.7% (average enrichment 4%) with BARs – 0.020;

- 16 – unprofiled assemblies with 1.6% enrichment

SPND sensitivity factors, neutronic constants and concentrations of transuranium elements were also calculated.

- abbreviations

| BAR | Burnable Absorber Rod |
| --- | --- |
| CPS | Control & Protection System |
| FA | Fuel Assembly |
| GFP | Gaseous Fission Product |
| ICID | In-Core Instrumentation Detectors |
| ICIS | In-Core Instrumentation System |
| ICIS-M | Modernized (improved) ICIS |
| NFMC | Neutron Flux Measuring Channel |
| NPP | Nuclear Power Plant |
| SPND | Self-Powered Neutron Detector |

- references

- V.D. Sidorenko, A.P. Lazarenko, S.N. Bolshagin, V.M. Tsvetkov. TVS-M Software Package (Version 1.4) Software Qualification Certificate # 239 of 23.09.2008; NRC KI software registration # 611 of 31.07.2006.

Annex 1

Bushehr NPP fuel:

Description of types and parameters

Table 1

Parameters of fuel assemblies

| Parameter, dimension | Value |
| --- | --- |
| Positioning of fuel rods | triangular mesh |
| Rods per assembly, pcs. | 311 |
| Pitch between rods, m | 12.7510-3 |
| Nominal turnkey size, m | 0.234 |
| Amount of guide channels, pcs. | 18 |
| Guide channel material | Zr+1%Nb alloy |
| External diameter of guide channel, m | 13.010-3 |
| Internal diameter of guide channel, m | 11.010-3 |
| Spacers per assembly, pcs. | 15 |
| Spacer material | Zr+1%Nb alloy |
| Spacer weight, kg | 0.55 |
| Amount of measuring channels, pcs. | 1 |
| Measuring channel material | Zr+1%Nb alloy |
| External diameter of measuring channel, m | 13.010-3 |
| Internal diameter of measuring channel, m | 11.010-3 |
| Central tube material | Zr+1%Nb alloy |
| External diameter of central tube, m | 13.010-3 |
| Internal diameter of central tube, m | 11.010-3 |

Table 2

Parameters of fuel rods

| Parameter, dimension | Value |
| --- | --- |
| Fuel pellet material | Uranium dioxide (UO2) |
| UO2 weight, kg | 1.575 |
| Cladding material | Zr+1%Nb alloy |
| External diameter of cladding, m | 9.110-3 |
| Internal diameter of cladding, m | 7.7310-3 |
| Fuel column height in cold state, m | 3.53 |
| Initial helium pressure within the cladding, MPa | 2.0 |
| External diameter of fuel pellet, m | 7.5710-3 |
| Fuel pellet height, m | 1110-3 |
| Fuel pellet central hole diameter, m | 1.510-3 |
| Fuel pellet density, kg/m3 | (10.410.7)103 |
| Length (height) of GFP plenum, m | 0.248 |
| Rod retainer material | ЭК 173 ИД |

Table 3

Parameters of CPS control assemblies

| Parameter, dimension | Value |
| --- | --- |
| Absorber rods per control assembly, pcs. | 18 |
| Absorber material – top section – bottom section | B4C Dy2O3+TiO2 |
| Absorber column height, m – total – top section – bottom section | 3.55 3.2 0.3 |
| Minimal absorber density, kg/m3 – top section (B4C) – bottom section (Dy2O3+TiO2) | 1.7103 4.9103 |
| External diameter of absorber rod cladding, m | 8.210-3 |
| Absorber rod cladding thickness, m | 0.510-3 |
| Absorber rod cladding material | 46ХНМУ |

Table 4

Parameters of ICID bundle

| Parameter, dimension | Value |
| --- | --- |
| ICIDs per bundle, pcs. | 18 |
| External diameter of ICID, m | 9.110-3 |
| ICID cladding material | Zr+1%Nb alloy |
| Absorber material | CrB2+Al |
| Absorber column height, m | 3.55 |
| Minimal absorber density, kg/m3 | 2.8103 |
| Natural boron content in absorber material, kg/m3 | from 0.020103 to 0.065103 |

Table 5

Types of fuel assemblies used in the 3 fuel cycle

| FA type | Average enrichment [U-235 wt%] | Amount and enrichment of different rod types in a FA [U-235 wt%] |  | Amount of ICIDs/ Natural boron content in ICID, g/cm3 |
| --- | --- | --- | --- | --- |
|  |  | Type 1 | Type 2 |  |
| 36 | 3.62 | 245 / 3.7 | 66/3.3 | – – – 18 / 0.020 18 / 0.036 |
| 16 | 1.60 | 311 / 1.6 | – |  |
| 24 | 2.40 | 311 / 2.4 | – |  |
| 40 | 4.0 | 245 / 4.1 | 66/3.7 |  |
| 40B20 | 4.0 | 245 / 4.1 | 66/3.7 |  |
| 36B20 | 3.62 | 245 / 3.7 | 66/3.3 |  |

Figure 1 – Core map and types of fuel assemblies in the 3 fuel cycle

Annex 2

ICID structural data for the Bushehr NPP

Table 1

Data on ICID structure for Bushehr-1

| Structural component | Element of structural component | Parameter | Value |
| --- | --- | --- | --- |
| Emitter | Emitter, rhodium (GOST 19351-74 standard) | Diameter, mm | 0.483 |
|  |  | Material | min. 99.9% of Rh |
|  |  | Isotopic composition | natural |
|  |  | Length, mm | 246 |
|  |  | Weight (mass), g | 0.5601±0.0018 |
| Insulator | Insulator | External diameter, mm | 1.05±0.01 |
|  |  | Internal diameter, mm | 0.75±0.01 |
|  |  | Material | min. 99.7% of SiO2 |
|  |  | Wall thickness, mm | 0.15±0.01 |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | 2.22 |
| Collector | Collector tube (GOST 14162-79) | External diameter, mm | 1.5±0.03 |
|  |  | Wall thickness, mm | 0.1 -0.02+0.03 |
|  |  | Material | ХН78Т |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | 8.35 |
| Shielding | Band sector (GOST 4986-79) | Thickness, mm | 0.5 -0.07 |
|  |  | Material | 12Х18Н10Т |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | 7.9 |
| Detector cable (ТУ16.К03.10-89 standard) | Sheath | External diameter, mm | 1.0±0.04 |
|  |  | Thickness, mm | 0.15 -0.05 |
|  |  | Material | 12Х18Н10Т |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | 7.9 |
|  | Conductor | Diameter, mm | 0.2±0.05 |
|  |  | Material | ХН78Т |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | 8.35 |
|  | Insulator | Material | min. 99% of MgO |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | MgO –2.65 |
| Filler | ICID filler | Substance | He |
|  |  | Isotopic composition | natural |
|  |  | Density, g/cm3 | 1.8∙10-4 |

Table 2

Data on ICID structure for Bushehr-1, delivery 2013.

| Structural component | Element of structural component | Parameter | Value |
| --- | --- | --- | --- |
| № 134001…№ 134046 |  |  |  |
| Emitter | Emitter, rhodium (GOST 19351-74 standard) | Diameter, mm | 0.480 - 0.483 |
|  |  | Material | min. 99.9% of Rh |
|  |  | Length, mm | 246.1 - 247.9 |
|  |  | Weight (mass), g | 0.5529 - 0.5654 |
| Insulator | Insulator | External diameter, mm | 1.1 ± 0.01 |
|  |  | Material | min. 99.8% of SiO2 |
|  |  | Wall thickness, mm | 0.160 - 0.185 |
|  |  | Density, g/cm3 | 2.22 |
| Collector | Collector tube (GOST 14162-79) | External diameter, mm | 1.5 ± 0.03 |
|  |  | Wall thickness, mm | 0.1 -0.02+0.03 |
|  |  | Material | 12Х18Н10Т |
|  |  | Density, g/cm3 | 7.9 |
| Shielding | Band sector (GOST 4986-79) | Thickness, mm | 0.5 -0.07 |
|  |  | Material | 12Х18Н10Т |
|  |  | Density, g/cm3 | 7.9 |
| Detector cable (ТУ16.К03.10-89 standard)детектора, по ТУ16.К03.10-89 | Sheath | External diameter, mm | 1.0 ± 0.01 |
|  |  | Thickness, mm | 0.14 - 0.16 |
|  |  | Material | 12Х18Н10Т |
|  |  | Density, g/cm3 | 7.9 |
|  | Conductor | Diameter, mm | 0.21 - 0.23 |
|  |  | Material | Inkonel 600 |
|  |  | плотность, гсм-3 | 8.4 |
|  | Insulator | Material | Al2O3– 99.6 % |
|  |  | Density, g/cm3 | 2.5 |
| Filler | ICID filler | Substance | He |
|  |  | Density, g/cm3 | 1.8∙10-4 |
| №134101…№13104 |  |  |  |
| Emitter | Emitter, rhodium (GOST 19351-74 standard) | Diameter, mm | 0.481 |
|  |  | Material | min. 99.9% of Rh |
|  |  | Length, mm | 246.6 - 246.7 |
|  |  | Weight (mass), g | 0.5565 - 0.5572 |
| Insulator | Insulator | External diameter, mm | 1.1 ± 0.01 |
|  |  | Material | min. 99.8% of SiO2 |
|  |  | Wall thickness, mm | 0.165 - 0.170 |
|  |  | Density, g/cm3 | 2.22 |
| №134201…№134204 |  |  |  |
| Эмиттер | Emitter, rhodium (GOST 19351-74 standard) | Diameter, mm | 0.481 - 0.482 |
|  |  | Material | min. 99.9% of Rh |
|  |  | Length, mm | 246.2 до 246.5 |
|  |  | Weight (mass), g | 0.5570 - 0.5578 |
| Insulator | Insulator | External diameter, mm | 1.1 ± 0.01 |
|  |  | Material | min. 99.8% of SiO2 |
|  |  | Wall thickness, mm | 0.165 - 0.170 |
|  |  | Density, g/cm3 | 2.22 |

Annex 3

Coefficients for SPND sensitivity computation functions

Table 1

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 16 kl-BDy 1.6% (311*1.6%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

1.6601E-03	1.7149E-03	Р1

2.3283E-02	2.1753E-02	Р2

-2.4397E-03	-2.4102E-03	Р3

8.8461E-05	8.8703E-05	Р4

-1.1350E-06	-1.1446E-06	Р5

1.8365E-04	1.8365E-04	Р6

-1.9089E-01	-1.9089E-01	Р7

-2.2528E-02	-2.2528E-02	Р8

-2.9639E-02	-2.9639E-02	Р9

-7.0902E-03	-7.0902E-03	Р10

1.2979E-03	1.2979E-03	Р11

9.8500E-04	9.8500E-04	Р12

2.1780E-02	2.1780E-02	Р13

-6.3251E-04	-6.3251E-04	Р14

-5.0749E-02	-5.0749E-02	Р15

2.3682E-02	2.3682E-02	Р16

-3.3452E-04	-3.3452E-04	Р17

-6.3721E-02	-6.3721E-02	Р18

1.8148E-02	1.8148E-02	Р19

-2.0007E-04	-2.0007E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 2

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 24 kl-BDy 2.4% (311*2.4%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

2.2546E-03	2.3323E-03	Р1

5.8059E-03	4.6441E-03	Р2

-9.1433E-04	-8.9762E-04	Р3

2.5046E-05	2.5154E-05	Р4

-2.3034E-07	-2.3317E-07	Р5

2.6668E-04	2.6668E-04	Р6

-1.1244E-01	-1.1244E-01	Р7

-2.2609E-02	-2.2609E-02	Р8

-1.6223E-02	-1.6223E-02	Р9

-5.9060E-03	-5.9060E-03	Р10

9.8678E-04	9.8678E-04	Р11

9.8500E-04	9.8500E-04	Р12

1.3684E-02	1.3684E-02	Р13

-2.4473E-04	-2.4473E-04	Р14

-5.9208E-02	-5.9208E-02	Р15

1.2899E-02	1.2899E-02	Р16

4.8010E-05	4.8010E-05	Р17

-6.9923E-02	-6.9923E-02	Р18

9.4609E-03	9.4609E-03	Р19

1.1048E-04	1.1048E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 3

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 24_B36  2.4% (311*2.4%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

2.2546E-03	2.3323E-03	Р1

5.8059E-03	4.6441E-03	Р2

-9.1433E-04	-8.9762E-04	Р3

2.5046E-05	2.5154E-05	Р4

-2.3034E-07	-2.3317E-07	Р5

2.6668E-04	2.6668E-04	Р6

-1.1244E-01	-1.1244E-01	Р7

-2.2609E-02	-2.2609E-02	Р8

-1.6223E-02	-1.6223E-02	Р9

-5.9060E-03	-5.9060E-03	Р10

9.8678E-04	9.8678E-04	Р11

9.8500E-04	9.8500E-04	Р12

3.8449E-03	3.8449E-03	Р13

-7.9018E-05	-7.9018E-05	Р14

-5.9208E-02	-5.9208E-02	Р15

1.2899E-02	1.2899E-02	Р16

4.8010E-05	4.8010E-05	Р17

-6.9923E-02	-6.9923E-02	Р18

9.4609E-03	9.4609E-03	Р19

1.1048E-04	1.1048E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 4

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 36 kl-BDy 3.62% (245*3.7%+66*3.3%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

3.0665E-03	3.1747E-03	Р1

-1.4040E-03	-2.0564E-03	Р2

-3.0870E-04	-3.1146E-04	Р3

5.6702E-06	5.9136E-06	Р4

-3.1992E-08	-3.3671E-08	Р5

3.3466E-04	3.3466E-04	Р6

-6.9863E-02	-6.9863E-02	Р7

-2.1938E-02	-2.1938E-02	Р8

-1.2988E-02	-1.2988E-02	Р9

-6.2028E-03	-6.2028E-03	Р10

7.6058E-04	7.6058E-04	Р11

9.8500E-04	9.8500E-04	Р12

7.4386E-03	7.4386E-03	Р13

-6.5675E-05	-6.5675E-05	Р14

-5.5348E-02	-5.5348E-02	Р15

4.4465E-03	4.4465E-03	Р16

2.5281E-04	2.5281E-04	Р17

-6.6472E-02	-6.6472E-02	Р18

2.9322E-03	2.9322E-03	Р19

2.5103E-04	2.5103E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 5

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 362B20 3.62% (245*3.7%+66*3.3%) SVP0.02 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

3.0665E-03	3.1747E-03	Р1

-1.4040E-03	-2.0564E-03	Р2

-3.0870E-04	-3.1146E-04	Р3

5.6702E-06	5.9136E-06	Р4

-3.1992E-08	-3.3671E-08	Р5

3.3466E-04	3.3466E-04	Р6

-6.9863E-02	-6.9863E-02	Р7

-2.1938E-02	-2.1938E-02	Р8

-1.2988E-02	-1.2988E-02	Р9

-6.2028E-03	-6.2028E-03	Р10

7.6058E-04	7.6058E-04	Р11

9.8500E-04	9.8500E-04	Р12

0.0000E+00	0.0000E+00	Р13

0.0000E+00	0.0000E+00	Р14

-5.0470E-02	-5.0470E-02	Р15

5.5986E-03	5.5986E-03	Р16

-1.1489E-04	-1.1489E-04	Р17

0.0000E+00	0.0000E+00	Р18

0.0000E+00	0.0000E+00	Р19

0.0000E+00	0.0000E+00	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 6

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 36_B20  3.62% (245*3.7%+66*3.3%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

3.0665E-03	3.1747E-03	Р1

-1.4040E-03	-2.0564E-03	Р2

-3.0870E-04	-3.1146E-04	Р3

5.6702E-06	5.9136E-06	Р4

-3.1992E-08	-3.3671E-08	Р5

3.3466E-04	3.3466E-04	Р6

-6.9863E-02	-6.9863E-02	Р7

-2.1938E-02	-2.1938E-02	Р8

-1.2988E-02	-1.2988E-02	Р9

-6.2028E-03	-6.2028E-03	Р10

7.6058E-04	7.6058E-04	Р11

9.8500E-04	9.8500E-04	Р12

2.0282E-03	2.0282E-03	Р13

-2.1051E-05	-2.1051E-05	Р14

-5.5348E-02	-5.5348E-02	Р15

4.4465E-03	4.4465E-03	Р16

2.5281E-04	2.5281E-04	Р17

-6.6472E-02	-6.6472E-02	Р18

2.9322E-03	2.9322E-03	Р19

2.5103E-04	2.5103E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 7

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 36_B36  3.62% (245*3.7%+66*3.3%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

3.0665E-03	3.1747E-03	Р1

-1.4040E-03	-2.0564E-03	Р2

-3.0870E-04	-3.1146E-04	Р3

5.6702E-06	5.9136E-06	Р4

-3.1992E-08	-3.3671E-08	Р5

3.3466E-04	3.3466E-04	Р6

-6.9863E-02	-6.9863E-02	Р7

-2.1938E-02	-2.1938E-02	Р8

-1.2988E-02	-1.2988E-02	Р9

-6.2028E-03	-6.2028E-03	Р10

7.6058E-04	7.6058E-04	Р11

9.8500E-04	9.8500E-04	Р12

2.5774E-03	2.5774E-03	Р13

-2.6389E-05	-2.6389E-05	Р14

-5.5348E-02	-5.5348E-02	Р15

4.4465E-03	4.4465E-03	Р16

2.5281E-04	2.5281E-04	Р17

-6.6472E-02	-6.6472E-02	Р18

2.9322E-03	2.9322E-03	Р19

2.5103E-04	2.5103E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 8

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 40 kl-BDy 4% (245*4.1%+66*3.7%) 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

3.2888E-03	3.4056E-03	Р1

-2.0574E-03	-2.6185E-03	Р2

-2.5075E-04	-2.5586E-04	Р3

4.3233E-06	4.5734E-06	Р4

-2.3113E-08	-2.4722E-08	Р5

3.4243E-04	3.4243E-04	Р6

-6.3294E-02	-6.3294E-02	Р7

-2.0920E-02	-2.0920E-02	Р8

-1.1222E-02	-1.1222E-02	Р9

-6.4724E-03	-6.4724E-03	Р10

7.1587E-04	7.1587E-04	Р11

9.8500E-04	9.8500E-04	Р12

6.3766E-03	6.3766E-03	Р13

-4.5976E-05	-4.5976E-05	Р14

-5.3324E-02	-5.3324E-02	Р15

3.1730E-03	3.1730E-03	Р16

2.6731E-04	2.6731E-04	Р17

-6.4602E-02	-6.4602E-02	Р18

1.9050E-03	1.9050E-03	Р19

2.6178E-04	2.6178E-04	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Table 9

Coefficients for SPND sensitivity computation functions; d=0.481мм

TVS 40B20 4% (245*4.1%+66*3.7%) SVP0.02 489.8 kg-UO2

Formulas:

F=S*M/( Kc*L*f(Q)) ,  MWt-TVS/(m*mkA);

S=P1*(1+P2*W+P3*W**2+P4*W**3+P5*W**4)* (1+P6*(1+P7*W)*(G-G0)) *

(1+P8*(1+P9*W)*(C-C0))*(1+(P10+P11*W)*(Q/Q0-1)) * (1+P12*(N-4))* ((1+P13*Wp+P14*(W-Wp)*Wp)*Lo/Kc + (1+P15+P16*Wp+P17*Wp**2) *Lb/Kcb + (1+P18+P19*Wp+P20*Wp**2) *Ld/Kcd)

Coefficient value	Coefficient

for Kc(NFMC)	for Kc(H2O)	denomination

3.2888E-03	3.4056E-03	Р1

-2.0574E-03	-2.6185E-03	Р2

-2.5075E-04	-2.5586E-04	Р3

4.3233E-06	4.5734E-06	Р4

-2.3113E-08	-2.4722E-08	Р5

3.4243E-04	3.4243E-04	Р6

-6.3294E-02	-6.3294E-02	Р7

-2.0920E-02	-2.0920E-02	Р8

-1.1222E-02	-1.1222E-02	Р9

-6.4724E-03	-6.4724E-03	Р10

7.1587E-04	7.1587E-04	Р11

9.8500E-04	9.8500E-04	Р12

0.0000E+00	0.0000E+00	Р13

0.0000E+00	0.0000E+00	Р14

-5.0521E-02	-5.0521E-02	Р15

4.9450E-03	4.9450E-03	Р16

-9.0363E-05	-9.0363E-05	Р17

0.0000E+00	0.0000E+00	Р18

0.0000E+00	0.0000E+00	Р19

0.0000E+00	0.0000E+00	Р20

G0	724.1	kg/m3

C0	0.6	gBnat/kgН2О

Q0	167.2	W/cmrod

M	311

D	1	 with solid absorber

D	0	 without solid absorber

f(Q)               	 function accounting for SPND burnup

Q	 	charge flown through, Kl

Remarks:

1) The second column (for Kc(H2O)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing water in the central tube.

That’s the approach currently adopted for Kc computations.

2) The first column (for Kc(NFMC)) should be used if the ICIS application software applies neighboring -rod load factors Kc calculated for assemblies containing NFMC in the central tube.

Annex 4

Neutronic constants for the ICIS

Table 1- Neutronic constants for VVER-1000 ICIS application software
TVS 24 2.4 % (311*2.4 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

100	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.8327072	- Fi1

-0.016208	- Fi2

K0	12718	12600	12485	12358	12227	12097	11970	11844	11726	11611

11499	11390	11284	11181	11081	10982	10887	10793	10701	10611

10523	10437	10352	10270	10189	10109	10032	9956	9882	9809

9738	9669	9602	9537	9473	9411	9350	9292	9235	9179

9126

M0	6516	6485	6456	6428	6401	6376	6351	6327	6304	6283

6262	6242	6223	6205	6187	6170	6154	6139	6124	6110

6096	6083	6071	6058	6047	6035	6024	6014	6003	5993

5983	5973	5964	5954	5945	5935	5926	5916	5906	5897

5887

B1	-2796	-2836	-2874	-2911	-2947	-2981	-3015	-3048	-3080	-3110

-3140	-3168	-3195	-3222	-3247	-3271	-3294	-3316	-3337	-3357

-3376	-3394	-3411	-3426	-3441	-3454	-3467	-3478	-3488	-3498

-3506	-3513	-3519	-3524	-3528	-3530	-3532	-3533	-3532	-3531

-3529

B2	7393	7496	7597	7694	7789	7881	7970	8056	8139	8220

8298	8373	8445	8514	8580	8644	8705	8762	8818	8870

8919	8966	9009	9050	9088	9123	9156	9185	9212	9236

9257	9275	9290	9303	9313	9320	9324	9325	9323	9319

9311

I1	-9494	-9469	-9443	-9418	-9392	-9366	-9340	-9314	-9287	-9260

-9233	-9206	-9178	-9151	-9123	-9095	-9066	-9038	-9009	-8980

-8951	-8921	-8892	-8862	-8832	-8802	-8771	-8740	-8710	-8678

-8647	-8616	-8584	-8552	-8520	-8487	-8454	-8422	-8388	-8355

-8322

I2	2435	2422	2410	2398	2387	2375	2364	2353	2343	2333

2323	2313	2304	2295	2286	2278	2270	2262	2254	2247

2240	2233	2227	2220	2215	2209	2204	2199	2194	2190

2185	2182	2178	2175	2172	2169	2167	2164	2163	2161

2160

I3	-1442	-1415	-1388	-1363	-1338	-1314	-1291	-1268	-1247	-1227

-1207	-1188	-1170	-1153	-1137	-1122	-1107	-1093	-1081	-1069

-1058	-1048	-1038	-1030	-1022	-1016	-1010	-1005	-1001	-997

-995	-994	-993	-993	-994	-996	-999	-1002	-1007	-1012

-1019

I4	-4512	-4424	-4339	-4257	-4178	-4101	-4027	-3956	-3887	-3821

-3758	-3698	-3640	-3585	-3533	-3484	-3437	-3394	-3352	-3314

-3278	-3245	-3215	-3188	-3163	-3141	-3122	-3105	-3092	-3081

-3072	-3067	-3064	-3064	-3067	-3072	-3080	-3091	-3105	-3121

-3140

I5	-2688	-2635	-2584	-2534	-2486	-2439	-2394	-2350	-2308	-2267

-2228	-2190	-2154	-2119	-2085	-2053	-2022	-1993	-1966	-1940

-1915	-1892	-1870	-1850	-1831	-1814	-1798	-1783	-1770	-1759

-1749	-1741	-1734	-1728	-1724	-1721	-1720	-1720	-1722	-1725

-1730

D1	-4019	-4108	-4187	-4257	-4319	-4372	-4417	-4455	-4485	-4509

-4525	-4536	-4541	-4540	-4534	-4523	-4508	-4489	-4466	-4439

-4410	-4378	-4344	-4308	-4270	-4231	-4191	-4151	-4110	-4070

-4030	-3992	-3954	-3919	-3885	-3853	-3825	-3799	-3777	-3759

-3744

D2	-3380	-3454	-3526	-3595	-3661	-3726	-3788	-3847	-3904	-3959

-4011	-4061	-4109	-4154	-4196	-4236	-4274	-4309	-4342	-4373

-4401	-4426	-4449	-4470	-4489	-4504	-4518	-4529	-4538	-4544

-4548	-4549	-4548	-4545	-4539	-4531	-4520	-4507	-4491	-4473

-4453

E1	-2514	-2485	-2460	-2436	-2415	-2397	-2380	-2366	-2354	-2344

-2336	-2329	-2324	-2321	-2319	-2318	-2318	-2320	-2322	-2326

-2330	-2335	-2340	-2346	-2352	-2359	-2365	-2372	-2379	-2385

-2391	-2397	-2402	-2407	-2411	-2414	-2416	-2417	-2417	-2416

-2414

E2	3570	3503	3442	3388	3339	3296	3258	3225	3197	3173

3154	3139	3128	3120	3115	3114	3115	3119	3125	3134

3144	3156	3169	3183	3197	3213	3229	3244	3260	3275

3290	3303	3316	3327	3336	3343	3349	3351	3352	3349

3343

EX	-735	-716	-697	-680	-664	-649	-636	-623	-611	-600

-590	-580	-572	-564	-557	-550	-545	-539	-534	-530

-526	-523	-520	-517	-514	-512	-510	-508	-506	-504

-502	-500	-499	-496	-494	-492	-489	-486	-483	-479

-475

ES	-2328	-2265	-2206	-2151	-2100	-2052	-2008	-1967	-1929	-1894

-1862	-1833	-1806	-1781	-1759	-1739	-1721	-1705	-1690	-1677

-1665	-1655	-1646	-1637	-1630	-1623	-1617	-1611	-1605	-1600

-1594	-1588	-1582	-1576	-1568	-1560	-1552	-1542	-1531	-1518

-1504

F1	-12930	-12714	-12515	-12334	-12169	-12020	-11886	-11767	-11661	-11569

-11489	-11420	-11363	-11316	-11279	-11251	-11231	-11218	-11213	-11214

-11220	-11231	-11246	-11265	-11286	-11309	-11334	-11360	-11385	-11410

-11433	-11454	-11473	-11488	-11498	-11504	-11505	-11499	-11486	-11466

-11437

F2	1389	1356	1325	1297	1272	1250	1230	1212	1197	1183

1172	1163	1155	1149	1145	1142	1140	1140	1141	1143

1145	1149	1153	1157	1162	1168	1173	1179	1185	1190

1195	1200	1204	1208	1211	1214	1215	1215	1214	1212

1209

MS	943	936	931	927	924	922	922	922	924	927

931	935	941	947	954	961	970	979	988	998

1008	1018	1029	1040	1052	1063	1074	1086	1097	1109

1120	1131	1141	1152	1162	1171	1181	1189	1197	1204

1211

CS	-210	-215	-220	-226	-231	-237	-242	-248	-253	-259

-265	-271	-276	-282	-288	-294	-300	-306	-312	-318

-324	-331	-337	-343	-349	-355	-361	-367	-373	-380

-386	-392	-398	-404	-410	-416	-422	-428	-433	-439

-445

SX	3095	3073	3057	3044	3036	3032	3032	3036	3043	3054

3067	3084	3103	3125	3150	3176	3205	3235	3267	3301

3336	3372	3409	3447	3485	3524	3563	3602	3641	3679

3717	3755	3791	3826	3860	3893	3924	3953	3980	4005

4027

CX	-825	-842	-859	-877	-895	-914	-933	-952	-972	-992

-1012	-1033	-1054	-1075	-1097	-1118	-1140	-1162	-1184	-1206

-1229	-1251	-1274	-1296	-1319	-1342	-1364	-1387	-1409	-1432

-1454	-1477	-1499	-1521	-1543	-1565	-1586	-1608	-1629	-1649

-1670

D0	1430	1430	1430	1430	1429	1429	1429	1429	1429	1428

1428	1428	1428	1427	1427	1427	1427	1426	1426	1426

1425	1425	1425	1424	1424	1424	1423	1423	1423	1423

1422	1422	1422	1422	1421	1421	1421	1421	1421	1420

1420

CD	-7412	-7309	-7209	-7111	-7015	-6921	-6830	-6741	-6654	-6570

-6488	-6408	-6331	-6256	-6183	-6112	-6044	-5978	-5915	-5853

-5794	-5738	-5683	-5631	-5582	-5534	-5489	-5446	-5406	-5368

-5332	-5298	-5267	-5238	-5211	-5187	-5165	-5145	-5128	-5113

-5100

DD	1991	1990	1988	1987	1985	1984	1982	1981	1980	1978

1977	1975	1974	1973	1972	1970	1969	1968	1967	1965

1964	1963	1962	1961	1960	1959	1958	1957	1956	1955

1954	1953	1952	1951	1950	1949	1948	1947	1947	1946

1945

L0	6143	6004	5876	5758	5651	5554	5466	5387	5316	5254

5199	5152	5111	5077	5049	5027	5010	4997	4989	4985

4984	4987	4992	4999	5008	5019	5031	5043	5056	5068

5079	5090	5099	5106	5111	5113	5112	5108	5099	5086

5068

J1	-6605	-6487	-6373	-6265	-6161	-6062	-5967	-5878	-5793	-5713

-5638	-5568	-5502	-5441	-5385	-5334	-5288	-5246	-5209	-5177

-5150	-5128	-5110	-5097	-5089	-5086	-5087	-5094	-5105	-5121

-5141	-5167	-5197	-5232	-5272	-5316	-5366	-5420	-5479	-5542

-5611

J2	2248	2189	2132	2077	2024	1973	1924	1878	1833	1790

1750	1712	1675	1641	1609	1579	1551	1525	1501	1479

1460	1442	1427	1413	1402	1393	1386	1381	1378	1377

1378	1381	1386	1394	1403	1415	1428	1444	1462	1482

1504

NU	2463	2478	2493	2508	2522	2536	2549	2562	2575	2588

2600	2611	2623	2634	2645	2655	2665	2675	2684	2693

2702	2710	2718	2726	2733	2740	2746	2753	2759	2764

2769	2774	2779	2783	2787	2790	2793	2796	2798	2801

2802

VX	21782	21899	22013	22124	22232	22337	22439	22538	22634	22727

22817	22903	22987	23068	23146	23221	23293	23362	23428	23491

23551	23608	23661	23712	23760	23805	23847	23886	23922	23955

23985	24012	24035	24056	24074	24089	24101	24110	24116	24119

24119

VI	20881	20906	20930	20954	20977	21000	21023	21046	21068	21090

21112	21133	21154	21174	21194	21214	21234	21253	21272	21290

21308	21326	21344	21361	21377	21394	21410	21426	21441	21456

21471	21485	21500	21513	21527	21540	21552	21565	21577	21589

21600

VP	3682	3703	3723	3743	3763	3782	3801	3820	3838	3856

3873	3891	3907	3924	3940	3955	3971	3986	4000	4014

4028	4042	4055	4068	4080	4092	4104	4115	4126	4137

4147	4157	4167	4176	4185	4193	4201	4209	4216	4223

4230

VE	3235	3240	3245	3250	3254	3259	3264	3268	3272	3276

3280	3284	3288	3292	3295	3299	3302	3305	3308	3311

3314	3317	3319	3322	3324	3326	3328	3330	3332	3334

3336	3337	3338	3340	3341	3342	3343	3343	3344	3345

3345

ESS1	-25005	-24711	-24444	-24204	-23988	-23797	-23629	-23483	-23357	-23251

-23164	-23095	-23042	-23005	-22982	-22972	-22974	-22988	-23011	-23044

-23085	-23132	-23185	-23243	-23304	-23368	-23434	-23499	-23565	-23628

-23688	-23745	-23796	-23842	-23880	-23910	-23931	-23941	-23940	-23926

-23899

ESS2	3561	3492	3430	3374	3323	3279	3240	3206	3177	3152

3132	3116	3104	3096	3091	3089	3091	3094	3100	3109

3119	3130	3143	3157	3172	3187	3203	3219	3235	3250

3264	3278	3290	3301	3310	3317	3322	3325	3324	3321

3314

Table 2 - Neutronic constants for VVER-1000 ICIS application software
TVS 24 KL-B 2.4 % (311*2.4 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

100	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1  =  0 PK8  =  0.985

0.7945536	- Fi1

-0.0171764	- Fi2

K0	9392	9337	9283	9214	9138	9057	8976	8894	8815	8737

8659	8583	8509	8435	8363	8292	8222	8154	8086	8020

7955	7891	7828	7766	7705	7646	7588	7531	7475	7420

7367	7315	7264	7215	7167	7120	7075	7031	6988	6947

6906

M0	5827	5812	5798	5783	5769	5756	5743	5730	5717	5705

5693	5681	5670	5659	5648	5638	5627	5618	5608	5598

5589	5580	5572	5563	5555	5547	5539	5532	5525	5517

5510	5504	5497	5490	5484	5478	5472	5466	5460	5455

5449

B1	-2606	-2647	-2687	-2726	-2764	-2801	-2836	-2871	-2904	-2936

-2967	-2997	-3026	-3054	-3080	-3106	-3130	-3153	-3175	-3196

-3216	-3234	-3252	-3268	-3283	-3298	-3311	-3322	-3333	-3343

-3351	-3359	-3365	-3370	-3374	-3377	-3378	-3379	-3379	-3377

-3374

B2	6844	6952	7058	7160	7259	7355	7448	7538	7626	7710

7791	7870	7945	8018	8087	8154	8217	8278	8335	8390

8442	8491	8536	8579	8619	8656	8690	8721	8749	8774

8796	8815	8831	8844	8854	8862	8866	8867	8865	8861

8853

I1	-6753	-6748	-6743	-6737	-6731	-6724	-6716	-6707	-6697	-6687

-6676	-6665	-6652	-6639	-6626	-6611	-6596	-6580	-6563	-6546

-6528	-6509	-6489	-6469	-6448	-6426	-6404	-6381	-6357	-6332

-6307	-6281	-6254	-6226	-6198	-6169	-6139	-6109	-6078	-6046

-6013

I2	2018	2012	2007	2002	1997	1992	1987	1982	1978	1973

1969	1964	1960	1956	1952	1948	1944	1940	1936	1933

1929	1926	1922	1919	1916	1913	1910	1907	1904	1902

1899	1896	1894	1892	1890	1887	1885	1883	1882	1880

1878

I3	-865	-849	-834	-819	-805	-791	-778	-765	-752	-740

-728	-717	-706	-696	-686	-677	-668	-660	-652	-644

-637	-630	-624	-619	-613	-608	-604	-600	-597	-594

-591	-589	-587	-586	-585	-585	-585	-586	-587	-588

-590

I4	-2750	-2699	-2649	-2601	-2554	-2509	-2465	-2423	-2382	-2342

-2304	-2268	-2233	-2199	-2167	-2137	-2107	-2080	-2053	-2029

-2005	-1984	-1963	-1944	-1927	-1911	-1896	-1883	-1872	-1862

-1853	-1846	-1840	-1836	-1833	-1832	-1832	-1834	-1837	-1841

-1847

I5	-1519	-1490	-1462	-1435	-1408	-1382	-1357	-1333	-1309	-1286

-1263	-1242	-1220	-1200	-1181	-1162	-1143	-1126	-1109	-1093

-1078	-1063	-1049	-1035	-1023	-1011	-1000	-989	-979	-970

-962	-954	-947	-941	-935	-930	-926	-922	-919	-917

-916

D1	-8217	-8143	-8070	-7998	-7927	-7857	-7787	-7718	-7651	-7584

-7518	-7453	-7388	-7325	-7262	-7200	-7139	-7078	-7018	-6959

-6901	-6844	-6787	-6731	-6675	-6621	-6566	-6513	-6460	-6408

-6357	-6306	-6256	-6206	-6157	-6108	-6060	-6013	-5966	-5920

-5874

D2	-5655	-5661	-5667	-5671	-5675	-5679	-5681	-5683	-5684	-5685

-5685	-5684	-5683	-5680	-5677	-5674	-5670	-5665	-5659	-5653

-5646	-5638	-5630	-5620	-5611	-5600	-5589	-5577	-5565	-5551

-5538	-5523	-5508	-5492	-5475	-5458	-5440	-5421	-5401	-5381

-5361

E1	-2071	-2054	-2039	-2024	-2011	-1999	-1989	-1979	-1971	-1964

-1957	-1952	-1948	-1944	-1942	-1941	-1940	-1940	-1941	-1943

-1945	-1948	-1952	-1956	-1961	-1966	-1972	-1978	-1985	-1992

-2000	-2008	-2016	-2025	-2033	-2042	-2051	-2060	-2070	-2079

-2088

E2	2545	2535	2523	2509	2494	2478	2461	2443	2425	2407

2388	2370	2353	2336	2320	2305	2292	2281	2271	2264

2259	2257	2258	2262	2269	2280	2295	2314	2338	2366

2398	2436	2480	2528	2583	2644	2711	2784	2865	2952

3047

EX	-452	-441	-431	-421	-412	-403	-395	-388	-381	-375

-369	-363	-358	-353	-349	-345	-341	-338	-335	-332

-329	-327	-325	-323	-321	-319	-317	-316	-314	-313

-311	-310	-308	-307	-305	-304	-302	-300	-298	-296

-294

ES	-1477	-1441	-1407	-1375	-1345	-1317	-1291	-1267	-1244	-1224

-1205	-1187	-1171	-1157	-1143	-1131	-1120	-1110	-1102	-1094

-1086	-1080	-1074	-1069	-1064	-1060	-1056	-1053	-1049	-1046

-1042	-1039	-1036	-1032	-1028	-1024	-1019	-1014	-1008	-1001

-994

F1	-10372	-10205	-10052	-9912	-9784	-9669	-9564	-9471	-9388	-9315

-9251	-9196	-9149	-9110	-9079	-9054	-9035	-9022	-9014	-9011

-9012	-9017	-9025	-9035	-9047	-9061	-9076	-9092	-9107	-9122

-9136	-9149	-9159	-9167	-9172	-9173	-9170	-9162	-9149	-9130

-9105

F2	975	953	933	914	898	883	869	857	847	838

830	824	819	815	812	810	808	808	808	809

811	813	815	818	822	825	829	832	836	839

843	846	849	851	854	855	856	856	856	855

853

MS	893	885	879	874	871	868	867	867	868	870

873	876	881	886	892	898	906	913	921	930

939	949	958	968	978	988	999	1009	1019	1029

1039	1049	1058	1068	1076	1085	1093	1100	1107	1113

1119

CS	-227	-230	-234	-237	-241	-245	-249	-253	-258	-262

-267	-272	-276	-281	-286	-292	-297	-302	-307	-313

-318	-324	-329	-335	-341	-346	-352	-358	-363	-369

-374	-380	-386	-391	-397	-402	-407	-413	-418	-423

-428

SX	2920	2897	2878	2864	2854	2847	2844	2845	2849	2857

2867	2880	2896	2915	2935	2958	2983	3010	3038	3068

3099	3131	3164	3197	3231	3266	3301	3336	3370	3405

3438	3471	3504	3535	3565	3593	3621	3646	3669	3690

3709

CX	-868	-879	-890	-903	-915	-929	-943	-958	-973	-989

-1006	-1023	-1040	-1058	-1076	-1095	-1114	-1133	-1153	-1173

-1193	-1213	-1233	-1254	-1274	-1295	-1316	-1336	-1357	-1378

-1398	-1419	-1439	-1459	-1479	-1499	-1518	-1537	-1556	-1575

-1593

D0	1408	1408	1408	1408	1408	1408	1408	1408	1408	1408

1408	1408	1408	1408	1407	1407	1407	1407	1407	1406

1406	1406	1406	1406	1405	1405	1405	1405	1405	1404

1404	1404	1404	1404	1404	1403	1403	1403	1403	1403

1403

CD	-4818	-4739	-4662	-4585	-4510	-4435	-4361	-4288	-4216	-4145

-4075	-4006	-3937	-3870	-3803	-3738	-3673	-3609	-3546	-3484

-3423	-3363	-3304	-3245	-3188	-3131	-3076	-3021	-2967	-2915

-2863	-2811	-2761	-2712	-2664	-2616	-2570	-2524	-2480	-2436

-2393

DD	1846	1845	1844	1843	1842	1841	1840	1839	1838	1837

1836	1835	1834	1833	1832	1832	1831	1830	1829	1828

1827	1826	1825	1824	1824	1823	1822	1821	1820	1819

1819	1818	1817	1816	1815	1814	1814	1813	1812	1811

1811

L0	5021	4915	4817	4727	4645	4570	4503	4442	4387	4339

4296	4259	4227	4200	4177	4159	4144	4134	4126	4122

4120	4121	4123	4127	4133	4140	4148	4156	4165	4173

4181	4188	4194	4198	4201	4202	4201	4197	4190	4180

4166

J1	-4496	-4421	-4350	-4281	-4216	-4153	-4094	-4037	-3984	-3933

-3886	-3841	-3799	-3761	-3725	-3692	-3663	-3636	-3612	-3592

-3574	-3559	-3547	-3538	-3532	-3530	-3530	-3533	-3539	-3548

-3560	-3575	-3593	-3614	-3638	-3665	-3695	-3727	-3763	-3802

-3844

J2	1671	1629	1590	1551	1515	1479	1445	1412	1381	1352

1323	1296	1271	1247	1224	1203	1184	1165	1148	1133

1119	1106	1095	1086	1077	1070	1065	1061	1058	1057

1058	1059	1063	1067	1073	1081	1090	1100	1112	1125

1139

NU	2469	2484	2498	2513	2527	2540	2554	2567	2579	2592

2604	2615	2627	2637	2648	2658	2668	2678	2687	2696

2704	2713	2720	2728	2735	2742	2748	2754	2760	2766

2771	2776	2780	2784	2788	2791	2794	2797	2799	2801

2803

VX	21803	21919	22031	22140	22247	22350	22451	22548	22642	22734

22822	22908	22991	23070	23147	23220	23291	23358	23423	23485

23543	23599	23652	23702	23748	23792	23833	23871	23906	23937

23966	23992	24015	24035	24052	24066	24077	24085	24090	24092

24091

VI	20912	20936	20961	20984	21008	21031	21054	21076	21098	21120

21141	21162	21183	21204	21224	21243	21263	21282	21300	21319

21337	21355	21372	21389	21406	21422	21438	21453	21469	21484

21498	21513	21527	21540	21554	21566	21579	21591	21603	21615

21626

VP	3706	3727	3747	3767	3787	3806	3825	3844	3862	3880

3897	3914	3931	3948	3964	3979	3995	4010	4024	4038

4052	4066	4079	4092	4104	4116	4128	4139	4150	4161

4171	4181	4191	4200	4209	4217	4225	4233	4240	4247

4254

VE	3235	3240	3245	3250	3255	3260	3264	3269	3273	3277

3281	3285	3289	3293	3296	3300	3303	3306	3309	3312

3315	3318	3320	3323	3325	3327	3329	3331	3333	3335

3336	3338	3339	3340	3341	3342	3343	3344	3345	3345

3345

ESS1	-20494	-20319	-20157	-20009	-19874	-19751	-19641	-19543	-19455	-19379

-19314	-19259	-19215	-19179	-19154	-19137	-19128	-19128	-19136	-19151

-19174	-19203	-19239	-19280	-19328	-19380	-19438	-19500	-19567	-19637

-19711	-19788	-19868	-19951	-20035	-20121	-20209	-20297	-20386	-20476

-20565

ESS2	2522	2510	2497	2482	2466	2449	2431	2413	2394	2375

2356	2338	2320	2303	2287	2273	2259	2248	2239	2231

2227	2224	2225	2229	2236	2247	2262	2280	2303	2331

2363	2400	2442	2490	2543	2602	2668	2739	2818	2903

2995

Table 3 Neutronic constants for VVER-1000 ICIS application software
TVS 24 KL-DY 2.4 % (311*2.4 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

100	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1  =  0 PK8  =  0.985

0.8030421	- Fi1

-0.0163921	- Fi2

K0	10352	10288	10225	10146	10058	9967	9875	9782	9693	9605

9518	9433	9349	9267	9186	9107	9029	8952	8877	8803

8730	8659	8589	8520	8452	8386	8321	8258	8196	8135

8076	8018	7962	7907	7854	7802	7751	7702	7655	7609

7564

M0	6083	6064	6046	6028	6011	5994	5977	5961	5946	5931

5916	5902	5888	5874	5861	5849	5836	5824	5812	5801

5790	5779	5769	5758	5749	5739	5730	5720	5711	5703

5694	5686	5678	5670	5662	5655	5647	5640	5633	5626

5619

B1	-2732	-2774	-2814	-2853	-2892	-2928	-2964	-2999	-3032	-3065

-3096	-3126	-3155	-3183	-3209	-3235	-3259	-3283	-3305	-3326

-3345	-3364	-3382	-3398	-3413	-3427	-3440	-3452	-3463	-3473

-3481	-3488	-3495	-3500	-3503	-3506	-3508	-3508	-3508	-3506

-3503

B2	7198	7308	7415	7518	7619	7717	7811	7903	7991	8077

8159	8239	8315	8388	8459	8526	8590	8651	8709	8765

8817	8866	8912	8955	8995	9032	9065	9096	9124	9149

9171	9189	9205	9218	9227	9234	9237	9238	9235	9230

9221

I1	-7879	-7871	-7862	-7852	-7842	-7831	-7819	-7807	-7793	-7779

-7765	-7749	-7733	-7716	-7699	-7680	-7661	-7642	-7621	-7600

-7578	-7555	-7532	-7507	-7482	-7457	-7430	-7403	-7375	-7347

-7317	-7287	-7256	-7225	-7193	-7160	-7126	-7092	-7056	-7020

-6984

I2	2164	2156	2149	2142	2136	2129	2123	2116	2110	2104

2098	2092	2086	2080	2075	2070	2064	2059	2054	2050

2045	2040	2036	2031	2027	2023	2019	2016	2012	2008

2005	2002	1999	1996	1993	1990	1987	1985	1982	1980

1978

I3	-1000	-982	-964	-947	-930	-914	-899	-884	-869	-855

-842	-829	-816	-805	-793	-783	-773	-763	-754	-745

-737	-730	-723	-717	-711	-705	-701	-697	-693	-690

-687	-685	-684	-683	-682	-682	-683	-684	-686	-688

-691

I4	-3157	-3098	-3040	-2985	-2931	-2878	-2828	-2779	-2732	-2687

-2644	-2602	-2562	-2524	-2487	-2452	-2419	-2388	-2358	-2331

-2305	-2280	-2258	-2237	-2218	-2201	-2185	-2171	-2159	-2149

-2140	-2133	-2128	-2125	-2123	-2123	-2125	-2129	-2134	-2141

-2150

I5	-1802	-1767	-1734	-1702	-1670	-1640	-1610	-1581	-1553	-1526

-1500	-1475	-1450	-1427	-1404	-1383	-1362	-1342	-1323	-1305

-1288	-1271	-1256	-1241	-1228	-1215	-1203	-1192	-1182	-1173

-1165	-1158	-1151	-1146	-1141	-1137	-1134	-1132	-1131	-1131

-1132

D1	-6291	-6249	-6206	-6164	-6121	-6078	-6034	-5991	-5948	-5904

-5861	-5817	-5773	-5730	-5686	-5643	-5599	-5555	-5512	-5469

-5425	-5382	-5339	-5296	-5254	-5211	-5169	-5127	-5085	-5043

-5002	-4960	-4920	-4879	-4839	-4799	-4760	-4721	-4682	-4644

-4606

D2	-4337	-4370	-4401	-4431	-4460	-4487	-4513	-4537	-4561	-4582

-4603	-4622	-4640	-4656	-4671	-4685	-4697	-4708	-4718	-4726

-4733	-4738	-4742	-4745	-4746	-4746	-4745	-4742	-4738	-4733

-4726	-4718	-4709	-4698	-4685	-4672	-4657	-4641	-4623	-4604

-4583

E1	-2120	-2098	-2078	-2061	-2045	-2030	-2018	-2007	-1998	-1990

-1984	-1979	-1975	-1973	-1971	-1971	-1971	-1972	-1974	-1977

-1980	-1984	-1989	-1993	-1998	-2003	-2009	-2014	-2019	-2024

-2029	-2034	-2038	-2042	-2045	-2047	-2049	-2050	-2051	-2050

-2048

E2	2670	2621	2578	2538	2503	2472	2445	2422	2402	2385

2372	2361	2353	2348	2345	2345	2346	2349	2354	2360

2368	2377	2387	2397	2408	2420	2432	2443	2455	2466

2477	2487	2496	2504	2511	2516	2520	2522	2521	2519

2515

EX	-509	-496	-484	-473	-463	-453	-444	-435	-428	-420

-413	-407	-401	-396	-391	-386	-382	-378	-375	-371

-368	-366	-363	-361	-359	-357	-355	-353	-352	-350

-348	-347	-345	-343	-342	-340	-338	-336	-334	-331

-328

ES	-1638	-1596	-1557	-1521	-1487	-1455	-1425	-1398	-1372	-1349

-1327	-1307	-1288	-1271	-1256	-1242	-1229	-1218	-1207	-1198

-1189	-1182	-1175	-1168	-1163	-1158	-1153	-1148	-1144	-1140

-1136	-1132	-1127	-1123	-1118	-1113	-1107	-1100	-1093	-1086

-1077

F1	-10608	-10435	-10275	-10130	-9997	-9877	-9768	-9671	-9585	-9509

-9442	-9385	-9336	-9296	-9263	-9237	-9217	-9204	-9195	-9192

-9193	-9198	-9206	-9217	-9230	-9244	-9260	-9276	-9293	-9308

-9323	-9336	-9347	-9355	-9361	-9362	-9359	-9351	-9338	-9319

-9294

F2	1003	980	958	939	921	905	891	878	868	858

850	843	837	833	830	827	826	825	825	826

828	830	832	835	838	842	845	849	852	856

859	862	865	867	869	870	871	871	870	868

865

MS	902	894	888	883	880	877	876	876	877	879

882	886	890	895	901	908	915	923	932	941

950	959	969	979	990	1000	1010	1021	1031	1042

1052	1062	1071	1081	1090	1098	1107	1114	1121	1128

1133

CS	-216	-219	-223	-227	-231	-235	-240	-244	-248	-253

-258	-262	-267	-272	-277	-282	-288	-293	-298	-303

-309	-314	-320	-325	-330	-336	-341	-347	-352	-358

-363	-369	-374	-379	-385	-390	-395	-400	-405	-410

-415

SX	2950	2926	2907	2893	2882	2876	2873	2874	2879	2886

2897	2911	2927	2946	2967	2990	3015	3043	3071	3102

3133	3166	3199	3234	3269	3304	3339	3375	3410	3445

3480	3513	3546	3578	3609	3638	3666	3692	3716	3737

3757

CX	-833	-845	-857	-870	-884	-898	-912	-928	-943	-959

-976	-993	-1011	-1028	-1047	-1065	-1084	-1103	-1122	-1142

-1162	-1181	-1201	-1221	-1242	-1262	-1282	-1302	-1322	-1342

-1362	-1382	-1402	-1421	-1441	-1460	-1479	-1497	-1516	-1534

-1551

D0	1404	1404	1404	1404	1404	1403	1403	1403	1403	1403

1403	1403	1402	1402	1402	1402	1402	1401	1401	1401

1401	1400	1400	1400	1399	1399	1399	1399	1398	1398

1398	1398	1397	1397	1397	1397	1397	1397	1396	1396

1396

CD	-5555	-5472	-5390	-5310	-5231	-5154	-5078	-5004	-4931	-4860

-4790	-4722	-4655	-4590	-4526	-4464	-4404	-4345	-4287	-4231

-4177	-4124	-4072	-4022	-3974	-3927	-3881	-3838	-3795	-3754

-3715	-3677	-3641	-3606	-3573	-3541	-3511	-3482	-3455	-3429

-3405

DD	1837	1836	1835	1834	1833	1832	1830	1829	1828	1827

1826	1825	1824	1823	1821	1820	1819	1818	1817	1816

1815	1814	1813	1812	1811	1810	1809	1808	1807	1806

1805	1804	1803	1802	1801	1800	1799	1798	1797	1796

1795

L0	5153	5042	4941	4847	4762	4684	4614	4551	4494	4443

4399	4360	4327	4299	4276	4256	4241	4230	4222	4218

4216	4216	4219	4224	4230	4237	4245	4253	4262	4270

4278	4286	4292	4297	4300	4301	4299	4295	4288	4277

4262

J1	-4640	-4562	-4487	-4415	-4346	-4280	-4217	-4158	-4101	-4048

-3998	-3951	-3907	-3866	-3828	-3794	-3762	-3734	-3709	-3687

-3668	-3652	-3640	-3630	-3624	-3621	-3621	-3624	-3630	-3639

-3651	-3667	-3686	-3707	-3732	-3760	-3792	-3826	-3863	-3904

-3948

J2	1756	1712	1670	1629	1590	1553	1517	1482	1449	1418

1388	1360	1333	1307	1283	1261	1240	1221	1203	1187

1172	1159	1147	1137	1128	1121	1115	1111	1108	1107

1107	1109	1112	1117	1124	1132	1141	1152	1165	1179

1194

NU	2467	2482	2497	2511	2525	2539	2552	2565	2578	2591

2603	2614	2626	2637	2647	2658	2668	2677	2686	2695

2704	2712	2720	2728	2735	2742	2748	2754	2760	2765

2771	2775	2780	2784	2788	2791	2794	2797	2799	2801

2803

VX	21797	21913	22026	22137	22244	22348	22449	22548	22643	22735

22824	22910	22994	23074	23151	23225	23296	23365	23430	23492

23551	23607	23660	23710	23758	23802	23843	23881	23916	23948

23977	24003	24026	24047	24064	24078	24089	24097	24102	24104

24103

VI	20901	20926	20950	20974	20997	21020	21043	21066	21088	21110

21131	21152	21173	21193	21213	21233	21252	21271	21290	21309

21327	21344	21362	21379	21395	21412	21428	21443	21458	21473

21488	21502	21516	21530	21543	21556	21569	21581	21593	21604

21615

VP	3698	3719	3739	3759	3779	3798	3817	3836	3854	3872

3889	3906	3923	3939	3955	3971	3986	4001	4016	4030

4044	4058	4071	4083	4096	4108	4120	4131	4142	4152

4163	4173	4182	4191	4200	4208	4216	4224	4231	4238

4245

VE	3235	3240	3245	3250	3255	3260	3264	3269	3273	3277

3281	3285	3289	3293	3296	3300	3303	3306	3309	3312

3315	3318	3320	3323	3325	3327	3329	3331	3333	3335

3336	3338	3339	3340	3341	3342	3343	3344	3345	3345

3345

ESS1	-20991	-20767	-20565	-20382	-20218	-20073	-19945	-19834	-19738	-19658

-19592	-19539	-19499	-19470	-19453	-19446	-19448	-19459	-19477	-19503

-19534	-19571	-19612	-19657	-19705	-19755	-19806	-19858	-19909	-19959

-20007	-20052	-20093	-20131	-20162	-20188	-20207	-20218	-20221	-20215

-20198

ESS2	2645	2597	2552	2513	2477	2446	2418	2394	2374	2356

2342	2331	2323	2317	2314	2312	2313	2316	2320	2326

2334	2342	2351	2361	2372	2383	2395	2406	2418	2429

2440	2450	2459	2467	2474	2480	2484	2486	2486	2485

2481

Table 4 - Neutronic constants for VVER-1000 ICIS application software
TVS 36 3.62 % (245*3.7 %+66*3.3 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

150	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1  =  0 PK8  =  0.985

0.7984826	- Fi1

-0.0149337	- Fi2

K0	13635	13467	13291	13110	12931	12758	12592	12432	12278	12130

11986	11847	11711	11578	11448	11321	11196	11073	10953	10834

10717	10602	10489	10378	10269	10161	10057	9954	9853	9755

9658	9565	9473	9385	9299	9216	9135	9057	8982	8910

8840

M0	6484	6452	6421	6391	6363	6335	6309	6284	6259	6236

6214	6192	6171	6152	6133	6114	6097	6080	6063	6048

6032	6018	6004	5990	5977	5964	5951	5939	5927	5916

5904	5893	5882	5871	5860	5849	5838	5826	5815	5804

5793

B1	-2793	-2837	-2880	-2921	-2962	-3001	-3039	-3075	-3111	-3145

-3178	-3209	-3240	-3269	-3296	-3323	-3348	-3372	-3395	-3416

-3436	-3455	-3473	-3489	-3504	-3518	-3530	-3542	-3552	-3560

-3568	-3574	-3579	-3583	-3585	-3586	-3586	-3585	-3582	-3578

-3573

B2	7375	7492	7605	7715	7822	7925	8025	8121	8215	8304

8391	8474	8553	8629	8702	8772	8838	8901	8960	9016

9068	9118	9164	9206	9245	9281	9313	9342	9368	9390

9409	9424	9436	9445	9450	9452	9450	9446	9437	9426

9411

I1	-9255	-9234	-9212	-9189	-9166	-9142	-9117	-9092	-9066	-9039

-9012	-8984	-8955	-8926	-8896	-8865	-8834	-8802	-8769	-8736

-8702	-8668	-8632	-8596	-8560	-8523	-8485	-8446	-8407	-8367

-8327	-8285	-8244	-8201	-8158	-8114	-8070	-8024	-7979	-7932

-7885

I2	2418	2404	2391	2378	2366	2353	2341	2330	2318	2307

2296	2286	2276	2266	2256	2247	2238	2230	2222	2214

2206	2199	2192	2185	2179	2173	2167	2161	2156	2152

2147	2143	2139	2136	2132	2129	2127	2125	2123	2121

2120

I3	-931	-919	-908	-898	-888	-878	-869	-860	-852	-844

-837	-830	-824	-818	-812	-807	-803	-798	-795	-791

-789	-786	-785	-783	-782	-782	-782	-782	-783	-784

-786	-788	-791	-794	-798	-802	-806	-811	-817	-823

-829

I4	-2958	-2919	-2882	-2846	-2812	-2780	-2748	-2719	-2690	-2664

-2638	-2614	-2592	-2571	-2552	-2534	-2517	-2502	-2489	-2477

-2466	-2457	-2450	-2443	-2439	-2436	-2434	-2434	-2435	-2438

-2442	-2448	-2455	-2463	-2473	-2485	-2498	-2512	-2528	-2546

-2565

I5	-2027	-1994	-1963	-1932	-1903	-1874	-1846	-1820	-1794	-1769

-1745	-1722	-1700	-1679	-1659	-1640	-1621	-1604	-1588	-1572

-1558	-1544	-1532	-1520	-1509	-1500	-1491	-1483	-1476	-1470

-1465	-1461	-1458	-1456	-1455	-1454	-1455	-1457	-1459	-1463

-1467

D1	-5065	-5160	-5245	-5319	-5383	-5437	-5483	-5519	-5547	-5567

-5580	-5585	-5583	-5574	-5559	-5539	-5513	-5482	-5446	-5407

-5363	-5315	-5265	-5212	-5156	-5098	-5039	-4978	-4916	-4854

-4792	-4730	-4669	-4608	-4549	-4492	-4437	-4384	-4335	-4288

-4245

D2	-4168	-4207	-4244	-4281	-4316	-4350	-4383	-4415	-4445	-4475

-4503	-4530	-4556	-4581	-4604	-4627	-4648	-4668	-4687	-4705

-4721	-4737	-4751	-4764	-4776	-4787	-4796	-4805	-4812	-4818

-4823	-4827	-4829	-4831	-4831	-4830	-4828	-4825	-4820	-4815

-4808

E1	-1907	-1895	-1884	-1876	-1870	-1865	-1862	-1861	-1862	-1864

-1867	-1871	-1877	-1884	-1892	-1901	-1911	-1921	-1933	-1945

-1957	-1970	-1984	-1998	-2012	-2026	-2040	-2054	-2068	-2082

-2095	-2108	-2121	-2133	-2145	-2156	-2166	-2175	-2183	-2191

-2197

E2	2213	2186	2164	2145	2131	2120	2113	2110	2110	2113

2119	2128	2139	2153	2169	2187	2208	2230	2254	2279

2305	2333	2361	2391	2420	2451	2481	2512	2543	2573

2603	2632	2661	2689	2716	2741	2765	2787	2808	2827

2843

EX	-533	-521	-510	-499	-490	-481	-473	-465	-459	-453

-447	-443	-438	-435	-431	-428	-426	-424	-422	-421

-419	-419	-418	-417	-417	-417	-416	-416	-416	-416

-415	-415	-415	-414	-413	-412	-411	-409	-407	-405

-402

ES	-1713	-1673	-1636	-1602	-1570	-1541	-1515	-1491	-1469	-1449

-1431	-1415	-1401	-1389	-1378	-1368	-1360	-1353	-1348	-1343

-1339	-1336	-1334	-1332	-1331	-1330	-1329	-1329	-1328	-1327

-1327	-1325	-1324	-1321	-1319	-1315	-1310	-1305	-1298	-1291

-1281

F1	-9688	-9573	-9472	-9384	-9308	-9244	-9192	-9151	-9120	-9099

-9087	-9084	-9089	-9102	-9121	-9148	-9180	-9217	-9260	-9307

-9357	-9411	-9468	-9526	-9587	-9648	-9710	-9772	-9833	-9893

-9951	-10008	-10061	-10111	-10157	-10199	-10236	-10267	-10293	-10311

-10323

F2	839	825	813	803	794	788	783	779	777	776

776	778	781	785	789	795	802	809	817	826

835	845	855	865	876	886	897	908	919	930

940	950	960	969	978	986	994	1001	1007	1012

1016

MS	600	599	600	601	604	608	612	618	625	633

641	650	660	671	682	694	707	720	734	748

763	778	793	808	824	840	856	873	889	905

922	938	954	970	986	1002	1017	1032	1047	1061

1075

CS	-131	-134	-137	-141	-145	-148	-153	-157	-161	-166

-171	-176	-182	-187	-193	-199	-205	-212	-218	-225

-231	-238	-245	-252	-260	-267	-275	-282	-290	-298

-306	-314	-322	-330	-338	-346	-355	-363	-371	-380

-388

SX	1939	1938	1940	1947	1957	1971	1988	2008	2032	2058

2088	2119	2154	2191	2230	2271	2314	2359	2406	2454

2503	2554	2606	2659	2712	2766	2821	2876	2932	2987

3043	3098	3153	3207	3261	3314	3366	3417	3467	3516

3563

CX	-504	-514	-525	-538	-551	-565	-580	-596	-612	-630

-649	-668	-688	-708	-730	-752	-775	-798	-822	-847

-872	-898	-924	-951	-978	-1005	-1033	-1062	-1090	-1119

-1149	-1178	-1208	-1238	-1268	-1298	-1329	-1359	-1390	-1421

-1451

D0	1439	1438	1438	1437	1437	1436	1436	1435	1435	1434

1434	1433	1432	1432	1431	1431	1430	1430	1429	1429

1428	1428	1427	1427	1426	1426	1425	1425	1424	1424

1424	1423	1423	1422	1422	1422	1421	1421	1421	1420

1420

CD	-6120	-6056	-5992	-5930	-5868	-5808	-5749	-5691	-5635	-5579

-5525	-5472	-5420	-5370	-5320	-5272	-5224	-5178	-5134	-5090

-5047	-5006	-4966	-4927	-4889	-4852	-4817	-4783	-4750	-4718

-4687	-4657	-4629	-4602	-4575	-4551	-4527	-4504	-4483	-4463

-4444

DD	2008	2006	2004	2002	2000	1998	1996	1994	1992	1990

1989	1987	1985	1983	1981	1980	1978	1976	1975	1973

1971	1970	1968	1967	1965	1963	1962	1960	1959	1958

1956	1955	1953	1952	1951	1949	1948	1947	1945	1944

1943

L0	4694	4601	4517	4442	4375	4316	4264	4220	4182	4151

4127	4108	4094	4086	4083	4084	4089	4098	4111	4126

4145	4165	4188	4213	4239	4266	4294	4322	4350	4378

4405	4431	4456	4479	4500	4519	4535	4548	4557	4563

4564

J1	-3916	-3874	-3836	-3801	-3768	-3739	-3713	-3690	-3669	-3652

-3638	-3627	-3619	-3613	-3611	-3612	-3616	-3623	-3633	-3645

-3661	-3680	-3702	-3727	-3755	-3786	-3820	-3857	-3897	-3940

-3986	-4035	-4087	-4142	-4200	-4261	-4326	-4393	-4463	-4536

-4612

J2	1667	1629	1592	1557	1524	1492	1461	1433	1405	1379

1355	1332	1311	1291	1272	1256	1240	1227	1214	1203

1194	1186	1180	1176	1172	1171	1170	1172	1175	1179

1185	1192	1201	1211	1223	1237	1252	1268	1286	1305

1326

NU	2460	2474	2488	2502	2515	2528	2541	2554	2566	2578

2589	2601	2612	2623	2633	2644	2654	2663	2673	2682

2691	2700	2708	2716	2724	2731	2739	2746	2753	2759

2765	2771	2777	2782	2787	2792	2797	2801	2805	2808

2812

VX	21761	21868	21973	22076	22176	22273	22368	22461	22551	22639

22724	22807	22887	22965	23041	23114	23184	23252	23318	23381

23442	23500	23555	23609	23659	23708	23754	23797	23838	23876

23912	23946	23977	24006	24032	24055	24077	24095	24112	24125

24137

VI	20869	20893	20917	20940	20963	20986	21009	21031	21053	21075

21096	21118	21139	21160	21180	21201	21221	21241	21260	21279

21299	21317	21336	21354	21373	21390	21408	21425	21442	21459

21476	21492	21509	21524	21540	21555	21571	21585	21600	21615

21629

VP	3672	3692	3712	3731	3750	3769	3788	3806	3824	3841

3859	3876	3893	3909	3926	3942	3958	3973	3988	4003

4018	4032	4046	4060	4074	4087	4100	4113	4125	4138

4149	4161	4173	4184	4194	4205	4215	4225	4235	4244

4254

VE	3234	3239	3243	3248	3253	3257	3261	3266	3270	3274

3278	3282	3285	3289	3292	3296	3299	3302	3306	3309

3311	3314	3317	3320	3322	3325	3327	3329	3331	3333

3335	3337	3339	3340	3342	3343	3344	3345	3347	3348

3348

ESS1	-18877	-18749	-18642	-18556	-18488	-18439	-18407	-18392	-18393	-18409

-18439	-18482	-18538	-18605	-18683	-18771	-18867	-18973	-19085	-19204

-19328	-19458	-19591	-19728	-19867	-20007	-20148	-20288	-20428	-20565

-20700	-20831	-20958	-21079	-21194	-21303	-21403	-21494	-21576	-21648

-21709

ESS2	2194	2166	2143	2124	2109	2098	2090	2086	2085	2088

2093	2101	2112	2126	2142	2159	2179	2201	2224	2249

2275	2302	2330	2359	2389	2419	2449	2480	2510	2540

2570	2599	2628	2656	2682	2707	2731	2754	2774	2793

2809

Table 5 - Neutronic constants for VVER-1000 ICIS application software
TVS 36 KL-B 3.62 % (245*3.7 %+66*3.3 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

150	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.7595761	- Fi1

-0.0155189	- Fi2

K0	10447	10341	10227	10104	9979	9854	9733	9614	9499	9386

9276	9169	9063	8960	8858	8757	8658	8561	8465	8370

8277	8185	8094	8005	7918	7832	7748	7665	7585	7506

7429	7354	7281	7211	7142	7076	7012	6950	6891	6834

6779

M0	5884	5865	5845	5827	5809	5791	5774	5757	5741	5725

5710	5695	5681	5667	5653	5640	5627	5615	5603	5591

5580	5569	5558	5547	5537	5527	5518	5508	5499	5490

5482	5473	5465	5457	5449	5441	5434	5426	5419	5411

5404

B1	-2604	-2651	-2696	-2740	-2783	-2824	-2864	-2903	-2940	-2976

-3011	-3044	-3076	-3107	-3136	-3164	-3190	-3216	-3240	-3262

-3283	-3303	-3322	-3339	-3355	-3369	-3382	-3394	-3405	-3414

-3422	-3428	-3433	-3437	-3440	-3441	-3440	-3439	-3436	-3432

-3426

B2	6837	6960	7080	7195	7308	7416	7522	7623	7721	7816

7907	7994	8078	8158	8235	8308	8378	8444	8507	8566

8621	8673	8721	8766	8807	8845	8879	8910	8937	8960

8980	8996	9009	9018	9024	9026	9025	9020	9011	8999

8983

I1	-6886	-6875	-6864	-6852	-6839	-6825	-6810	-6794	-6777	-6760

-6741	-6722	-6702	-6681	-6659	-6636	-6612	-6588	-6562	-6536

-6509	-6480	-6451	-6421	-6391	-6359	-6326	-6293	-6258	-6223

-6187	-6150	-6112	-6073	-6033	-5993	-5951	-5909	-5866	-5822

-5777

I2	2047	2039	2032	2025	2018	2011	2005	1998	1992	1986

1980	1974	1968	1962	1957	1952	1946	1941	1936	1932

1927	1923	1918	1914	1910	1906	1902	1899	1895	1892

1889	1886	1883	1880	1877	1875	1872	1870	1868	1866

1864

I3	-607	-599	-592	-584	-577	-571	-564	-558	-552	-546

-541	-536	-531	-526	-522	-517	-513	-510	-506	-503

-500	-497	-495	-493	-491	-489	-487	-486	-485	-484

-484	-483	-483	-484	-484	-485	-486	-487	-488	-490

-492

I4	-1973	-1946	-1920	-1895	-1871	-1847	-1824	-1803	-1782	-1761

-1742	-1724	-1706	-1689	-1673	-1658	-1643	-1630	-1617	-1605

-1594	-1584	-1575	-1566	-1558	-1551	-1545	-1540	-1535	-1532

-1529	-1527	-1526	-1526	-1526	-1528	-1530	-1533	-1537	-1541

-1547

I5	-1251	-1230	-1209	-1189	-1170	-1151	-1132	-1115	-1097	-1080

-1063	-1047	-1032	-1017	-1002	-988	-975	-962	-949	-937

-925	-914	-904	-893	-884	-875	-866	-858	-850	-843

-836	-830	-825	-819	-815	-810	-807	-803	-801	-798

-797

D1	-8706	-8669	-8629	-8585	-8538	-8488	-8436	-8381	-8323	-8263

-8201	-8136	-8070	-8002	-7933	-7862	-7789	-7716	-7641	-7566

-7490	-7413	-7336	-7259	-7181	-7103	-7026	-6949	-6872	-6796

-6720	-6646	-6572	-6500	-6429	-6359	-6292	-6225	-6161	-6099

-6039

D2	-6141	-6135	-6128	-6121	-6112	-6104	-6095	-6085	-6074	-6063

-6052	-6039	-6027	-6013	-5999	-5985	-5969	-5953	-5937	-5920

-5902	-5884	-5865	-5846	-5826	-5805	-5784	-5762	-5740	-5717

-5693	-5669	-5644	-5619	-5593	-5566	-5539	-5511	-5483	-5454

-5424

E1	-1622	-1615	-1609	-1604	-1601	-1599	-1597	-1597	-1598	-1600

-1602	-1606	-1610	-1615	-1621	-1628	-1635	-1643	-1651	-1660

-1669	-1679	-1689	-1699	-1710	-1721	-1732	-1743	-1755	-1766

-1778	-1789	-1801	-1812	-1823	-1834	-1844	-1855	-1865	-1874

-1883

E2	1668	1671	1672	1674	1674	1675	1675	1675	1676	1676

1677	1678	1680	1683	1686	1690	1695	1702	1710	1719

1729	1741	1755	1771	1789	1808	1830	1855	1882	1911

1943	1978	2016	2057	2101	2148	2199	2253	2311	2372

2438

EX	-350	-343	-336	-329	-323	-317	-312	-307	-303	-299

-295	-292	-289	-286	-283	-281	-279	-277	-276	-274

-273	-272	-271	-270	-270	-269	-268	-268	-267	-267

-266	-265	-265	-264	-263	-262	-260	-259	-258	-256

-254

ES	-1166	-1139	-1114	-1091	-1070	-1050	-1032	-1016	-1001	-987

-974	-963	-953	-944	-936	-930	-923	-918	-914	-910

-907	-904	-902	-901	-899	-898	-898	-897	-896	-896

-895	-894	-893	-892	-891	-889	-886	-883	-880	-876

-871

F1	-7997	-7903	-7820	-7746	-7683	-7629	-7584	-7548	-7519	-7499

-7485	-7478	-7478	-7483	-7494	-7510	-7531	-7555	-7584	-7616

-7650	-7687	-7727	-7767	-7809	-7852	-7894	-7937	-7979	-8020

-8060	-8098	-8133	-8166	-8195	-8221	-8243	-8260	-8273	-8280

-8281

F2	619	609	600	593	586	581	577	574	572	571

571	572	574	576	579	583	587	592	597	603

609	615	622	629	636	643	650	657	664	670

677	683	690	695	701	705	710	714	717	719

721

MS	570	569	569	570	572	575	579	584	589	596

603	612	621	630	640	651	663	675	687	700

713	726	740	754	769	783	798	812	827	842

857	871	886	900	914	928	942	955	968	981

993

CS	-140	-142	-144	-147	-149	-153	-156	-160	-164	-168

-172	-177	-182	-187	-192	-198	-203	-209	-215	-221

-227	-234	-240	-247	-254	-260	-267	-274	-282	-289

-296	-304	-311	-318	-326	-333	-341	-348	-356	-364

-371

SX	1837	1834	1835	1839	1847	1858	1873	1890	1910	1934

1959	1988	2018	2051	2086	2123	2162	2203	2245	2288

2333	2378	2425	2473	2521	2570	2620	2669	2719	2769

2819	2868	2917	2966	3014	3061	3107	3153	3196	3239

3280

CX	-524	-532	-540	-550	-560	-572	-584	-598	-612	-628

-644	-661	-679	-698	-717	-737	-758	-780	-802	-824

-848	-871	-895	-920	-945	-971	-996	-1023	-1049	-1076

-1102	-1130	-1157	-1184	-1212	-1239	-1267	-1294	-1322	-1349

-1377

D0	1417	1417	1417	1416	1416	1416	1415	1415	1415	1414

1414	1413	1413	1412	1412	1412	1411	1411	1410	1410

1410	1409	1409	1408	1408	1408	1407	1407	1407	1406

1406	1406	1405	1405	1405	1405	1404	1404	1404	1404

1404

CD	-4331	-4269	-4208	-4147	-4086	-4026	-3966	-3906	-3846	-3787

-3728	-3670	-3612	-3554	-3497	-3439	-3382	-3326	-3270	-3214

-3158	-3103	-3048	-2993	-2939	-2885	-2831	-2778	-2725	-2672

-2620	-2568	-2516	-2464	-2413	-2363	-2312	-2262	-2212	-2163

-2113

DD	1870	1868	1866	1864	1862	1860	1859	1857	1855	1853

1852	1850	1848	1847	1845	1843	1842	1840	1839	1837

1836	1834	1833	1831	1830	1829	1827	1826	1825	1823

1822	1821	1820	1819	1818	1816	1815	1814	1813	1812

1811

L0	3988	3912	3842	3779	3723	3673	3630	3592	3560	3532

3510	3493	3480	3471	3466	3464	3466	3471	3479	3489

3502	3516	3532	3550	3569	3588	3608	3628	3649	3669

3689	3708	3725	3742	3757	3770	3780	3789	3794	3797

3796

J1	-2858	-2828	-2800	-2774	-2750	-2728	-2709	-2691	-2675	-2661

-2649	-2640	-2632	-2626	-2622	-2621	-2621	-2623	-2628	-2634

-2642	-2653	-2665	-2680	-2696	-2715	-2735	-2758	-2782	-2809

-2837	-2868	-2900	-2935	-2972	-3010	-3051	-3094	-3138	-3185

-3234

J2	1312	1283	1255	1229	1203	1178	1155	1133	1112	1092

1073	1055	1038	1023	1008	995	983	972	962	953

945	938	933	928	925	923	922	922	923	925

929	933	939	946	954	963	973	984	996	1010

1024

NU	2465	2479	2493	2506	2519	2532	2545	2558	2570	2582

2593	2605	2616	2626	2637	2647	2657	2667	2676	2685

2694	2703	2711	2719	2727	2734	2741	2748	2755	2761

2767	2773	2778	2784	2789	2793	2798	2802	2806	2809

2813

VX	21778	21884	21988	22090	22189	22286	22380	22472	22561	22648

22732	22814	22893	22970	23044	23116	23186	23253	23317	23379

23439	23496	23550	23602	23652	23699	23744	23786	23825	23863

23897	23930	23960	23987	24012	24034	24054	24071	24086	24099

24109

VI	20894	20918	20942	20965	20988	21011	21034	21056	21078	21100

21122	21143	21164	21185	21206	21226	21246	21266	21286	21305

21324	21343	21362	21380	21398	21416	21433	21451	21468	21485

21501	21517	21533	21549	21565	21580	21595	21610	21624	21639

21653

VP	3691	3711	3731	3751	3770	3789	3808	3826	3844	3862

3879	3897	3914	3931	3947	3963	3979	3995	4010	4025

4040	4054	4069	4083	4096	4110	4123	4136	4148	4161

4173	4184	4196	4207	4218	4228	4239	4249	4259	4268

4277

VE	3234	3239	3244	3249	3253	3258	3262	3266	3270	3275

3279	3282	3286	3290	3293	3297	3300	3303	3307	3310

3313	3315	3318	3321	3323	3326	3328	3330	3332	3334

3336	3338	3339	3341	3342	3344	3345	3346	3347	3348

3349

ESS1	-15979	-15902	-15838	-15787	-15748	-15721	-15705	-15699	-15704	-15719

-15743	-15777	-15818	-15868	-15925	-15989	-16060	-16136	-16219	-16306

-16399	-16495	-16596	-16699	-16806	-16915	-17026	-17138	-17251	-17365

-17478	-17592	-17704	-17815	-17924	-18031	-18136	-18237	-18334	-18427

-18516

ESS2	1644	1645	1646	1646	1645	1645	1645	1644	1644	1644

1645	1646	1648	1650	1653	1657	1662	1669	1676	1685

1696	1708	1722	1738	1755	1775	1797	1821	1847	1876

1908	1942	1980	2020	2063	2109	2159	2212	2268	2328

2392

Table 6 - Neutronic constants for VVER-1000 ICIS application software
TVS 36 KL-DY 3.62 % (245*3.7 %+66*3.3 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

150	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.76832	- Fi1

-0.0149325	- Fi2

K0	11483	11364	11235	11096	10955	10816	10680	10548	10419	10294

10172	10053	9935	9821	9708	9597	9487	9379	9273	9169

9066	8964	8864	8766	8669	8574	8481	8390	8301	8214

8129	8047	7966	7888	7813	7740	7669	7601	7535	7472

7412

M0	6138	6114	6091	6069	6047	6026	6006	5986	5966	5948

5929	5912	5894	5878	5862	5846	5831	5816	5802	5788

5774	5761	5748	5735	5723	5712	5700	5689	5678	5667

5657	5646	5636	5627	5617	5607	5598	5589	5580	5571

5562

B1	-2730	-2777	-2823	-2867	-2910	-2952	-2992	-3031	-3069	-3105

-3140	-3173	-3205	-3236	-3265	-3293	-3320	-3345	-3369	-3392

-3413	-3433	-3452	-3469	-3485	-3499	-3513	-3524	-3535	-3544

-3552	-3558	-3563	-3567	-3569	-3570	-3569	-3568	-3565	-3560

-3554

B2	7190	7314	7435	7553	7667	7777	7883	7986	8085	8181

8273	8362	8446	8527	8605	8679	8749	8816	8879	8938

8994	9046	9095	9140	9181	9219	9253	9283	9310	9333

9353	9369	9381	9390	9395	9396	9394	9388	9379	9366

9349

I1	-7970	-7956	-7942	-7926	-7909	-7892	-7874	-7854	-7834	-7813

-7792	-7769	-7745	-7721	-7696	-7669	-7642	-7614	-7586	-7556

-7525	-7494	-7462	-7429	-7394	-7360	-7324	-7287	-7250	-7211

-7172	-7132	-7091	-7049	-7006	-6962	-6918	-6872	-6826	-6779

-6731

I2	2192	2183	2173	2164	2156	2147	2138	2130	2122	2114

2106	2099	2091	2084	2077	2070	2063	2057	2050	2044

2038	2032	2027	2021	2016	2011	2006	2001	1996	1992

1988	1984	1980	1976	1973	1970	1966	1963	1961	1958

1956

I3	-694	-685	-676	-668	-660	-653	-645	-638	-632	-625

-619	-613	-608	-603	-598	-593	-589	-585	-581	-578

-575	-572	-570	-567	-566	-564	-563	-562	-561	-561

-561	-561	-561	-562	-563	-565	-567	-569	-571	-574

-577

I4	-2234	-2204	-2175	-2146	-2119	-2092	-2067	-2043	-2019	-1997

-1976	-1955	-1936	-1918	-1900	-1884	-1868	-1854	-1841	-1828

-1817	-1807	-1797	-1789	-1781	-1775	-1770	-1765	-1762	-1760

-1758	-1758	-1758	-1760	-1763	-1766	-1771	-1776	-1783	-1791

-1799

I5	-1456	-1433	-1410	-1387	-1365	-1344	-1324	-1304	-1284	-1265

-1247	-1230	-1213	-1196	-1180	-1165	-1150	-1136	-1123	-1110

-1098	-1086	-1075	-1065	-1055	-1045	-1037	-1029	-1021	-1014

-1008	-1002	-997	-993	-989	-985	-983	-981	-979	-978

-978

D1	-6745	-6751	-6752	-6748	-6740	-6727	-6710	-6689	-6664	-6636

-6604	-6568	-6530	-6488	-6444	-6397	-6347	-6296	-6242	-6186

-6128	-6069	-6009	-5947	-5884	-5820	-5756	-5691	-5626	-5561

-5495	-5430	-5365	-5301	-5237	-5175	-5113	-5053	-4994	-4936

-4881

D2	-4807	-4836	-4862	-4888	-4911	-4933	-4954	-4973	-4991	-5007

-5021	-5034	-5045	-5055	-5064	-5070	-5076	-5079	-5081	-5082

-5081	-5079	-5075	-5069	-5062	-5053	-5043	-5032	-5018	-5004

-4987	-4970	-4950	-4929	-4907	-4883	-4857	-4830	-4802	-4772

-4740

E1	-1650	-1641	-1633	-1627	-1623	-1619	-1618	-1617	-1618	-1620

-1623	-1627	-1631	-1637	-1644	-1651	-1659	-1668	-1677	-1687

-1697	-1707	-1718	-1729	-1740	-1751	-1762	-1773	-1784	-1795

-1805	-1815	-1825	-1835	-1843	-1852	-1859	-1866	-1872	-1878

-1882

E2	1706	1691	1678	1668	1661	1656	1654	1654	1657	1661

1668	1676	1686	1698	1711	1726	1742	1758	1776	1795

1814	1834	1855	1876	1897	1918	1939	1960	1980	2000

2020	2039	2057	2075	2091	2106	2120	2132	2143	2152

2159

EX	-392	-384	-376	-368	-361	-355	-349	-343	-338	-333

-329	-325	-322	-319	-316	-313	-311	-309	-308	-306

-305	-304	-302	-302	-301	-300	-299	-299	-298	-297

-297	-296	-295	-294	-293	-292	-291	-289	-288	-286

-283

ES	-1287	-1257	-1229	-1203	-1179	-1157	-1136	-1117	-1100	-1085

-1070	-1057	-1046	-1035	-1026	-1018	-1011	-1005	-999	-995

-991	-987	-985	-982	-980	-979	-977	-976	-975	-974

-972	-971	-969	-967	-965	-962	-959	-955	-950	-945

-939

F1	-8166	-8069	-7982	-7906	-7840	-7784	-7736	-7698	-7668	-7646

-7631	-7624	-7622	-7627	-7638	-7654	-7675	-7700	-7729	-7761

-7796	-7834	-7875	-7916	-7959	-8003	-8048	-8092	-8136	-8178

-8220	-8259	-8296	-8331	-8362	-8390	-8414	-8433	-8447	-8456

-8459

F2	635	624	615	607	600	595	590	587	585	584

583	584	585	588	591	594	598	603	608	614

620	626	633	640	647	654	661	668	675	683

689	696	703	709	714	720	725	729	733	736

738

MS	575	574	574	575	577	580	584	589	595	602

609	618	627	636	647	658	669	682	694	707

721	734	748	763	777	792	807	822	837	852

867	882	897	911	926	940	954	968	981	994

1006

CS	-134	-136	-139	-141	-144	-148	-151	-155	-159	-163

-167	-172	-176	-181	-187	-192	-197	-203	-209	-215

-221	-227	-233	-240	-247	-253	-260	-267	-274	-281

-288	-295	-302	-310	-317	-324	-332	-339	-346	-354

-361

SX	1853	1850	1851	1855	1863	1875	1889	1907	1928	1952

1978	2007	2038	2071	2107	2144	2184	2225	2268	2312

2357	2404	2451	2500	2549	2599	2649	2700	2750	2801

2852	2902	2953	3002	3051	3099	3146	3193	3238	3281

3323

CX	-507	-514	-523	-533	-543	-555	-568	-581	-596	-611

-627	-644	-662	-680	-699	-719	-740	-761	-782	-804

-827	-850	-874	-898	-923	-947	-973	-998	-1024	-1050

-1076	-1103	-1129	-1156	-1183	-1210	-1237	-1264	-1291	-1318

-1345

D0	1414	1413	1413	1412	1412	1411	1411	1411	1410	1410

1409	1409	1408	1408	1407	1407	1406	1406	1405	1405

1404	1404	1403	1403	1402	1402	1401	1401	1400	1400

1400	1399	1399	1399	1398	1398	1398	1397	1397	1397

1397

CD	-4839	-4780	-4721	-4662	-4605	-4548	-4491	-4436	-4381	-4326

-4273	-4220	-4167	-4116	-4065	-4015	-3965	-3916	-3868	-3821

-3774	-3728	-3682	-3638	-3594	-3550	-3507	-3465	-3424	-3383

-3343	-3304	-3266	-3228	-3190	-3154	-3118	-3083	-3048	-3014

-2981

DD	1862	1860	1858	1856	1853	1851	1849	1847	1845	1843

1841	1839	1837	1835	1834	1832	1830	1828	1826	1825

1823	1821	1820	1818	1816	1815	1813	1812	1810	1809

1808	1806	1805	1803	1802	1801	1800	1798	1797	1796

1795

L0	4082	4003	3931	3866	3808	3757	3712	3672	3639	3611

3588	3570	3556	3547	3542	3540	3542	3547	3555	3566

3579	3593	3610	3628	3647	3667	3688	3709	3730	3751

3771	3790	3809	3826	3841	3854	3865	3874	3880	3883

3882

J1	-2934	-2903	-2873	-2846	-2821	-2798	-2777	-2758	-2741	-2727

-2714	-2704	-2695	-2689	-2685	-2683	-2683	-2685	-2689	-2696

-2704	-2715	-2727	-2742	-2759	-2778	-2799	-2822	-2847	-2875

-2904	-2936	-2970	-3005	-3043	-3083	-3125	-3170	-3216	-3264

-3315

J2	1368	1338	1309	1281	1254	1229	1204	1181	1159	1138

1119	1100	1083	1066	1051	1038	1025	1013	1003	994

986	979	973	969	965	963	962	962	964	966

970	975	981	988	996	1006	1016	1028	1041	1056

1071

NU	2463	2477	2491	2505	2518	2531	2544	2556	2569	2580

2592	2603	2615	2625	2636	2646	2656	2666	2675	2684

2693	2702	2710	2718	2726	2733	2741	2748	2754	2761

2767	2773	2778	2783	2788	2793	2797	2802	2805	2809

2812

VX	21772	21879	21984	22086	22186	22283	22378	22471	22560	22648

22733	22815	22895	22972	23047	23120	23190	23257	23322	23384

23444	23502	23557	23609	23659	23707	23752	23795	23835	23872

23907	23940	23970	23997	24023	24045	24065	24083	24098	24111

24121

VI	20885	20909	20933	20956	20979	21002	21025	21047	21069	21091

21113	21134	21155	21176	21197	21217	21237	21257	21276	21296

21315	21333	21352	21370	21388	21406	21424	21441	21458	21475

21491	21507	21523	21539	21555	21570	21585	21600	21614	21628

21642

VP	3684	3704	3724	3744	3763	3782	3800	3819	3837	3855

3872	3889	3906	3923	3939	3956	3971	3987	4002	4017

4032	4047	4061	4075	4088	4102	4115	4127	4140	4152

4164	4176	4187	4198	4209	4220	4230	4240	4249	4259

4268

VE	3234	3239	3244	3248	3253	3258	3262	3266	3270	3275

3279	3282	3286	3290	3293	3297	3300	3303	3307	3310

3313	3315	3318	3321	3323	3326	3328	3330	3332	3334

3336	3338	3339	3341	3342	3344	3345	3346	3347	3348

3349

ESS1	-16260	-16165	-16086	-16023	-15975	-15941	-15921	-15913	-15918	-15934

-15961	-15999	-16046	-16102	-16166	-16237	-16316	-16401	-16491	-16586

-16685	-16788	-16894	-17001	-17111	-17221	-17331	-17441	-17549	-17656

-17760	-17861	-17958	-18051	-18138	-18219	-18294	-18361	-18421	-18472

-18514

ESS2	1680	1664	1651	1641	1634	1629	1627	1627	1629	1633

1640	1648	1658	1669	1682	1696	1712	1729	1746	1764

1784	1803	1823	1844	1864	1885	1906	1926	1947	1966

1986	2004	2022	2039	2055	2069	2083	2094	2105	2113

2120

Table 7 - Neutronic constants for VVER-1000 ICIS application software
TVS 36B20 3.62 % (245*3.7 %+66*3.3 %) SVP0.02 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

1	- R presence (0 – no; 1 – yes)

50	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.7822937	- Fi1

-0.0145377	- Fi2

K0	12781	12766	12758	12746	12730	12710	12687	12661	12634	12604

12574	12542	12509	12475	12439	12405	12369	12332	12295	12257

12219	12180	12141	12102	12062	12022	11982	11942	11902	11862

11819	11780	11740	11699	11658	11618	11577	11537	11496	11456

11416

M0	6541	6538	6536	6533	6529	6526	6522	6518	6514	6510

6505	6500	6495	6490	6485	6480	6474	6468	6463	6457

6451	6445	6439	6433	6426	6420	6414	6408	6401	6395

6389	6383	6376	6370	6364	6358	6352	6347	6341	6335

6330

B1	-2834	-2845	-2857	-2869	-2881	-2893	-2906	-2918	-2931	-2944

-2958	-2971	-2985	-2999	-3013	-3027	-3042	-3057	-3072	-3087

-3103	-3118	-3134	-3150	-3167	-3183	-3200	-3217	-3234	-3251

-3269	-3287	-3305	-3323	-3342	-3360	-3379	-3398	-3418	-3437

-3457

B2	7492	7522	7552	7583	7614	7646	7678	7711	7745	7780

7815	7850	7886	7923	7961	7999	8037	8077	8116	8157

8198	8240	8282	8325	8368	8413	8457	8503	8549	8595

8642	8690	8739	8788	8837	8888	8938	8990	9042	9095

9148

I1	-9398	-9395	-9392	-9390	-9389	-9387	-9386	-9386	-9386	-9387

-9388	-9389	-9391	-9393	-9396	-9399	-9403	-9407	-9411	-9416

-9421	-9427	-9433	-9440	-9447	-9454	-9462	-9471	-9479	-9489

-9498	-9508	-9519	-9530	-9541	-9553	-9566	-9578	-9591	-9605

-9619

I2	2376	2374	2371	2368	2365	2362	2360	2357	2354	2351

2348	2345	2343	2340	2337	2334	2331	2328	2325	2322

2319	2316	2313	2310	2307	2305	2302	2299	2296	2292

2289	2286	2283	2280	2277	2274	2271	2268	2265	2262

2259

I3	-869	-865	-861	-857	-853	-849	-845	-842	-839	-835

-832	-829	-826	-823	-820	-818	-815	-813	-811	-809

-807	-805	-803	-801	-800	-798	-797	-796	-795	-794

-793	-792	-792	-791	-791	-791	-791	-791	-791	-791

-791

I4	-2775	-2761	-2747	-2733	-2719	-2707	-2694	-2682	-2670	-2658

-2647	-2637	-2626	-2617	-2607	-2598	-2589	-2581	-2573	-2565

-2558	-2551	-2545	-2539	-2533	-2528	-2523	-2519	-2515	-2511

-2507	-2505	-2502	-2500	-2498	-2497	-2496	-2495	-2495	-2495

-2495

I5	-1826	-1817	-1808	-1799	-1791	-1782	-1774	-1766	-1758	-1750

-1742	-1735	-1728	-1720	-1713	-1707	-1700	-1694	-1687	-1681

-1675	-1669	-1664	-1658	-1653	-1648	-1643	-1638	-1633	-1629

-1625	-1620	-1616	-1613	-1609	-1605	-1602	-1599	-1596	-1593

-1590

D1	-5215	-5245	-5275	-5305	-5336	-5366	-5397	-5427	-5458	-5488

-5518	-5548	-5577	-5606	-5634	-5662	-5689	-5715	-5740	-5765

-5788	-5811	-5832	-5853	-5872	-5889	-5906	-5921	-5934	-5946

-5956	-5964	-5971	-5976	-5978	-5979	-5978	-5974	-5968	-5960

-5950

D2	-4052	-4096	-4139	-4181	-4222	-4261	-4300	-4338	-4374	-4410

-4444	-4477	-4510	-4541	-4571	-4600	-4628	-4654	-4680	-4705

-4728	-4751	-4772	-4793	-4812	-4830	-4847	-4863	-4878	-4892

-4905	-4916	-4927	-4936	-4945	-4952	-4958	-4963	-4968	-4971

-4972

E1	-1735	-1731	-1727	-1723	-1720	-1718	-1716	-1714	-1713	-1712

-1712	-1712	-1712	-1712	-1713	-1715	-1716	-1718	-1719	-1721

-1723	-1726	-1728	-1731	-1733	-1736	-1738	-1741	-1744	-1746

-1749	-1751	-1754	-1756	-1758	-1760	-1762	-1764	-1765	-1766

-1767

E2	1861	1848	1837	1828	1820	1813	1808	1804	1801	1799

1798	1798	1800	1801	1804	1808	1811	1816	1821	1826

1832	1838	1844	1850	1857	1863	1869	1875	1881	1887

1892	1897	1901	1905	1908	1910	1911	1912	1912	1911

1908

EX	-468	-465	-463	-460	-458	-455	-453	-451	-449	-447

-445	-443	-441	-440	-438	-437	-435	-434	-432	-431

-430	-429	-427	-426	-425	-424	-423	-422	-421	-420

-420	-419	-418	-417	-416	-415	-415	-414	-413	-412

-411

ES	-1518	-1508	-1499	-1490	-1482	-1474	-1466	-1458	-1451	-1444

-1438	-1431	-1425	-1420	-1414	-1409	-1404	-1399	-1395	-1390

-1386	-1382	-1378	-1375	-1371	-1368	-1364	-1361	-1358	-1355

-1352	-1349	-1346	-1343	-1340	-1337	-1334	-1331	-1329	-1326

-1323

F1	-8683	-8645	-8609	-8576	-8546	-8518	-8493	-8470	-8449	-8430

-8414	-8399	-8387	-8376	-8367	-8360	-8354	-8349	-8346	-8344

-8344	-8344	-8345	-8348	-8351	-8354	-8359	-8364	-8369	-8374

-8380	-8386	-8393	-8399	-8405	-8410	-8416	-8421	-8425	-8429

-8433

F2	695	691	687	683	680	677	674	672	670	668

667	665	664	663	663	663	662	662	663	663

664	664	665	666	667	668	669	670	672	673

674	676	677	678	680	681	682	684	685	686

687

MS	586	585	584	583	582	582	581	581	581	581

582	582	583	584	585	586	588	589	591	593

594	596	598	601	603	605	608	610	613	616

618	621	624	627	630	633	636	639	642	645

648

CS	-130	-131	-132	-133	-134	-135	-136	-137	-138	-139

-140	-141	-142	-143	-144	-145	-146	-148	-149	-150

-151	-153	-154	-155	-156	-158	-159	-160	-162	-163

-164	-166	-167	-169	-170	-172	-173	-175	-176	-178

-179

SX	1889	1885	1882	1880	1878	1877	1876	1876	1877	1879

1880	1883	1886	1890	1894	1898	1903	1908	1914	1920

1927	1934	1941	1949	1957	1965	1974	1983	1992	2001

2010	2020	2030	2040	2050	2060	2070	2080	2091	2101

2111

CX	-494	-497	-500	-504	-507	-511	-514	-518	-522	-525

-529	-533	-537	-541	-546	-550	-554	-559	-563	-567

-572	-577	-581	-586	-591	-596	-601	-606	-611	-616

-621	-626	-632	-637	-642	-648	-653	-659	-664	-670

-676

D0	1434	1435	1435	1435	1435	1435	1435	1435	1435	1435

1435	1435	1435	1435	1435	1435	1435	1435	1435	1435

1435	1435	1435	1434	1434	1434	1434	1434	1434	1434

1433	1433	1433	1433	1433	1433	1432	1432	1432	1432

1432

CD	-5488	-5469	-5451	-5433	-5416	-5398	-5381	-5365	-5349	-5333

-5317	-5302	-5287	-5273	-5259	-5245	-5231	-5218	-5206	-5193

-5181	-5169	-5158	-5147	-5136	-5126	-5116	-5107	-5097	-5088

-5080	-5072	-5064	-5056	-5049	-5042	-5036	-5030	-5024	-5018

-5013

DD	1892	1891	1891	1890	1890	1890	1889	1889	1888	1888

1887	1887	1886	1886	1885	1885	1884	1883	1883	1882

1882	1881	1880	1880	1879	1879	1878	1877	1877	1876

1875	1874	1874	1873	1872	1872	1871	1870	1869	1869

1868

L0	4576	4546	4518	4491	4467	4444	4422	4403	4384	4368

4352	4338	4325	4314	4303	4294	4286	4278	4272	4266

4261	4257	4254	4251	4248	4246	4245	4243	4242	4242

4241	4240	4240	4239	4238	4238	4236	4235	4233	4231

4228

J1	-3518	-3500	-3482	-3466	-3450	-3435	-3420	-3406	-3394	-3381

-3370	-3359	-3350	-3340	-3332	-3324	-3318	-3312	-3306	-3302

-3298	-3295	-3292	-3291	-3290	-3290	-3291	-3292	-3295	-3298

-3301	-3306	-3311	-3317	-3324	-3331	-3340	-3349	-3359	-3369

-3381

J2	1623	1603	1584	1565	1546	1528	1511	1494	1478	1462

1447	1433	1419	1405	1392	1380	1368	1357	1346	1336

1327	1318	1309	1301	1294	1287	1281	1275	1270	1265

1261	1258	1255	1252	1251	1249	1249	1248	1249	1250

1251

NU	2458	2464	2470	2476	2482	2488	2494	2500	2505	2511

2516	2521	2527	2532	2537	2542	2546	2551	2556	2560

2565	2569	2573	2577	2581	2585	2589	2593	2597	2600

2604	2607	2610	2613	2616	2619	2622	2625	2628	2630

2633

VX	21722	21773	21824	21874	21923	21971	22018	22064	22109	22153

22196	22238	22280	22320	22359	22398	22436	22472	22508	22542

22576	22609	22641	22672	22702	22731	22759	22786	22812	22838

22862	22886	22908	22930	22950	22970	22988	23006	23023	23039

23054

VI	20883	20890	20898	20905	20912	20920	20927	20935	20942	20949

20957	20964	20971	20978	20986	20993	21000	21007	21014	21022

21029	21036	21043	21050	21057	21064	21071	21078	21085	21092

21099	21106	21113	21120	21127	21134	21141	21148	21155	21162

21168

VP	3678	3686	3693	3700	3707	3714	3721	3728	3735	3742

3749	3755	3762	3768	3775	3781	3788	3794	3800	3806

3812	3818	3824	3830	3836	3842	3848	3853	3859	3864

3870	3875	3880	3886	3891	3896	3901	3906	3911	3916

3921

VE	3232	3235	3237	3239	3241	3243	3245	3247	3249	3251

3253	3255	3257	3259	3260	3262	3264	3265	3267	3269

3270	3272	3273	3275	3276	3277	3279	3280	3281	3282

3283	3284	3286	3287	3288	3289	3290	3290	3291	3292

3293

ESS1	-17137	-17090	-17048	-17012	-16981	-16955	-16933	-16916	-16903	-16894

-16889	-16888	-16890	-16895	-16903	-16914	-16927	-16942	-16960	-16979

-17000	-17022	-17046	-17070	-17095	-17121	-17147	-17173	-17199	-17225

-17250	-17274	-17297	-17319	-17339	-17358	-17375	-17390	-17402	-17412

-17419

ESS2	1837	1824	1813	1803	1795	1788	1783	1779	1776	1774

1773	1773	1774	1776	1779	1782	1786	1790	1795	1800

1806	1812	1818	1824	1830	1836	1843	1848	1854	1860

1865	1869	1873	1877	1880	1882	1883	1884	1883	1882

1879

Table 8 - Neutronic constants for VVER-1000 ICIS application software
TVS 40  4 % (245*4.1 %+66*3.7 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

150	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.7876131	- Fi1

-0.014639	- Fi2

K0	13837	13675	13505	13331	13158	12991	12829	12674	12524	12380

12239	12103	11971	11841	11714	11589	11467	11346	11228	11111

10995	10882	10769	10658	10549	10441	10335	10231	10128	10027

9928	9830	9735	9642	9550	9462	9375	9290	9208	9128

9051

M0	6470	6441	6412	6385	6358	6333	6308	6284	6262	6240

6219	6198	6179	6160	6142	6124	6108	6091	6076	6061

6046	6032	6018	6005	5992	5979	5967	5955	5943	5931

5920	5908	5897	5886	5874	5863	5852	5841	5829	5818

5806

B1	-2773	-2817	-2859	-2899	-2939	-2978	-3015	-3051	-3086	-3120

-3153	-3184	-3214	-3243	-3271	-3298	-3324	-3348	-3371	-3393

-3414	-3434	-3452	-3469	-3486	-3500	-3514	-3527	-3538	-3548

-3558	-3565	-3572	-3578	-3582	-3585	-3587	-3588	-3588	-3586

-3583

B2	7321	7435	7547	7655	7760	7862	7961	8056	8149	8238

8324	8407	8487	8564	8638	8708	8776	8840	8901	8959

9014	9066	9114	9160	9202	9241	9277	9310	9340	9366

9390	9410	9427	9441	9452	9460	9465	9466	9465	9460

9452

I1	-9145	-9129	-9113	-9096	-9078	-9060	-9040	-9020	-8999	-8978

-8955	-8932	-8908	-8883	-8858	-8832	-8805	-8777	-8748	-8719

-8689	-8658	-8626	-8593	-8560	-8526	-8491	-8456	-8419	-8382

-8344	-8306	-8266	-8226	-8185	-8143	-8101	-8057	-8013	-7968

-7923

I2	2411	2398	2386	2375	2363	2352	2341	2330	2320	2310

2300	2290	2281	2272	2263	2254	2245	2237	2229	2222

2214	2207	2200	2194	2187	2181	2175	2170	2164	2159

2154	2150	2145	2141	2137	2134	2130	2127	2124	2122

2119

I3	-827	-818	-809	-801	-793	-786	-779	-772	-766	-761

-755	-750	-746	-742	-738	-735	-732	-729	-727	-726

-724	-723	-723	-723	-723	-724	-725	-726	-728	-731

-733	-737	-740	-744	-748	-753	-758	-764	-770	-776

-783

I4	-2639	-2608	-2579	-2551	-2525	-2499	-2475	-2452	-2431	-2411

-2392	-2374	-2358	-2343	-2330	-2317	-2306	-2296	-2288	-2281

-2275	-2270	-2267	-2265	-2264	-2264	-2266	-2269	-2274	-2280

-2287	-2295	-2305	-2316	-2328	-2341	-2356	-2372	-2389	-2408

-2428

I5	-1879	-1852	-1826	-1800	-1775	-1751	-1728	-1705	-1684	-1663

-1643	-1624	-1605	-1588	-1571	-1555	-1540	-1526	-1513	-1500

-1489	-1478	-1467	-1458	-1450	-1442	-1435	-1429	-1424	-1420

-1416	-1413	-1411	-1410	-1410	-1411	-1412	-1414	-1417	-1421

-1426

D1	-5218	-5334	-5439	-5532	-5614	-5685	-5746	-5797	-5839	-5872

-5895	-5911	-5919	-5919	-5913	-5899	-5879	-5854	-5823	-5787

-5746	-5701	-5652	-5599	-5543	-5485	-5424	-5362	-5297	-5232

-5166	-5100	-5034	-4968	-4903	-4840	-4778	-4718	-4660	-4606

-4555

D2	-4274	-4330	-4384	-4435	-4485	-4532	-4577	-4619	-4660	-4698

-4734	-4768	-4800	-4829	-4857	-4882	-4905	-4925	-4944	-4960

-4974	-4986	-4996	-5003	-5008	-5011	-5012	-5011	-5007	-5001

-4993	-4983	-4971	-4956	-4939	-4920	-4899	-4875	-4850	-4822

-4792

E1	-1771	-1762	-1755	-1749	-1745	-1743	-1742	-1743	-1745	-1748

-1753	-1758	-1765	-1773	-1781	-1791	-1801	-1812	-1823	-1836

-1848	-1861	-1875	-1889	-1903	-1917	-1931	-1946	-1960	-1974

-1988	-2002	-2015	-2028	-2041	-2053	-2065	-2076	-2086	-2095

-2104

E2	1936	1917	1902	1891	1883	1878	1876	1878	1882	1889

1899	1911	1926	1942	1960	1981	2002	2026	2051	2076

2103	2131	2160	2189	2218	2248	2278	2308	2338	2367

2396	2424	2452	2478	2504	2528	2551	2572	2591	2609

2624

EX	-486	-476	-466	-458	-450	-443	-436	-430	-425	-420

-416	-412	-409	-406	-403	-401	-399	-398	-397	-396

-395	-395	-394	-394	-394	-394	-395	-395	-395	-395

-395	-395	-395	-395	-395	-395	-394	-393	-392	-390

-388

ES	-1571	-1538	-1507	-1478	-1452	-1427	-1405	-1385	-1367	-1351

-1336	-1323	-1312	-1302	-1294	-1286	-1280	-1275	-1271	-1268

-1265	-1264	-1263	-1262	-1262	-1262	-1262	-1263	-1263	-1264

-1264	-1264	-1264	-1263	-1262	-1260	-1258	-1254	-1250	-1245

-1239

F1	-8969	-8877	-8796	-8726	-8667	-8618	-8579	-8549	-8528	-8515

-8511	-8514	-8523	-8540	-8563	-8592	-8625	-8664	-8708	-8755

-8806	-8860	-8917	-8975	-9036	-9098	-9162	-9225	-9289	-9352

-9414	-9476	-9535	-9592	-9647	-9699	-9747	-9792	-9832	-9867

-9897

F2	733	723	714	707	701	696	693	691	690	690

691	694	697	701	706	711	718	725	732	740

749	758	768	777	787	798	808	819	829	840

851	861	871	882	891	901	910	919	927	934

941

MS	532	532	533	535	538	541	546	551	557	564

571	579	588	597	607	618	629	641	653	665

678	692	705	719	734	749	764	779	794	810

825	841	857	873	889	905	921	937	953	969

985

CS	-116	-119	-121	-124	-127	-130	-134	-137	-141	-145

-149	-153	-157	-162	-167	-171	-177	-182	-187	-193

-198	-204	-210	-216	-223	-229	-236	-242	-249	-256

-264	-271	-279	-286	-294	-302	-310	-318	-327	-335

-344

SX	1712	1713	1717	1724	1735	1748	1763	1782	1803	1826

1852	1880	1910	1942	1976	2012	2050	2089	2130	2173

2217	2263	2309	2357	2406	2456	2506	2558	2610	2663

2716	2770	2823	2878	2932	2986	3041	3095	3149	3202

3255

CX	-443	-452	-461	-471	-482	-494	-506	-519	-532	-547

-562	-577	-594	-610	-628	-646	-665	-685	-705	-725

-747	-768	-791	-814	-838	-862	-886	-912	-938	-964

-991	-1018	-1046	-1074	-1103	-1133	-1162	-1193	-1223	-1255

-1286

D0	1441	1440	1440	1439	1439	1438	1438	1437	1437	1436

1436	1435	1434	1434	1433	1433	1432	1432	1431	1431

1430	1430	1429	1429	1428	1428	1427	1427	1426	1426

1425	1425	1424	1424	1424	1423	1423	1422	1422	1422

1421

CD	-5799	-5744	-5691	-5638	-5587	-5537	-5487	-5439	-5392	-5346

-5301	-5256	-5213	-5171	-5130	-5090	-5051	-5013	-4976	-4940

-4906	-4872	-4839	-4807	-4776	-4747	-4718	-4690	-4664	-4638

-4613	-4590	-4567	-4546	-4525	-4506	-4488	-4470	-4454	-4439

-4424

DD	2014	2012	2009	2007	2005	2003	2000	1998	1996	1994

1992	1990	1988	1986	1984	1983	1981	1979	1977	1976

1974	1972	1971	1969	1967	1966	1964	1963	1962	1960

1959	1958	1956	1955	1954	1953	1952	1950	1949	1948

1947

L0	4372	4292	4220	4155	4097	4046	4002	3964	3931	3905

3884	3868	3857	3851	3848	3850	3856	3865	3877	3892

3910	3929	3951	3975	4000	4026	4054	4081	4110	4138

4166	4193	4220	4245	4269	4292	4312	4330	4346	4359

4369

J1	-3424	-3390	-3358	-3329	-3302	-3279	-3258	-3240	-3225	-3213

-3204	-3197	-3193	-3192	-3194	-3199	-3206	-3216	-3229	-3245

-3264	-3285	-3309	-3336	-3366	-3399	-3434	-3473	-3514	-3557

-3604	-3654	-3706	-3761	-3819	-3880	-3943	-4009	-4078	-4150

-4225

J2	1542	1508	1477	1446	1417	1389	1363	1338	1314	1291

1270	1251	1232	1215	1200	1185	1172	1161	1150	1141

1134	1127	1122	1119	1116	1116	1116	1118	1121	1125

1131	1138	1147	1157	1168	1180	1194	1209	1226	1244

1263

NU	2460	2472	2485	2497	2509	2521	2532	2544	2555	2566

2577	2587	2597	2607	2617	2627	2636	2645	2654	2663

2671	2680	2688	2696	2703	2711	2718	2725	2731	2738

2744	2750	2756	2762	2767	2772	2777	2782	2787	2791

2795

VX	21752	21849	21945	22038	22129	22218	22305	22390	22473	22554

22633	22710	22784	22857	22927	22996	23062	23126	23188	23248

23306	23362	23416	23468	23518	23565	23611	23654	23696	23735

23772	23807	23840	23871	23900	23927	23952	23974	23995	24014

24030

VI	20869	20889	20910	20930	20950	20970	20990	21010	21030	21049

21069	21088	21107	21126	21145	21164	21182	21200	21219	21237

21255	21273	21290	21308	21325	21343	21360	21377	21394	21410

21427	21443	21459	21476	21492	21507	21523	21539	21554	21570

21585

VP	3671	3688	3706	3723	3740	3757	3773	3790	3806	3822

3838	3853	3869	3884	3899	3914	3928	3943	3957	3971

3985	3999	4012	4026	4039	4052	4064	4077	4089	4101

4113	4125	4137	4148	4159	4170	4181	4192	4202	4212

4222

VE	3234	3238	3242	3247	3251	3255	3259	3263	3266	3270

3274	3277	3281	3284	3287	3291	3294	3297	3300	3303

3305	3308	3311	3313	3316	3318	3320	3323	3325	3327

3329	3331	3332	3334	3336	3337	3339	3340	3341	3342

3343

ESS1	-17498	-17405	-17331	-17273	-17232	-17206	-17196	-17199	-17217	-17247

-17289	-17343	-17408	-17482	-17567	-17660	-17760	-17869	-17984	-18104

-18230	-18361	-18495	-18632	-18772	-18914	-19057	-19200	-19342	-19484

-19623	-19761	-19895	-20025	-20151	-20272	-20386	-20494	-20595	-20687

-20771

ESS2	1914	1895	1879	1867	1859	1853	1851	1852	1856	1863

1872	1884	1898	1914	1932	1952	1974	1997	2021	2047

2074	2101	2129	2158	2188	2217	2247	2277	2306	2335

2364	2392	2419	2446	2471	2495	2517	2538	2557	2575

2590

Table 9 - Neutronic constants for VVER-1000 ICIS application software
TVS 40 KL-B 4 % (245*4.1 %+66*3.7 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

150	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.7482721	- Fi1

-0.0151073	- Fi2

K0	10696	10589	10476	10355	10231	10108	9989	9872	9758	9647

9538	9432	9328	9225	9124	9025	8927	8830	8735	8640

8547	8455	8364	8274	8185	8097	8011	7926	7843	7760

7680	7601	7524	7448	7374	7302	7232	7164	7098	7034

6972

M0	5893	5874	5856	5838	5821	5804	5787	5771	5756	5741

5726	5712	5698	5684	5671	5658	5646	5634	5622	5610

5599	5588	5578	5567	5557	5547	5537	5528	5519	5510

5501	5492	5483	5475	5466	5458	5450	5442	5434	5426

5418

B1	-2588	-2633	-2677	-2720	-2762	-2802	-2841	-2879	-2915	-2951

-2985	-3018	-3049	-3080	-3109	-3137	-3164	-3189	-3213	-3236

-3258	-3279	-3298	-3316	-3333	-3349	-3363	-3376	-3388	-3399

-3408	-3416	-3423	-3429	-3433	-3437	-3439	-3440	-3439	-3437

-3435

B2	6794	6913	7028	7141	7250	7356	7459	7558	7654	7747

7837	7923	8006	8086	8163	8236	8306	8373	8436	8496

8553	8607	8657	8704	8748	8788	8826	8860	8890	8918

8942	8963	8981	8995	9006	9014	9019	9020	9018	9013

9004

I1	-6887	-6879	-6870	-6861	-6851	-6840	-6827	-6815	-6801	-6786

-6770	-6754	-6736	-6718	-6698	-6678	-6657	-6635	-6612	-6588

-6564	-6538	-6512	-6484	-6456	-6427	-6397	-6366	-6334	-6301

-6267	-6233	-6197	-6161	-6124	-6085	-6046	-6006	-5965	-5924

-5881

I2	2049	2042	2035	2028	2022	2015	2009	2003	1996	1991

1985	1979	1973	1968	1963	1958	1953	1948	1943	1938

1934	1929	1925	1921	1917	1913	1909	1906	1902	1899

1895	1892	1889	1886	1884	1881	1879	1876	1874	1872

1870

I3	-547	-541	-535	-530	-524	-519	-514	-509	-505	-501

-496	-493	-489	-485	-482	-479	-476	-474	-471	-469

-467	-465	-464	-463	-462	-461	-460	-460	-459	-459

-459	-460	-461	-461	-462	-464	-465	-467	-469	-471

-473

I4	-1790	-1768	-1747	-1727	-1708	-1690	-1672	-1655	-1638	-1622

-1607	-1593	-1580	-1567	-1555	-1543	-1533	-1523	-1514	-1505

-1497	-1490	-1484	-1478	-1473	-1469	-1466	-1463	-1461	-1460

-1459	-1459	-1460	-1462	-1464	-1467	-1471	-1475	-1480	-1486

-1493

I5	-1177	-1160	-1142	-1125	-1109	-1093	-1077	-1062	-1047	-1033

-1019	-1005	-992	-979	-967	-955	-943	-932	-921	-911

-901	-891	-882	-873	-865	-857	-850	-843	-836	-830

-824	-818	-813	-808	-804	-800	-797	-794	-791	-789

-787

D1	-8766	-8741	-8712	-8680	-8645	-8607	-8566	-8523	-8477	-8429

-8378	-8326	-8271	-8214	-8155	-8094	-8032	-7968	-7903	-7836

-7768	-7700	-7630	-7559	-7487	-7415	-7342	-7268	-7195	-7121

-7046	-6972	-6898	-6824	-6751	-6677	-6605	-6533	-6462	-6391

-6322

D2	-6191	-6186	-6181	-6175	-6168	-6161	-6153	-6145	-6136	-6126

-6116	-6105	-6094	-6082	-6069	-6056	-6042	-6028	-6013	-5997

-5981	-5964	-5946	-5928	-5910	-5890	-5870	-5850	-5829	-5807

-5785	-5762	-5738	-5714	-5690	-5664	-5638	-5612	-5584	-5557

-5528

E1	-1511	-1507	-1503	-1501	-1499	-1498	-1499	-1500	-1502	-1505

-1508	-1513	-1518	-1524	-1530	-1537	-1545	-1553	-1562	-1571

-1581	-1591	-1601	-1612	-1623	-1635	-1646	-1658	-1670	-1682

-1695	-1707	-1720	-1732	-1745	-1757	-1770	-1782	-1794	-1806

-1817

E2	1452	1454	1456	1459	1461	1464	1468	1472	1476	1481

1487	1493	1500	1508	1517	1526	1537	1549	1561	1575

1591	1607	1625	1644	1665	1687	1711	1736	1763	1792

1823	1855	1890	1926	1964	2005	2048	2093	2140	2190

2242

EX	-324	-317	-311	-306	-301	-296	-292	-288	-284	-281

-278	-275	-272	-270	-268	-266	-265	-264	-263	-262

-261	-260	-259	-259	-258	-258	-258	-257	-257	-257

-256	-256	-256	-255	-254	-254	-253	-252	-251	-249

-248

ES	-1083	-1060	-1039	-1020	-1002	-985	-970	-956	-943	-932

-921	-912	-904	-896	-890	-884	-879	-875	-872	-869

-867	-865	-863	-862	-861	-861	-861	-860	-860	-860

-860	-860	-860	-859	-858	-857	-855	-853	-851	-848

-844

F1	-7432	-7356	-7289	-7231	-7181	-7139	-7105	-7078	-7058	-7044

-7037	-7036	-7040	-7050	-7064	-7083	-7106	-7132	-7163	-7196

-7232	-7270	-7311	-7353	-7396	-7440	-7485	-7531	-7576	-7621

-7664	-7707	-7749	-7788	-7825	-7860	-7892	-7920	-7945	-7966

-7983

F2	545	537	531	525	521	517	515	513	512	511

512	513	515	518	521	524	528	533	538	543

549	555	562	568	575	582	589	596	603	610

617	624	631	638	644	651	657	662	668	673

677

MS	504	504	505	506	508	511	515	519	525	531

537	544	552	561	570	579	589	600	611	622

634	646	659	672	685	698	712	726	739	754

768	782	797	811	825	840	854	868	883	897

911

CS	-122	-124	-126	-128	-130	-133	-136	-139	-142	-146

-149	-153	-157	-161	-165	-170	-174	-179	-184	-189

-195	-200	-206	-211	-217	-223	-229	-236	-242	-249

-256	-262	-269	-276	-284	-291	-298	-306	-314	-321

-329

SX	1618	1618	1620	1626	1634	1645	1658	1674	1693	1713

1736	1761	1788	1817	1848	1881	1915	1951	1988	2027

2067	2108	2150	2193	2238	2283	2329	2375	2422	2470

2518	2566	2615	2664	2712	2761	2809	2858	2906	2953

3000

CX	-456	-462	-470	-478	-487	-496	-507	-518	-530	-542

-556	-570	-584	-600	-616	-632	-650	-667	-686	-705

-725	-745	-766	-787	-809	-832	-855	-878	-902	-926

-951	-976	-1002	-1028	-1054	-1081	-1109	-1136	-1164	-1192

-1221

D0	1420	1419	1419	1419	1418	1418	1418	1417	1417	1416

1416	1415	1415	1414	1414	1414	1413	1413	1412	1412

1411	1411	1411	1410	1410	1409	1409	1408	1408	1408

1407	1407	1407	1406	1406	1406	1406	1405	1405	1405

1405

CD	-4149	-4100	-4051	-4002	-3953	-3904	-3855	-3806	-3757	-3709

-3660	-3611	-3562	-3513	-3464	-3416	-3367	-3318	-3269	-3221

-3172	-3123	-3075	-3026	-2977	-2929	-2880	-2832	-2783	-2734

-2686	-2637	-2589	-2540	-2492	-2443	-2395	-2346	-2298	-2250

-2201

DD	1876	1874	1872	1870	1869	1867	1865	1863	1861	1860

1858	1856	1854	1853	1851	1849	1848	1846	1845	1843

1842	1840	1839	1837	1836	1834	1833	1831	1830	1829

1827	1826	1825	1824	1822	1821	1820	1819	1818	1816

1815

L0	3740	3673	3612	3557	3508	3465	3427	3394	3366	3342

3323	3308	3297	3290	3286	3285	3288	3293	3301	3311

3323	3337	3352	3369	3388	3407	3427	3447	3468	3488

3509	3529	3548	3567	3584	3600	3614	3627	3637	3645

3651

J1	-2526	-2501	-2477	-2456	-2436	-2419	-2403	-2389	-2377	-2366

-2358	-2352	-2347	-2345	-2344	-2345	-2348	-2353	-2360	-2368

-2379	-2391	-2406	-2422	-2440	-2460	-2482	-2506	-2532	-2559

-2589	-2620	-2653	-2689	-2726	-2765	-2805	-2848	-2893	-2939

-2988

J2	1228	1202	1177	1154	1131	1109	1088	1068	1049	1032

1015	999	984	971	958	946	936	926	917	910

903	898	893	889	887	885	885	885	887	890

893	898	903	910	918	926	936	947	958	971

985

NU	2464	2477	2489	2501	2513	2525	2536	2548	2559	2570

2580	2591	2601	2611	2621	2630	2639	2649	2657	2666

2674	2683	2691	2698	2706	2713	2720	2727	2734	2740

2746	2752	2758	2764	2769	2774	2779	2784	2788	2792

2796

VX	21768	21865	21959	22052	22142	22230	22317	22401	22483	22563

22641	22716	22790	22862	22931	22999	23064	23127	23188	23248

23305	23359	23412	23463	23512	23558	23603	23645	23685	23724

23760	23794	23826	23856	23883	23909	23933	23954	23974	23991

24006

VI	20892	20913	20933	20954	20974	20994	21014	21034	21054	21074

21093	21112	21131	21150	21169	21188	21206	21225	21243	21261

21279	21297	21315	21332	21350	21367	21384	21401	21418	21434

21451	21467	21484	21500	21516	21531	21547	21562	21578	21593

21608

VP	3689	3706	3724	3741	3758	3775	3792	3809	3825	3841

3857	3873	3888	3904	3919	3934	3949	3963	3978	3992

4006	4020	4033	4047	4060	4073	4086	4099	4111	4123

4135	4147	4159	4170	4182	4193	4204	4214	4225	4235

4245

VE	3234	3238	3243	3247	3251	3255	3259	3263	3267	3271

3275	3278	3282	3285	3288	3292	3295	3298	3301	3304

3306	3309	3312	3314	3317	3319	3321	3324	3326	3328

3330	3331	3333	3335	3336	3338	3339	3341	3342	3343

3344

ESS1	-14861	-14810	-14770	-14741	-14721	-14712	-14712	-14721	-14739	-14766

-14801	-14843	-14893	-14949	-15013	-15083	-15158	-15240	-15327	-15418

-15514	-15615	-15719	-15827	-15938	-16052	-16168	-16286	-16406	-16528

-16650	-16773	-16897	-17021	-17144	-17266	-17388	-17508	-17626	-17742

-17856

ESS2	1424	1425	1427	1429	1431	1434	1437	1440	1445	1449

1455	1461	1468	1476	1485	1494	1505	1517	1530	1544

1559	1575	1593	1612	1633	1655	1678	1703	1730	1759

1789	1821	1855	1890	1928	1968	2009	2053	2099	2148

2198

Table 10 - Neutronic constants for VVER-1000 ICIS application software
TVS 40 KL-DY 4 % (245*4.1 %+66*3.7 %) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

150	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.7571623	- Fi1

-0.0145703	- Fi2

K0	11746	11626	11498	11362	11223	11086	10952	10822	10695	10572

10452	10334	10218	10105	9994	9884	9776	9669	9564	9459

9357	9255	9155	9055	8958	8861	8766	8673	8581	8490

8401	8314	8229	8146	8064	7985	7908	7833	7760	7689

7621

M0	6145	6123	6101	6079	6059	6039	6019	6000	5982	5964

5946	5929	5913	5897	5881	5866	5851	5837	5823	5809

5796	5783	5770	5758	5746	5734	5723	5711	5700	5689

5679	5668	5658	5648	5637	5627	5618	5608	5598	5588

5579

B1	-2716	-2762	-2806	-2849	-2891	-2931	-2970	-3008	-3045	-3080

-3114	-3147	-3179	-3210	-3239	-3267	-3294	-3319	-3343	-3366

-3388	-3409	-3428	-3446	-3463	-3478	-3493	-3506	-3518	-3528

-3538	-3546	-3553	-3558	-3563	-3566	-3568	-3568	-3568	-3566

-3563

B2	7166	7285	7401	7513	7622	7728	7830	7930	8026	8118

8208	8294	8377	8456	8533	8606	8676	8742	8805	8865

8922	8975	9025	9072	9116	9156	9193	9227	9257	9285

9309	9329	9347	9361	9371	9379	9383	9384	9382	9376

9368

I1	-7937	-7928	-7917	-7906	-7894	-7881	-7867	-7852	-7836	-7820

-7802	-7783	-7764	-7743	-7722	-7700	-7676	-7652	-7627	-7601

-7574	-7546	-7517	-7487	-7457	-7425	-7392	-7359	-7325	-7289

-7253	-7216	-7178	-7138	-7098	-7057	-7016	-6973	-6929	-6884

-6839

I2	2196	2187	2178	2169	2160	2151	2142	2134	2126	2118

2110	2103	2095	2088	2081	2074	2068	2061	2055	2049

2043	2037	2032	2026	2021	2016	2012	2007	2003	1998

1994	1991	1987	1983	1980	1977	1974	1972	1969	1967

1965

I3	-625	-618	-611	-605	-598	-592	-587	-581	-576	-571

-567	-563	-559	-555	-551	-548	-545	-542	-540	-538

-536	-534	-532	-531	-530	-530	-529	-529	-530	-530

-531	-532	-533	-534	-536	-538	-540	-543	-546	-549

-552

I4	-2022	-1998	-1975	-1952	-1930	-1910	-1890	-1871	-1852	-1835

-1818	-1803	-1788	-1774	-1761	-1749	-1738	-1727	-1718	-1709

-1701	-1694	-1688	-1683	-1679	-1675	-1673	-1671	-1670	-1670

-1671	-1673	-1676	-1679	-1683	-1689	-1695	-1702	-1709	-1718

-1728

I5	-1366	-1346	-1326	-1307	-1288	-1270	-1253	-1236	-1219	-1203

-1188	-1173	-1158	-1144	-1131	-1118	-1106	-1094	-1083	-1072

-1062	-1052	-1043	-1034	-1026	-1018	-1011	-1004	-998	-993

-988	-983	-979	-976	-973	-970	-968	-967	-966	-965

-965

D1	-6836	-6852	-6863	-6870	-6871	-6869	-6862	-6851	-6835	-6816

-6794	-6767	-6738	-6705	-6669	-6630	-6589	-6545	-6498	-6449

-6399	-6346	-6291	-6235	-6177	-6118	-6058	-5997	-5935	-5872

-5809	-5745	-5682	-5618	-5554	-5491	-5428	-5365	-5304	-5243

-5183

D2	-4911	-4933	-4954	-4974	-4993	-5010	-5026	-5042	-5055	-5068

-5080	-5090	-5099	-5107	-5114	-5120	-5124	-5127	-5130	-5130

-5130	-5129	-5126	-5122	-5117	-5111	-5104	-5095	-5086	-5075

-5063	-5049	-5035	-5019	-5003	-4985	-4965	-4945	-4924	-4901

-4877

E1	-1544	-1536	-1530	-1526	-1522	-1520	-1519	-1519	-1521	-1523

-1526	-1531	-1536	-1542	-1548	-1556	-1564	-1573	-1582	-1592

-1602	-1612	-1623	-1634	-1646	-1657	-1669	-1681	-1692	-1704

-1715	-1727	-1738	-1748	-1759	-1769	-1778	-1787	-1796	-1804

-1811

E2	1520	1505	1493	1483	1476	1472	1470	1470	1473	1477

1484	1492	1502	1514	1527	1542	1558	1575	1593	1612

1631	1652	1673	1694	1716	1739	1761	1783	1806	1828

1850	1871	1892	1912	1932	1950	1968	1984	2000	2014

2026

EX	-362	-355	-348	-342	-336	-330	-325	-321	-317	-313

-309	-306	-304	-301	-299	-297	-295	-294	-292	-291

-290	-290	-289	-288	-288	-287	-287	-287	-286	-286

-286	-285	-285	-284	-284	-283	-282	-281	-280	-278

-276

ES	-1194	-1169	-1145	-1123	-1102	-1083	-1066	-1050	-1036	-1022

-1010	-1000	-990	-982	-974	-967	-962	-957	-953	-949

-946	-944	-942	-940	-939	-938	-937	-937	-936	-936

-935	-934	-933	-932	-931	-929	-926	-924	-920	-916

-911

F1	-7589	-7510	-7440	-7379	-7327	-7283	-7247	-7218	-7197	-7182

-7174	-7172	-7176	-7185	-7199	-7218	-7241	-7268	-7299	-7333

-7369	-7409	-7450	-7493	-7537	-7583	-7629	-7676	-7722	-7768

-7814	-7858	-7900	-7941	-7980	-8016	-8049	-8079	-8105	-8127

-8145

F2	557	549	542	536	532	528	525	523	521	521

521	523	524	527	530	534	538	542	547	553

559	565	571	578	585	592	599	606	613	620

627	635	641	648	655	661	667	673	678	683

687

MS	509	509	509	511	513	516	520	524	530	536

542	550	558	566	576	585	596	606	617	629

641	653	666	679	692	706	720	734	748	762

777	792	806	821	836	850	865	879	894	908

923

CS	-118	-119	-121	-124	-126	-129	-132	-135	-138	-141

-145	-148	-152	-156	-161	-165	-170	-174	-179	-184

-189	-195	-200	-206	-211	-217	-223	-229	-236	-242

-249	-255	-262	-269	-276	-283	-290	-298	-305	-313

-320

SX	1633	1632	1635	1641	1649	1660	1674	1690	1709	1730

1753	1778	1806	1835	1867	1900	1934	1971	2009	2048

2088	2130	2173	2217	2262	2308	2355	2402	2450	2499

2547	2597	2646	2696	2745	2795	2844	2894	2942	2991

3039

CX	-442	-448	-456	-464	-473	-483	-493	-504	-516	-528

-541	-555	-570	-585	-601	-617	-634	-652	-670	-689

-708	-728	-748	-769	-790	-812	-835	-858	-881	-905

-929	-954	-979	-1004	-1030	-1056	-1083	-1110	-1137	-1164

-1192

D0	1416	1416	1415	1415	1414	1414	1413	1413	1412	1412

1411	1411	1410	1410	1409	1409	1408	1408	1407	1407

1406	1406	1405	1405	1404	1404	1403	1403	1402	1402

1401	1401	1401	1400	1400	1399	1399	1399	1398	1398

1398

CD	-4624	-4574	-4524	-4475	-4427	-4379	-4331	-4285	-4238	-4193

-4147	-4103	-4059	-4015	-3972	-3930	-3888	-3847	-3806	-3766

-3726	-3687	-3649	-3611	-3574	-3537	-3501	-3465	-3430	-3395

-3361	-3327	-3295	-3262	-3230	-3199	-3168	-3138	-3109	-3080

-3051

DD	1869	1867	1865	1863	1861	1858	1856	1854	1852	1850

1848	1846	1845	1843	1841	1839	1837	1835	1833	1832

1830	1828	1826	1825	1823	1821	1820	1818	1817	1815

1814	1812	1810	1809	1808	1806	1805	1803	1802	1801

1799

L0	3827	3758	3695	3639	3588	3543	3504	3470	3440	3416

3396	3381	3369	3362	3358	3357	3359	3365	3372	3383

3395	3410	3426	3443	3462	3482	3502	3523	3544	3566

3587	3607	3627	3646	3664	3680	3695	3708	3718	3727

3733

J1	-2593	-2566	-2542	-2519	-2498	-2479	-2463	-2448	-2435	-2424

-2415	-2408	-2403	-2400	-2399	-2400	-2403	-2408	-2414	-2423

-2434	-2446	-2461	-2478	-2496	-2517	-2539	-2564	-2590	-2619

-2649	-2681	-2716	-2752	-2790	-2830	-2873	-2917	-2963	-3011

-3061

J2	1281	1254	1228	1203	1179	1156	1134	1114	1094	1075

1058	1041	1026	1012	999	986	975	965	956	948

941	936	931	927	925	923	923	923	925	928

931	936	942	949	957	966	976	988	1000	1013

1028

NU	2462	2475	2488	2500	2512	2524	2535	2547	2558	2569

2579	2590	2600	2610	2620	2629	2639	2648	2657	2665

2674	2682	2690	2698	2705	2713	2720	2727	2733	2740

2746	2752	2758	2763	2769	2774	2778	2783	2788	2792

2796

VX	21763	21860	21955	22048	22139	22228	22315	22400	22482	22563

22641	22717	22792	22864	22934	23002	23067	23131	23193	23252

23310	23365	23418	23469	23518	23565	23610	23653	23694	23732

23769	23803	23835	23865	23893	23919	23943	23965	23984	24002

24017

VI	20883	20904	20925	20945	20965	20986	21006	21025	21045	21065

21084	21103	21122	21141	21160	21179	21197	21216	21234	21252

21270	21288	21306	21323	21340	21358	21375	21392	21408	21425

21441	21458	21474	21490	21506	21522	21537	21553	21568	21583

21598

VP	3682	3700	3717	3734	3751	3768	3785	3802	3818	3834

3850	3866	3881	3897	3912	3927	3941	3956	3970	3985

3998	4012	4026	4039	4052	4065	4078	4091	4103	4115

4127	4139	4151	4162	4173	4184	4195	4206	4216	4226

4236

VE	3234	3238	3243	3247	3251	3255	3259	3263	3267	3271

3275	3278	3282	3285	3288	3292	3295	3298	3301	3304

3306	3309	3312	3314	3317	3319	3321	3324	3326	3328

3330	3331	3333	3335	3336	3338	3339	3341	3342	3343

3344

ESS1	-15196	-15117	-15052	-15002	-14964	-14940	-14928	-14927	-14938	-14959

-14990	-15031	-15080	-15138	-15204	-15277	-15356	-15442	-15533	-15629

-15729	-15834	-15941	-16052	-16164	-16279	-16394	-16510	-16626	-16741

-16855	-16967	-17077	-17184	-17288	-17388	-17484	-17574	-17659	-17737

-17809

ESS2	1494	1479	1466	1456	1448	1443	1441	1441	1443	1447

1453	1461	1470	1481	1494	1508	1524	1540	1558	1577

1596	1616	1637	1659	1680	1702	1724	1747	1769	1791

1813	1834	1855	1875	1895	1913	1931	1948	1963	1977

1990

Table 11 - Neutronic constants for VVER-1000 ICIS application software
TVS 40B20 4 % (245*4.1 %+66*3.7 %) SVP0.02 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

1	- R presence (0 – no; 1 – yes)

50	 -burnup increment (*0.01 MWd/kgU)

41	 - number of burnup increments DD1=0 PK8=0.985

0.7711229	- Fi1

-0.0142254	- Fi2

K0	13019	13001	12989	12973	12953	12931	12906	12879	12850	12820

12789	12757	12723	12690	12654	12620	12585	12549	12512	12476

12438	12401	12363	12325	12287	12249	12210	12172	12132	12094

12055	12016	11976	11937	11898	11859	11820	11781	11741	11702

11663

M0	6538	6535	6532	6529	6525	6522	6518	6514	6510	6505

6501	6496	6492	6487	6482	6477	6471	6466	6461	6455

6450	6444	6438	6433	6427	6421	6415	6410	6404	6398

6392	6387	6381	6375	6369	6364	6358	6353	6348	6342

6337

B1	-2827	-2836	-2846	-2856	-2866	-2876	-2887	-2898	-2909	-2921

-2932	-2945	-2957	-2970	-2983	-2996	-3010	-3023	-3038	-3052

-3067	-3082	-3097	-3113	-3129	-3145	-3161	-3178	-3195	-3213

-3230	-3248	-3266	-3285	-3304	-3323	-3342	-3362	-3382	-3402

-3423

B2	7474	7497	7522	7547	7574	7601	7629	7657	7687	7717

7748	7780	7813	7846	7880	7916	7952	7988	8026	8064

8103	8143	8184	8226	8268	8312	8356	8401	8446	8493

8540	8588	8637	8687	8737	8789	8841	8894	8948	9002

9058

I1	-9332	-9328	-9324	-9320	-9317	-9315	-9313	-9312	-9310	-9310

-9310	-9310	-9311	-9312	-9314	-9316	-9319	-9322	-9325	-9329

-9334	-9339	-9344	-9350	-9356	-9363	-9370	-9378	-9386	-9395

-9404	-9413	-9423	-9434	-9444	-9456	-9468	-9480	-9493	-9506

-9519

I2	2374	2371	2368	2365	2362	2359	2357	2354	2351	2348

2345	2342	2340	2337	2334	2331	2329	2326	2323	2320

2317	2315	2312	2309	2307	2304	2301	2298	2296	2293

2290	2288	2285	2282	2280	2277	2275	2272	2269	2267

2264

I3	-775	-772	-769	-765	-762	-760	-757	-754	-751	-749

-746	-744	-742	-740	-738	-736	-734	-732	-731	-729

-728	-726	-725	-724	-723	-722	-721	-720	-720	-719

-719	-718	-718	-718	-718	-718	-718	-718	-719	-719

-720

I4	-2486	-2475	-2464	-2453	-2443	-2433	-2423	-2413	-2404	-2395

-2387	-2379	-2371	-2363	-2356	-2349	-2343	-2336	-2330	-2325

-2319	-2314	-2310	-2305	-2301	-2298	-2294	-2291	-2288	-2286

-2284	-2282	-2281	-2279	-2279	-2278	-2278	-2278	-2278	-2279

-2280

I5	-1700	-1692	-1685	-1677	-1670	-1663	-1656	-1649	-1643	-1636

-1630	-1624	-1618	-1612	-1606	-1600	-1595	-1589	-1584	-1579

-1574	-1569	-1564	-1560	-1556	-1551	-1547	-1543	-1540	-1536

-1532	-1529	-1526	-1523	-1520	-1517	-1514	-1512	-1509	-1507

-1505

D1	-5395	-5415	-5437	-5460	-5484	-5509	-5535	-5562	-5589	-5616

-5644	-5673	-5702	-5730	-5759	-5788	-5817	-5845	-5873	-5901

-5928	-5954	-5980	-6004	-6028	-6051	-6073	-6093	-6112	-6130

-6146	-6160	-6173	-6184	-6193	-6200	-6204	-6207	-6207	-6205

-6200

D2	-4241	-4265	-4289	-4312	-4336	-4360	-4383	-4407	-4430	-4454

-4477	-4500	-4523	-4546	-4569	-4592	-4615	-4637	-4660	-4682

-4705	-4727	-4749	-4772	-4794	-4816	-4838	-4860	-4881	-4903

-4925	-4946	-4968	-4989	-5010	-5032	-5053	-5074	-5095	-5116

-5137

E1	-1616	-1613	-1611	-1609	-1607	-1606	-1605	-1605	-1604	-1604

-1604	-1604	-1605	-1606	-1606	-1608	-1609	-1610	-1612	-1614

-1616	-1618	-1620	-1622	-1624	-1627	-1629	-1632	-1634	-1637

-1639	-1642	-1645	-1647	-1650	-1652	-1655	-1657	-1660	-1662

-1664

E2	1631	1627	1623	1620	1617	1615	1613	1612	1612	1611

1612	1612	1613	1614	1616	1618	1621	1623	1626	1629

1633	1636	1640	1644	1648	1653	1657	1662	1666	1671

1676	1681	1686	1691	1695	1700	1705	1710	1714	1719

1723

EX	-429	-426	-424	-422	-420	-418	-416	-415	-413	-411

-410	-408	-407	-405	-404	-403	-402	-401	-399	-398

-397	-397	-396	-395	-394	-393	-392	-392	-391	-390

-390	-389	-388	-388	-387	-387	-386	-385	-385	-384

-384

ES	-1397	-1390	-1382	-1375	-1368	-1362	-1355	-1349	-1343	-1338

-1333	-1327	-1322	-1318	-1313	-1309	-1305	-1301	-1297	-1293

-1290	-1286	-1283	-1280	-1277	-1274	-1271	-1268	-1266	-1263

-1261	-1258	-1256	-1253	-1251	-1249	-1246	-1244	-1242	-1239

-1237

F1	-8051	-8021	-7993	-7967	-7943	-7922	-7902	-7884	-7869	-7855

-7843	-7832	-7823	-7816	-7809	-7805	-7801	-7799	-7798	-7798

-7799	-7800	-7803	-7806	-7810	-7815	-7820	-7826	-7832	-7838

-7844	-7851	-7858	-7864	-7871	-7878	-7884	-7890	-7895	-7901

-7905

F2	609	605	602	600	597	595	593	592	590	589

588	587	587	586	586	586	586	587	587	588

588	589	590	591	592	593	594	595	596	598

599	600	601	603	604	605	606	607	608	609

610

MS	519	518	518	517	517	517	517	517	517	518

518	519	520	521	522	523	524	526	527	529

530	532	534	536	538	540	542	544	547	549

551	554	556	559	561	564	567	569	572	575

577

CS	-114	-115	-116	-117	-117	-118	-119	-120	-121	-122

-122	-123	-124	-125	-126	-127	-128	-129	-130	-131

-132	-133	-134	-135	-136	-137	-138	-139	-140	-142

-143	-144	-145	-146	-147	-149	-150	-151	-152	-154

-155

SX	1666	1663	1662	1661	1660	1660	1661	1662	1663	1665

1667	1670	1673	1677	1680	1685	1689	1694	1700	1705

1711	1717	1724	1731	1738	1745	1753	1760	1768	1776

1785	1793	1802	1810	1819	1828	1837	1846	1856	1865

1874

CX	-432	-435	-438	-440	-443	-446	-449	-452	-455	-458

-462	-465	-468	-472	-475	-479	-482	-486	-489	-493

-497	-501	-505	-509	-513	-517	-521	-525	-529	-533

-537	-542	-546	-551	-555	-560	-564	-569	-574	-578

-583

D0	1437	1437	1437	1437	1437	1437	1437	1437	1437	1437

1437	1437	1437	1437	1437	1437	1437	1437	1437	1437

1437	1437	1437	1436	1436	1436	1436	1436	1436	1436

1435	1435	1435	1435	1435	1435	1434	1434	1434	1434

1434

CD	-5206	-5190	-5175	-5159	-5144	-5130	-5115	-5101	-5088	-5074

-5061	-5048	-5036	-5024	-5012	-5000	-4989	-4978	-4967	-4957

-4947	-4937	-4928	-4919	-4910	-4901	-4893	-4885	-4878	-4870

-4863	-4857	-4850	-4844	-4838	-4833	-4828	-4823	-4818	-4814

-4810

DD	1897	1896	1896	1896	1895	1895	1895	1894	1894	1894

1893	1893	1892	1892	1891	1891	1890	1890	1889	1889

1888	1887	1887	1886	1885	1885	1884	1883	1883	1882

1881	1880	1879	1879	1878	1877	1876	1875	1874	1873

1872

L0	4278	4252	4228	4205	4184	4164	4146	4129	4113	4099

4086	4074	4063	4053	4044	4036	4029	4023	4018	4013

4009	4005	4002	4000	3998	3997	3996	3995	3994	3994

3993	3993	3993	3993	3993	3993	3992	3991	3990	3989

3987

J1	-3083	-3069	-3055	-3042	-3030	-3018	-3007	-2996	-2986	-2977

-2969	-2961	-2953	-2947	-2940	-2935	-2930	-2926	-2922	-2920

-2917	-2916	-2914	-2914	-2914	-2915	-2917	-2919	-2921	-2925

-2929	-2933	-2939	-2945	-2951	-2958	-2966	-2974	-2983	-2993

-3003

J2	1507	1490	1473	1457	1441	1425	1410	1396	1382	1368

1355	1343	1330	1319	1308	1297	1287	1277	1268	1259

1251	1243	1236	1229	1222	1216	1211	1206	1201	1197

1194	1191	1188	1186	1184	1183	1182	1182	1182	1183

1184

NU	2458	2463	2469	2474	2479	2485	2490	2495	2500	2505

2510	2514	2519	2524	2528	2533	2537	2541	2545	2550

2554	2558	2561	2565	2569	2573	2576	2580	2583	2586

2590	2593	2596	2599	2602	2604	2607	2610	2612	2615

2617

VX	21717	21763	21809	21854	21897	21940	21983	22024	22065	22105

22144	22182	22219	22256	22292	22327	22361	22394	22427	22459

22490	22520	22550	22578	22606	22633	22659	22685	22709	22733

22756	22778	22800	22821	22840	22859	22878	22895	22912	22927

22942

VI	20880	20887	20893	20900	20907	20913	20920	20926	20933	20939

20946	20952	20958	20965	20971	20978	20984	20991	20997	21003

21010	21016	21023	21029	21035	21042	21048	21054	21061	21067

21073	21079	21086	21092	21098	21104	21111	21117	21123	21129

21136

VP	3676	3683	3689	3695	3702	3708	3714	3721	3727	3733

3739	3745	3751	3757	3762	3768	3774	3780	3785	3791

3796	3802	3807	3812	3818	3823	3828	3833	3838	3843

3848	3853	3858	3863	3868	3873	3877	3882	3886	3891

3895

VE	3232	3234	3236	3238	3240	3242	3244	3246	3248	3249

3251	3253	3254	3256	3258	3259	3261	3262	3264	3265

3267	3268	3269	3271	3272	3273	3274	3276	3277	3278

3279	3280	3281	3282	3283	3284	3285	3286	3286	3287

3288

ESS1	-15930	-15904	-15882	-15862	-15846	-15833	-15822	-15815	-15809	-15807

-15807	-15809	-15813	-15820	-15828	-15838	-15850	-15864	-15879	-15896

-15914	-15934	-15954	-15976	-15998	-16021	-16045	-16070	-16095	-16120

-16146	-16172	-16198	-16224	-16250	-16276	-16301	-16326	-16350	-16374

-16396

ESS2	1606	1602	1598	1595	1593	1591	1590	1588	1588	1587

1588	1588	1589	1590	1592	1593	1595	1598	1600	1603

1606	1610	1613	1617	1621	1625	1630	1634	1639	1643

1648	1653	1658	1663	1668	1673	1678	1683	1688	1693

1698

Table 12 - Neutronic constants for VVER-1000 ICIS application software
TVS 16 1.6% (311*1.6%) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

100	 -burnup increment (*0.01 MWd/kgU)

31	 - number of burnup increments DD1=0 PK8=0.985

0.8555381	- Fi1

-0.0179265	- Fi2

K0	11583	11505	11424	11317	11200	11082	10967	10854	10746	10641

10540	10442	10348	10256	10168	10082	9999	9918	9840	9765

9692	9622	9554	9488	9425	9363	9305	9248	9193	9141

9091

M0	6511	6472	6436	6401	6369	6338	6309	6282	6257	6233

6210	6189	6169	6151	6133	6117	6101	6086	6073	6059

6047	6035	6023	6012	6000	5990	5979	5968	5957	5946

5934

B1	-2785	-2835	-2883	-2929	-2974	-3016	-3057	-3096	-3133	-3169

-3202	-3234	-3264	-3292	-3318	-3343	-3366	-3387	-3406	-3423

-3438	-3452	-3464	-3474	-3482	-3489	-3493	-3496	-3497	-3496

-3494

B2	7356	7488	7616	7739	7857	7970	8079	8182	8281	8374

8463	8547	8626	8700	8770	8834	8894	8949	8999	9044

9084	9119	9149	9175	9196	9212	9223	9229	9230	9226

9218

I1	-9563	-9529	-9495	-9461	-9427	-9393	-9358	-9324	-9290	-9255

-9221	-9186	-9151	-9117	-9082	-9047	-9012	-8977	-8942	-8907

-8871	-8836	-8801	-8765	-8730	-8694	-8658	-8623	-8587	-8551

-8515

I2	2441	2425	2410	2395	2381	2367	2354	2342	2329	2318

2306	2296	2285	2276	2266	2257	2249	2241	2234	2227

2221	2215	2209	2204	2200	2196	2193	2190	2187	2185

2184

I3	-2100	-2029	-1961	-1895	-1833	-1773	-1716	-1662	-1611	-1563

-1518	-1476	-1436	-1399	-1366	-1335	-1307	-1281	-1259	-1240

-1223	-1209	-1199	-1191	-1186	-1184	-1184	-1188	-1194	-1204

-1216

I4	-6492	-6270	-6057	-5854	-5659	-5473	-5296	-5128	-4969	-4819

-4677	-4545	-4422	-4308	-4202	-4106	-4018	-3940	-3870	-3810

-3758	-3716	-3682	-3657	-3641	-3634	-3636	-3648	-3668	-3696

-3734

I5	-3390	-3284	-3181	-3083	-2988	-2898	-2812	-2730	-2652	-2578

-2508	-2442	-2380	-2323	-2269	-2220	-2174	-2133	-2096	-2063

-2034	-2009	-1988	-1971	-1958	-1950	-1945	-1945	-1948	-1956

-1968

D1	-2834	-2914	-2985	-3046	-3099	-3144	-3181	-3211	-3234	-3251

-3262	-3268	-3269	-3267	-3260	-3250	-3238	-3223	-3207	-3190

-3171	-3153	-3135	-3118	-3102	-3087	-3075	-3066	-3060	-3058

-3060

D2	-2600	-2722	-2840	-2952	-3060	-3162	-3260	-3353	-3440	-3523

-3601	-3673	-3741	-3804	-3862	-3915	-3963	-4006	-4044	-4077

-4105	-4128	-4146	-4159	-4167	-4171	-4169	-4162	-4151	-4134

-4113

E1	-3248	-3171	-3102	-3040	-2984	-2936	-2893	-2855	-2823	-2796

-2773	-2755	-2740	-2728	-2719	-2713	-2708	-2706	-2704	-2704

-2704	-2704	-2704	-2703	-2702	-2699	-2694	-2687	-2677	-2664

-2648

E2	5525	5314	5124	4954	4804	4671	4555	4455	4370	4298

4238	4190	4152	4123	4101	4087	4078	4074	4073	4074

4077	4079	4081	4080	4076	4067	4053	4032	4004	3966

3918

EX	-943	-904	-869	-836	-806	-779	-754	-732	-712	-694

-677	-663	-650	-639	-629	-620	-612	-605	-599	-594

-589	-585	-581	-576	-572	-568	-563	-558	-552	-546

-539

ES	-2954	-2831	-2719	-2616	-2523	-2437	-2360	-2291	-2228	-2172

-2122	-2078	-2040	-2006	-1976	-1950	-1927	-1908	-1891	-1875

-1861	-1848	-1836	-1824	-1811	-1798	-1783	-1766	-1747	-1725

-1700

F1	-16817	-16299	-15831	-15409	-15032	-14697	-14402	-14143	-13919	-13727

-13564	-13427	-13316	-13226	-13155	-13101	-13062	-13034	-13016	-13004

-12996	-12990	-12984	-12974	-12958	-12934	-12898	-12850	-12785	-12702

-12598

F2	2192	2093	2004	1924	1853	1790	1735	1687	1645	1610

1581	1557	1538	1522	1511	1503	1497	1494	1493	1492

1493	1494	1494	1494	1492	1489	1483	1475	1463	1448

1428

MS	1454	1423	1395	1372	1352	1336	1323	1313	1306	1301

1299	1299	1301	1304	1309	1315	1322	1329	1338	1347

1355	1364	1372	1380	1387	1393	1398	1401	1403	1403

1401

CS	-344	-354	-363	-372	-381	-390	-398	-406	-414	-421

-429	-436	-443	-449	-456	-462	-468	-474	-479	-485

-490	-495	-500	-505	-510	-515	-520	-524	-529	-533

-538

SX	4827	4724	4635	4559	4495	4443	4401	4369	4346	4332

4325	4326	4332	4344	4361	4382	4406	4433	4462	4491

4521	4551	4579	4606	4629	4650	4666	4678	4684	4684

4676

CX	-1367	-1395	-1424	-1451	-1479	-1506	-1532	-1558	-1583	-1608

-1633	-1657	-1680	-1704	-1726	-1748	-1770	-1791	-1811	-1832

-1851	-1870	-1889	-1907	-1924	-1941	-1958	-1974	-1989	-2004

-2018

D0	1421	1422	1422	1422	1423	1423	1423	1423	1423	1423

1423	1423	1423	1422	1422	1422	1422	1422	1421	1421

1421	1421	1420	1420	1420	1420	1420	1419	1419	1419

1419

CD	-8479	-8293	-8113	-7939	-7771	-7609	-7453	-7304	-7160	-7023

-6891	-6766	-6646	-6533	-6426	-6325	-6230	-6141	-6058	-5981

-5910	-5845	-5786	-5734	-5687	-5647	-5612	-5584	-5561	-5545

-5535

DD	1974	1973	1972	1971	1969	1968	1967	1966	1965	1964

1963	1962	1961	1960	1959	1958	1957	1955	1954	1953

1952	1951	1950	1949	1948	1947	1946	1945	1944	1944

1943

L0	7881	7593	7332	7098	6889	6704	6540	6397	6274	6169

6080	6006	5946	5898	5861	5833	5814	5801	5793	5790

5788	5788	5788	5785	5780	5769	5753	5730	5697	5655

5600

J1	-10619	-10258	-9913	-9585	-9272	-8976	-8696	-8433	-8185	-7954

-7739	-7540	-7358	-7191	-7041	-6907	-6790	-6688	-6603	-6534

-6481	-6444	-6424	-6420	-6432	-6460	-6504	-6565	-6642	-6735

-6844

J2	2959	2838	2722	2612	2507	2408	2314	2226	2143	2066

1994	1927	1866	1811	1761	1716	1677	1643	1615	1592

1575	1563	1557	1556	1561	1571	1586	1607	1633	1665

1703

NU	2469	2492	2514	2535	2556	2576	2595	2613	2631	2647

2663	2678	2692	2706	2718	2730	2741	2751	2760	2769

2777	2783	2790	2795	2799	2803	2806	2808	2809	2809

2809

VX	21823	22001	22172	22336	22494	22644	22788	22925	23055	23178

23294	23404	23506	23602	23691	23773	23849	23917	23979	24034

24082	24123	24157	24185	24205	24219	24226	24226	24220	24206

24186

VI	20895	20932	20969	21004	21038	21072	21104	21136	21167	21196

21225	21253	21280	21306	21332	21356	21379	21402	21423	21444

21464	21482	21500	21517	21533	21548	21562	21576	21588	21599

21610

VP	3695	3726	3756	3786	3814	3842	3869	3894	3919	3943

3966	3988	4009	4030	4049	4068	4085	4102	4118	4133

4147	4160	4172	4183	4194	4203	4212	4219	4226	4232

4237

VE	3236	3244	3251	3258	3265	3272	3278	3284	3290	3295

3300	3305	3310	3314	3318	3322	3326	3329	3332	3335

3337	3339	3341	3343	3344	3345	3346	3346	3347	3347

3346

ESS1	-32391	-31611	-30907	-30275	-29713	-29215	-28779	-28399	-28072	-27795

-27562	-27370	-27216	-27094	-27002	-26935	-26889	-26860	-26845	-26839

-26839	-26839	-26838	-26829	-26811	-26777	-26726	-26651	-26551	-26420

-26255

ESS2	5528	5314	5121	4948	4795	4660	4542	4441	4354	4281

4220	4171	4132	4102	4080	4065	4056	4052	4050	4052

4054	4056	4057	4056	4052	4042	4028	4006	3976	3938

3889

Table 13 - Neutronic constants for VVER-1000 ICIS application software
TVS 16 KL-B 1.6% (311*1.6%) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

100	 -burnup increment (*0.01 MWd/kgU)

31	 - number of burnup increments DD1=0 PK8=0.985

0.8170956	- Fi1

-0.0194947	- Fi2

K0	8232	8236	8233	8197	8145	8086	8023	7960	7895	7832

7769	7707	7646	7586	7528	7471	7415	7361	7308	7257

7207	7159	7112	7067	7024	6982	6941	6902	6864	6828

6794

M0	5742	5729	5716	5703	5691	5679	5667	5655	5644	5633

5622	5611	5601	5591	5581	5571	5562	5553	5544	5536

5528	5520	5512	5505	5498	5492	5485	5480	5474	5469

5464

B1	-2584	-2637	-2688	-2737	-2785	-2830	-2873	-2915	-2954	-2991

-3027	-3061	-3092	-3122	-3150	-3176	-3200	-3222	-3242	-3260

-3276	-3290	-3302	-3313	-3321	-3327	-3332	-3335	-3335	-3334

-3331

B2	6783	6922	7055	7183	7307	7425	7538	7646	7749	7848

7941	8029	8112	8190	8262	8330	8393	8451	8504	8551

8594	8632	8664	8692	8714	8731	8744	8751	8754	8751

8743

I1	-6477	-6483	-6488	-6492	-6494	-6495	-6495	-6493	-6490	-6485

-6479	-6472	-6463	-6453	-6442	-6429	-6415	-6400	-6383	-6365

-6346	-6325	-6303	-6279	-6254	-6228	-6200	-6171	-6141	-6110

-6076

I2	1977	1973	1968	1964	1960	1957	1953	1949	1945	1942

1938	1935	1931	1928	1925	1921	1918	1915	1912	1909

1906	1904	1901	1898	1896	1893	1891	1888	1886	1883

1881

I3	-1147	-1112	-1078	-1046	-1015	-986	-957	-931	-905	-881

-858	-836	-816	-797	-780	-764	-749	-735	-723	-712

-702	-694	-687	-682	-678	-675	-673	-673	-674	-676

-680

I4	-3587	-3477	-3372	-3271	-3173	-3081	-2992	-2907	-2827	-2751

-2679	-2611	-2547	-2488	-2433	-2382	-2335	-2292	-2253	-2219

-2189	-2163	-2141	-2123	-2110	-2101	-2096	-2095	-2098	-2105

-2117

I5	-1748	-1698	-1649	-1603	-1558	-1514	-1473	-1433	-1396	-1360

-1325	-1293	-1262	-1233	-1206	-1181	-1157	-1135	-1115	-1097

-1081	-1066	-1053	-1042	-1033	-1025	-1019	-1015	-1013	-1013

-1014

D1	-7361	-7224	-7097	-6978	-6867	-6763	-6666	-6576	-6493	-6415

-6343	-6276	-6213	-6155	-6101	-6051	-6003	-5959	-5917	-5876

-5838	-5800	-5763	-5727	-5690	-5654	-5616	-5577	-5537	-5494

-5449

D2	-4900	-4942	-4982	-5019	-5055	-5088	-5118	-5146	-5172	-5195

-5216	-5235	-5252	-5266	-5277	-5287	-5294	-5298	-5301	-5301

-5298	-5294	-5286	-5277	-5265	-5251	-5235	-5216	-5195	-5171

-5145

E1	-2617	-2559	-2507	-2461	-2421	-2386	-2356	-2331	-2309	-2292

-2278	-2267	-2259	-2254	-2250	-2249	-2249	-2250	-2252	-2254

-2257	-2259	-2261	-2261	-2261	-2259	-2255	-2249	-2240	-2228

-2213

E2	3874	3708	3562	3435	3327	3235	3159	3098	3050	3015

2991	2977	2972	2975	2985	3000	3020	3043	3068	3094

3120	3145	3167	3186	3200	3208	3210	3203	3187	3161

3123

EX	-538	-520	-502	-486	-471	-458	-445	-434	-423	-414

-405	-397	-390	-384	-378	-373	-368	-364	-360	-357

-354	-351	-348	-346	-343	-340	-338	-335	-332	-328

-325

ES	-1757	-1695	-1638	-1585	-1537	-1493	-1453	-1416	-1384	-1354

-1328	-1305	-1284	-1265	-1249	-1235	-1222	-1211	-1202	-1193

-1185	-1178	-1171	-1164	-1157	-1150	-1143	-1134	-1125	-1114

-1102

F1	-13113	-12733	-12389	-12079	-11802	-11555	-11336	-11145	-10978	-10835

-10713	-10610	-10525	-10456	-10401	-10358	-10325	-10301	-10283	-10271

-10261	-10253	-10243	-10232	-10216	-10194	-10164	-10124	-10072	-10007

-9927

F2	1478	1415	1359	1308	1263	1223	1188	1158	1132	1110

1092	1077	1065	1056	1049	1044	1040	1039	1038	1037

1037	1037	1037	1036	1034	1031	1026	1019	1010	998

984

MS	1377	1345	1317	1293	1273	1256	1242	1231	1223	1217

1214	1213	1213	1215	1219	1224	1230	1236	1244	1251

1259	1266	1274	1280	1286	1292	1295	1298	1299	1298

1295

CS	-385	-389	-393	-397	-401	-406	-410	-415	-420	-425

-430	-436	-441	-446	-451	-456	-462	-467	-472	-477

-482	-486	-491	-495	-499	-503	-507	-511	-514	-517

-520

SX	4558	4454	4364	4285	4219	4164	4119	4084	4058	4040

4030	4027	4030	4038	4051	4068	4088	4111	4135	4161

4187	4212	4237	4260	4280	4298	4311	4320	4323	4320

4311

CX	-1483	-1492	-1502	-1513	-1526	-1539	-1553	-1568	-1584	-1601

-1618	-1636	-1654	-1672	-1690	-1709	-1727	-1746	-1764	-1782

-1800	-1817	-1833	-1849	-1864	-1879	-1892	-1904	-1916	-1926

-1934

D0	1399	1400	1401	1401	1402	1402	1402	1403	1403	1403

1403	1403	1403	1403	1403	1403	1403	1403	1403	1402

1402	1402	1402	1402	1402	1402	1402	1402	1402	1402

1402

CD	-4856	-4735	-4617	-4503	-4391	-4283	-4177	-4074	-3975	-3878

-3785	-3694	-3607	-3522	-3441	-3363	-3287	-3215	-3146	-3079

-3016	-2956	-2899	-2844	-2793	-2745	-2700	-2658	-2619	-2583

-2549

DD	1823	1823	1823	1823	1823	1822	1822	1822	1821	1821

1821	1820	1820	1819	1819	1818	1818	1817	1816	1816

1815	1814	1813	1813	1812	1811	1810	1809	1808	1807

1806

L0	6196	5992	5808	5642	5493	5361	5245	5143	5054	4978

4914	4860	4816	4780	4752	4731	4716	4705	4698	4694

4692	4690	4689	4686	4681	4673	4661	4644	4620	4590

4552

J1	-6794	-6587	-6388	-6199	-6020	-5849	-5688	-5536	-5393	-5259

-5135	-5020	-4914	-4817	-4729	-4651	-4582	-4522	-4472	-4431

-4399	-4376	-4362	-4358	-4363	-4377	-4400	-4433	-4474	-4525

-4586

J2	2066	1990	1917	1847	1781	1719	1659	1604	1551	1502

1456	1414	1375	1340	1308	1279	1254	1233	1214	1199

1188	1179	1175	1173	1175	1181	1190	1202	1218	1237

1259

NU	2475	2498	2520	2541	2561	2581	2600	2618	2635	2651

2667	2682	2696	2709	2721	2733	2743	2753	2762	2771

2778	2785	2791	2796	2800	2804	2806	2808	2809	2810

2809

VX	21849	22024	22192	22353	22508	22656	22797	22931	23059	23180

23294	23401	23502	23595	23682	23763	23836	23903	23963	24016

24063	24103	24136	24162	24181	24194	24200	24199	24192	24178

24157

VI	20934	20971	21007	21041	21075	21108	21141	21172	21202	21231

21260	21287	21314	21340	21365	21389	21412	21434	21455	21475

21495	21513	21531	21547	21563	21578	21592	21605	21617	21628

21638

VP	3725	3756	3786	3815	3843	3871	3897	3923	3947	3971

3994	4016	4037	4057	4076	4095	4112	4129	4145	4159

4173	4186	4198	4209	4220	4229	4238	4245	4252	4258

4262

VE	3237	3244	3252	3259	3266	3272	3279	3285	3290	3296

3301	3306	3311	3315	3319	3323	3326	3330	3333	3335

3338	3340	3342	3343	3345	3346	3347	3347	3347	3347

3347

ESS1	-25962	-25376	-24853	-24390	-23982	-23627	-23322	-23061	-22844	-22665

-22521	-22410	-22327	-22270	-22234	-22216	-22214	-22223	-22240	-22261

-22284	-22304	-22319	-22325	-22318	-22296	-22253	-22189	-22098	-21977

-21823

ESS2	3850	3683	3536	3409	3299	3207	3130	3069	3020	2984

2960	2945	2939	2942	2951	2965	2984	3006	3031	3056

3081	3105	3127	3145	3158	3165	3165	3158	3141	3113

3074

Table 14 - Neutronic constants for VVER-1000 ICIS application software

TVS 16 KL-DY 1.6% (311*1.6%) 489.8 kg-UO2

4898.0	- U mass

3020.0	- reference temperature

7161.0	- reference density

0	- R presence (0 – no; 1 – yes)

100	 -burnup increment (*0.01 MWd/kgU)

31	 - number of burnup increments DD1=0 PK8=0.985

0.8256029	- Fi1

-0.0184088	- Fi2

K0	9087	9088	9081	9038	8977	8908	8836	8763	8690	8618

8546	8476	8407	8340	8274	8210	8147	8086	8027	7969

7913	7859	7807	7756	7707	7660	7615	7571	7529	7488

7449

M0	5990	5973	5956	5939	5923	5907	5892	5877	5863	5848

5835	5821	5808	5796	5783	5771	5760	5749	5738	5728

5718	5708	5699	5690	5682	5674	5666	5658	5651	5645

5638

B1	-2707	-2761	-2812	-2862	-2909	-2955	-2999	-3041	-3080	-3118

-3154	-3188	-3220	-3250	-3278	-3304	-3328	-3351	-3371	-3389

-3406	-3420	-3432	-3443	-3451	-3458	-3463	-3465	-3466	-3465

-3462

B2	7128	7269	7405	7535	7661	7781	7896	8006	8111	8210

8305	8394	8478	8557	8631	8699	8763	8821	8874	8922

8965	9002	9035	9062	9084	9101	9113	9120	9121	9117

9109

I1	-7627	-7629	-7629	-7628	-7626	-7622	-7616	-7609	-7601	-7591

-7579	-7566	-7552	-7536	-7519	-7500	-7480	-7459	-7436	-7411

-7385	-7358	-7329	-7298	-7266	-7233	-7198	-7162	-7124	-7085

-7045

I2	2127	2120	2113	2107	2100	2094	2088	2082	2076	2070

2065	2059	2054	2049	2044	2039	2035	2030	2026	2022

2018	2014	2010	2007	2003	2000	1997	1994	1991	1989

1986

I3	-1341	-1300	-1260	-1222	-1185	-1150	-1117	-1085	-1055	-1027

-1000	-975	-951	-929	-909	-890	-872	-857	-843	-830

-820	-810	-803	-797	-792	-790	-788	-789	-791	-794

-800

I4	-4171	-4041	-3917	-3798	-3683	-3574	-3470	-3371	-3276	-3187

-3103	-3024	-2950	-2881	-2816	-2757	-2703	-2654	-2610	-2571

-2537	-2508	-2484	-2465	-2451	-2443	-2439	-2440	-2446	-2457

-2473

I5	-2103	-2044	-1986	-1931	-1877	-1826	-1777	-1730	-1686	-1643

-1603	-1565	-1529	-1495	-1463	-1433	-1406	-1381	-1358	-1337

-1318	-1301	-1287	-1274	-1264	-1256	-1250	-1246	-1245	-1245

-1248

D1	-5569	-5450	-5341	-5240	-5147	-5061	-4982	-4910	-4844	-4784

-4729	-4679	-4634	-4593	-4556	-4522	-4491	-4462	-4436	-4411

-4388	-4365	-4343	-4321	-4298	-4275	-4251	-4225	-4197	-4166

-4133

D2	-3736	-3790	-3842	-3892	-3940	-3986	-4029	-4071	-4110	-4147

-4182	-4215	-4245	-4273	-4300	-4323	-4345	-4365	-4382	-4398

-4411	-4422	-4430	-4437	-4441	-4444	-4444	-4442	-4437	-4431

-4422

E1	-2673	-2616	-2566	-2520	-2479	-2443	-2411	-2384	-2360	-2340

-2323	-2308	-2297	-2288	-2281	-2276	-2272	-2270	-2269	-2268

-2268	-2268	-2268	-2267	-2266	-2264	-2261	-2256	-2249	-2240

-2229

E2	3981	3846	3724	3614	3515	3428	3351	3284	3226	3177

3135	3100	3072	3049	3031	3018	3009	3003	2999	2997

2996	2996	2995	2993	2990	2985	2977	2965	2950	2929

2903

EX	-609	-587	-567	-548	-531	-515	-501	-488	-476	-465

-455	-446	-438	-431	-424	-418	-413	-408	-404	-400

-397	-394	-391	-388	-385	-382	-379	-375	-372	-368

-364

ES	-1949	-1878	-1812	-1752	-1697	-1647	-1602	-1560	-1523	-1489

-1459	-1432	-1408	-1387	-1368	-1351	-1337	-1324	-1312	-1302

-1292	-1284	-1275	-1267	-1259	-1250	-1241	-1231	-1220	-1207

-1193

F1	-13427	-13033	-12677	-12356	-12068	-11812	-11585	-11386	-11214	-11065

-10938	-10831	-10743	-10672	-10614	-10570	-10536	-10512	-10494	-10482

-10473	-10465	-10457	-10446	-10431	-10410	-10381	-10342	-10292	-10228

-10148

F2	1522	1457	1398	1345	1298	1257	1220	1188	1161	1137

1117	1101	1088	1078	1070	1064	1060	1057	1056	1055

1055	1055	1055	1055	1054	1051	1047	1042	1034	1024

1011

MS	1391	1359	1331	1307	1286	1269	1255	1244	1236	1230

1227	1226	1227	1229	1233	1238	1244	1251	1258	1266

1274	1281	1289	1296	1302	1307	1311	1314	1315	1314

1311

CS	-362	-367	-373	-378	-383	-388	-394	-399	-404	-410

-415	-420	-426	-431	-436	-441	-446	-451	-456	-461

-465	-470	-474	-479	-483	-487	-491	-494	-498	-501

-504

SX	4605	4500	4408	4329	4262	4207	4162	4126	4100	4083

4073	4070	4073	4082	4095	4113	4133	4157	4182	4208

4235	4262	4287	4310	4331	4349	4363	4372	4376	4374

4364

CX	-1410	-1423	-1437	-1452	-1467	-1483	-1499	-1516	-1533	-1551

-1568	-1586	-1604	-1622	-1641	-1659	-1677	-1695	-1712	-1730

-1747	-1763	-1779	-1795	-1810	-1824	-1838	-1851	-1863	-1874

-1884

D0	1394	1395	1395	1396	1396	1396	1397	1397	1397	1397

1397	1397	1397	1397	1397	1397	1397	1396	1396	1396

1396	1396	1395	1395	1395	1395	1395	1395	1395	1395

1395

CD	-5884	-5758	-5635	-5515	-5399	-5286	-5177	-5071	-4968	-4869

-4773	-4681	-4592	-4507	-4425	-4346	-4271	-4199	-4131	-4066

-4005	-3946	-3892	-3841	-3793	-3748	-3707	-3670	-3636	-3605

-3578

DD	1813	1813	1813	1812	1812	1812	1811	1811	1810	1810

1809	1809	1808	1807	1807	1806	1805	1804	1803	1802

1802	1801	1800	1799	1797	1796	1795	1794	1793	1792

1790

L0	6368	6156	5964	5791	5636	5499	5378	5271	5179	5100

5033	4978	4932	4895	4866	4844	4828	4817	4810	4806

4804	4802	4801	4798	4793	4785	4772	4755	4730	4699

4659

J1	-7034	-6816	-6607	-6408	-6219	-6040	-5870	-5710	-5560	-5419

-5288	-5167	-5056	-4954	-4862	-4780	-4708	-4645	-4592	-4549

-4515	-4491	-4477	-4473	-4478	-4493	-4518	-4553	-4597	-4651

-4715

J2	2185	2103	2025	1951	1880	1813	1749	1689	1633	1581

1532	1487	1445	1407	1373	1342	1316	1292	1273	1257

1245	1236	1231	1230	1232	1238	1248	1262	1279	1299

1324

NU	2473	2496	2518	2539	2560	2580	2599	2617	2634	2650

2666	2681	2695	2708	2721	2732	2743	2753	2762	2770

2778	2785	2791	2796	2800	2804	2806	2808	2809	2809

2809

VX	21842	22018	22188	22350	22506	22655	22798	22933	23062	23184

23299	23407	23508	23603	23691	23772	23846	23913	23974	24028

24074	24115	24148	24174	24194	24207	24213	24212	24205	24190

24169

VI	20921	20958	20994	21029	21063	21096	21128	21160	21190	21220

21248	21276	21302	21328	21353	21377	21400	21422	21444	21464

21483	21502	21519	21536	21552	21567	21581	21594	21606	21617

21627

VP	3715	3746	3776	3806	3834	3861	3888	3913	3938	3962

3985	4007	4028	4048	4067	4086	4103	4120	4135	4150

4164	4177	4189	4200	4210	4220	4228	4236	4242	4248

4253

VE	3237	3244	3252	3259	3266	3272	3279	3285	3290	3296

3301	3306	3311	3315	3319	3323	3327	3330	3333	3335

3338	3340	3342	3343	3345	3346	3347	3347	3347	3347

3347

ESS1	-26534	-25963	-25448	-24985	-24572	-24205	-23883	-23601	-23358	-23151

-22976	-22831	-22713	-22619	-22547	-22494	-22456	-22431	-22417	-22409

-22407	-22406	-22403	-22397	-22385	-22362	-22327	-22278	-22210	-22121

-22008

ESS2	3958	3821	3698	3587	3487	3399	3321	3253	3195	3144

3101	3066	3037	3014	2996	2982	2972	2966	2961	2959

2958	2957	2957	2955	2952	2947	2938	2927	2911	2891

2865

Annex 5

Tables of transuranium elements for the ICIS

Table 1 - TVS 24 2.4 % (311*2.4 %) 489.8 kg-UO2

W	U235	U236	U238	Np37	Pu38	Pu39	Pu40	Pu41	Pu42	Am41	Am2m	Am43	Cm42	Cm43	Cm44

0	5.1386E-04	0.0000E+00	2.0633E-02	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00

2	4.6606E-04	8.2478E-06	2.0601E-02	1.3256E-07	2.8601E-09	2.3071E-05	1.1484E-06	1.1618E-07	2.2734E-09	1.7532E-10	5.2193E-13	1.9352E-11	4.8942E-12	5.3761E-15	2.3042E-13

4	4.2354E-04	1.5529E-05	2.0569E-02	3.7344E-07	1.6154E-08	4.2182E-05	3.9229E-06	7.5594E-07	3.1040E-08	2.3724E-09	1.2536E-11	5.6393E-10	1.3334E-10	3.0471E-13	1.4059E-11

6	3.8514E-04	2.2036E-05	2.0537E-02	6.8526E-07	4.3934E-08	5.7058E-05	7.4875E-06	1.9925E-06	1.2797E-07	9.5924E-09	6.7978E-11	3.6692E-09	8.1156E-10	2.8708E-12	1.4226E-10

8	3.5016E-04	2.7887E-05	2.0504E-02	1.0548E-06	8.9295E-08	6.8800E-05	1.1447E-05	3.6980E-06	3.2910E-07	2.4024E-08	2.0456E-10	1.3117E-08	2.7179E-09	1.3165E-11	7.0002E-10

10	3.1816E-04	3.3161E-05	2.0470E-02	1.4714E-06	1.5481E-07	7.8138E-05	1.5590E-05	5.7173E-06	6.5904E-07	4.6622E-08	4.5021E-10	3.3987E-08	6.6090E-09	4.0941E-11	2.3346E-09

12	2.8878E-04	3.7916E-05	2.0436E-02	1.9260E-06	2.4259E-07	8.5588E-05	1.9793E-05	7.9178E-06	1.1321E-06	7.7313E-08	8.1769E-10	7.2086E-08	1.3179E-08	9.9910E-11	6.1078E-09

14	2.6179E-04	4.2199E-05	2.0401E-02	2.4105E-06	3.5437E-07	9.1535E-05	2.3971E-05	1.0197E-05	1.7546E-06	1.1532E-07	1.3056E-09	1.3343E-07	2.2974E-08	2.0666E-10	1.3540E-08

16	2.3696E-04	4.6046E-05	2.0365E-02	2.9181E-06	4.9144E-07	9.6272E-05	2.8066E-05	1.2480E-05	2.5271E-06	1.5943E-07	1.9018E-09	2.2385E-07	3.6357E-08	3.7920E-10	2.6619E-08

18	2.1415E-04	4.9491E-05	2.0329E-02	3.4424E-06	6.5470E-07	1.0003E-04	3.2039E-05	1.4713E-05	3.4457E-06	2.0821E-07	2.5873E-09	3.4862E-07	5.3495E-08	6.3544E-10	4.7784E-08

20	1.9318E-04	5.2560E-05	2.0292E-02	3.9778E-06	8.4462E-07	1.0300E-04	3.5857E-05	1.6858E-05	4.5037E-06	2.6020E-07	3.3396E-09	5.1232E-07	7.4372E-08	9.9179E-10	7.9882E-08

22	1.7398E-04	5.5275E-05	2.0255E-02	4.5192E-06	1.0610E-06	1.0531E-04	3.9480E-05	1.8904E-05	5.6912E-06	3.1404E-07	4.1358E-09	7.1849E-07	9.8776E-08	1.4612E-09	1.2605E-07

24	1.5639E-04	5.7663E-05	2.0217E-02	5.0620E-06	1.3035E-06	1.0711E-04	4.2914E-05	2.0815E-05	6.9997E-06	3.6839E-07	4.9540E-09	9.6991E-07	1.2645E-07	2.0541E-09	1.8978E-07

26	1.4031E-04	5.9747E-05	2.0178E-02	5.6022E-06	1.5715E-06	1.0848E-04	4.6151E-05	2.2586E-05	8.4177E-06	4.2207E-07	5.7732E-09	1.2683E-06	1.5697E-07	2.7767E-09	2.7470E-07

28	1.2563E-04	6.1546E-05	2.0139E-02	6.1361E-06	1.8636E-06	1.0953E-04	4.9186E-05	2.4215E-05	9.9333E-06	4.7410E-07	6.5759E-09	1.6144E-06	1.8987E-07	3.6305E-09	3.8455E-07

30	1.1228E-04	6.3080E-05	2.0100E-02	6.6604E-06	2.1781E-06	1.1030E-04	5.2017E-05	2.5704E-05	1.1534E-05	5.2372E-07	7.3474E-09	2.0079E-06	2.2460E-07	4.6124E-09	5.2306E-07

32	1.0018E-04	6.4363E-05	2.0059E-02	7.1720E-06	2.5128E-06	1.1087E-04	5.4618E-05	2.7076E-05	1.3205E-05	5.7060E-07	8.0798E-09	2.4480E-06	2.6048E-07	5.7129E-09	6.9359E-07

34	8.9215E-05	6.5419E-05	2.0019E-02	7.6681E-06	2.8657E-06	1.1127E-04	5.7025E-05	2.8313E-05	1.4940E-05	6.1418E-07	8.7642E-09	2.9326E-06	2.9714E-07	6.9228E-09	8.9982E-07

36	7.9311E-05	6.6263E-05	1.9978E-02	8.1469E-06	3.2345E-06	1.1155E-04	5.9243E-05	2.9423E-05	1.6725E-05	6.5419E-07	9.3951E-09	3.4592E-06	3.3406E-07	8.2288E-09	1.1449E-06

38	7.0386E-05	6.6914E-05	1.9936E-02	8.6065E-06	3.6164E-06	1.1173E-04	6.1280E-05	3.0418E-05	1.8550E-05	6.9052E-07	9.9698E-09	4.0248E-06	3.7075E-07	9.6151E-09	1.4317E-06

40	6.2365E-05	6.7386E-05	1.9894E-02	9.0455E-06	4.0089E-06	1.1185E-04	6.3144E-05	3.1309E-05	2.0406E-05	7.2322E-07	1.0488E-08	4.6261E-06	4.0677E-07	1.1064E-08	1.7626E-06

42	5.5175E-05	6.7697E-05	1.9851E-02	9.4625E-06	4.4091E-06	1.1192E-04	6.4844E-05	3.2105E-05	2.2281E-05	7.5239E-07	1.0951E-08	5.2592E-06	4.4174E-07	1.2557E-08	2.1397E-06

44	4.8745E-05	6.7859E-05	1.9808E-02	9.8567E-06	4.8144E-06	1.1196E-04	6.6391E-05	3.2816E-05	2.4169E-05	7.7825E-07	1.1362E-08	5.9203E-06	4.7534E-07	1.4076E-08	2.5644E-06

46	4.3010E-05	6.7889E-05	1.9765E-02	1.0227E-05	5.2220E-06	1.1198E-04	6.7795E-05	3.3451E-05	2.6059E-05	8.0105E-07	1.1725E-08	6.6055E-06	5.0734E-07	1.5604E-08	3.0379E-06

48	3.7904E-05	6.7798E-05	1.9721E-02	1.0574E-05	5.6295E-06	1.1198E-04	6.9066E-05	3.4019E-05	2.7946E-05	8.2107E-07	1.2044E-08	7.3106E-06	5.3754E-07	1.7123E-08	3.5607E-06

50	3.3370E-05	6.7601E-05	1.9677E-02	1.0897E-05	6.0345E-06	1.1199E-04	7.0214E-05	3.4526E-05	2.9823E-05	8.3860E-07	1.2323E-08	8.0317E-06	5.6582E-07	1.8619E-08	4.1329E-06

52	2.9351E-05	6.7308E-05	1.9633E-02	1.1197E-05	6.4348E-06	1.1200E-04	7.1251E-05	3.4981E-05	3.1685E-05	8.5392E-07	1.2568E-08	8.7652E-06	5.9213E-07	2.0078E-08	4.7542E-06

54	2.5795E-05	6.6932E-05	1.9588E-02	1.1472E-05	6.8284E-06	1.1201E-04	7.2185E-05	3.5388E-05	3.3525E-05	8.6732E-07	1.2782E-08	9.5074E-06	6.1645E-07	2.1490E-08	5.4239E-06

56	2.2654E-05	6.6481E-05	1.9543E-02	1.1725E-05	7.2135E-06	1.1203E-04	7.3026E-05	3.5754E-05	3.5342E-05	8.7905E-07	1.2970E-08	1.0255E-05	6.3880E-07	2.2847E-08	6.1408E-06

58	1.9883E-05	6.5966E-05	1.9498E-02	1.1954E-05	7.5887E-06	1.1206E-04	7.3782E-05	3.6084E-05	3.7130E-05	8.8935E-07	1.3136E-08	1.1005E-05	6.5924E-07	2.4140E-08	6.9034E-06

60	1.7442E-05	6.5395E-05	1.9453E-02	1.2162E-05	7.9527E-06	1.1210E-04	7.4462E-05	3.6382E-05	3.8887E-05	8.9844E-07	1.3282E-08	1.1754E-05	6.7785E-07	2.5366E-08	7.7102E-06

62	1.5295E-05	6.4776E-05	1.9408E-02	1.2349E-05	8.3042E-06	1.1214E-04	7.5074E-05	3.6651E-05	4.0610E-05	9.0648E-07	1.3413E-08	1.2500E-05	6.9473E-07	2.6523E-08	8.5591E-06

64	1.3408E-05	6.4116E-05	1.9362E-02	1.2515E-05	8.6424E-06	1.1219E-04	7.5623E-05	3.6896E-05	4.2299E-05	9.1366E-07	1.3530E-08	1.3241E-05	7.1000E-07	2.7607E-08	9.4479E-06

66	1.1750E-05	6.3420E-05	1.9317E-02	1.2662E-05	8.9667E-06	1.1225E-04	7.6117E-05	3.7118E-05	4.3951E-05	9.2010E-07	1.3636E-08	1.3974E-05	7.2378E-07	2.8620E-08	1.0375E-05

68	1.0296E-05	6.2696E-05	1.9271E-02	1.2790E-05	9.2764E-06	1.1231E-04	7.6561E-05	3.7321E-05	4.5565E-05	9.2592E-07	1.3732E-08	1.4699E-05	7.3619E-07	2.9563E-08	1.1336E-05

70	9.6369E-06	6.2325E-05	1.9248E-02	1.2848E-05	9.4257E-06	1.1234E-04	7.6766E-05	3.7415E-05	4.6358E-05	9.2863E-07	1.3777E-08	1.5057E-05	7.4191E-07	3.0009E-08	1.1830E-05

Table 2 - TVS 36  3.62 % (245*3.7 %+66*3.3 %) 489.8 kg-UO2

W	U235	U236	U238	Np37	Pu38	Pu39	Pu40	Pu41	Pu42	Am41	Am2m	Am43	Cm42	Cm43	Cm44

0	7.7401E-04	0.0000E+00	2.0376E-02	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00

2	7.2443E-04	8.9315E-06	2.0349E-02	1.2372E-07	2.0815E-09	1.9874E-05	7.1209E-07	6.1026E-08	8.1795E-10	9.1698E-11	2.1351E-13	5.9809E-12	1.8941E-12	1.7024E-15	5.9428E-14

4	6.7824E-04	1.7193E-05	2.0322E-02	3.5202E-07	1.1966E-08	3.7702E-05	2.5483E-06	4.2842E-07	1.1990E-08	1.3294E-09	5.7391E-12	1.8483E-10	5.5112E-11	1.0288E-13	3.8218E-12

6	6.3491E-04	2.4878E-05	2.0295E-02	6.5301E-07	3.3061E-08	5.2600E-05	5.0441E-06	1.2091E-06	5.2666E-08	5.7406E-09	3.4452E-11	1.2702E-09	3.5668E-10	1.0297E-12	4.0639E-11

8	5.9408E-04	3.2049E-05	2.0267E-02	1.0163E-06	6.8163E-08	6.5143E-05	7.9407E-06	2.3796E-06	1.4306E-07	1.5263E-08	1.1347E-10	4.7695E-09	1.2623E-09	4.9903E-12	2.0910E-10

10	5.5549E-04	3.8750E-05	2.0239E-02	1.4335E-06	1.1975E-07	7.5743E-05	1.1088E-05	3.8698E-06	3.0041E-07	3.1265E-08	2.7062E-10	1.2918E-08	3.2262E-09	1.6326E-11	7.2596E-10

12	5.1897E-04	4.5016E-05	2.0210E-02	1.8970E-06	1.9003E-07	8.4715E-05	1.4390E-05	5.6010E-06	5.3806E-07	5.4473E-08	5.2828E-10	2.8526E-08	6.7316E-09	4.1759E-11	1.9699E-09

14	4.8436E-04	5.0872E-05	2.0181E-02	2.4003E-06	2.8099E-07	9.2307E-05	1.7783E-05	7.5006E-06	8.6554E-07	8.5038E-08	9.0037E-10	5.4806E-08	1.2236E-08	9.0265E-11	4.5165E-09

16	4.5154E-04	5.6342E-05	2.0151E-02	2.9375E-06	3.9441E-07	9.8717E-05	2.1218E-05	9.5063E-06	1.2892E-06	1.2266E-07	1.3919E-09	9.5191E-08	2.0132E-08	1.7267E-10	9.1627E-09

18	4.2043E-04	6.1443E-05	2.0121E-02	3.5033E-06	5.3183E-07	1.0411E-04	2.4659E-05	1.1567E-05	1.8126E-06	1.6670E-07	1.9999E-09	1.5319E-07	3.0729E-08	3.0111E-10	1.6942E-08

20	3.9093E-04	6.6192E-05	2.0090E-02	4.0928E-06	6.9458E-07	1.0863E-04	2.8077E-05	1.3641E-05	2.4374E-06	2.1628E-07	2.7147E-09	2.3223E-07	4.4239E-08	4.8834E-10	2.9131E-08

22	3.6301E-04	7.0596E-05	2.0059E-02	4.7013E-06	8.8352E-07	1.1238E-04	3.1430E-05	1.5707E-05	3.1625E-06	2.7047E-07	3.5223E-09	3.3549E-07	6.0751E-08	7.4669E-10	4.7226E-08

24	3.3658E-04	7.4675E-05	2.0027E-02	5.3246E-06	1.0997E-06	1.1546E-04	3.4718E-05	1.7724E-05	3.9875E-06	3.2816E-07	4.4056E-09	4.6603E-07	8.0316E-08	1.0885E-09	7.2983E-08

26	3.1157E-04	7.8442E-05	1.9995E-02	5.9589E-06	1.3435E-06	1.1798E-04	3.7924E-05	1.9671E-05	4.9095E-06	3.8820E-07	5.3451E-09	6.2652E-07	1.0287E-07	1.5247E-09	1.0836E-07

28	2.8793E-04	8.1906E-05	1.9962E-02	6.6005E-06	1.6154E-06	1.2000E-04	4.1034E-05	2.1536E-05	5.9250E-06	4.4949E-07	6.3205E-09	8.1923E-07	1.2827E-07	2.0644E-09	1.5553E-07

30	2.6562E-04	8.5079E-05	1.9929E-02	7.2460E-06	1.9152E-06	1.2159E-04	4.4038E-05	2.3306E-05	7.0296E-06	5.1098E-07	7.3120E-09	1.0460E-06	1.5631E-07	2.7149E-09	2.1681E-07

32	2.4465E-04	8.7960E-05	1.9895E-02	7.8920E-06	2.2420E-06	1.2283E-04	4.6897E-05	2.4995E-05	8.2152E-06	5.7194E-07	8.3038E-09	1.3081E-06	1.8658E-07	3.4787E-09	2.9452E-07

34	2.2492E-04	9.0571E-05	1.9861E-02	8.5349E-06	2.5958E-06	1.2374E-04	4.9635E-05	2.6571E-05	9.4805E-06	6.3139E-07	9.2779E-09	1.6065E-06	2.1893E-07	4.3591E-09	3.9135E-07

36	2.0638E-04	9.2919E-05	1.9826E-02	9.1725E-06	2.9754E-06	1.2437E-04	5.2248E-05	2.8034E-05	1.0820E-05	6.8854E-07	1.0219E-08	1.9417E-06	2.5301E-07	5.3558E-09	5.0991E-07

38	1.8901E-04	9.5014E-05	1.9791E-02	9.8018E-06	3.3798E-06	1.2478E-04	5.4730E-05	2.9385E-05	1.2227E-05	7.4272E-07	1.1115E-08	2.3137E-06	2.8846E-07	6.4655E-09	6.5289E-07

40	1.7275E-04	9.6866E-05	1.9755E-02	1.0421E-05	3.8072E-06	1.2500E-04	5.7080E-05	3.0626E-05	1.3696E-05	7.9344E-07	1.1954E-08	2.7222E-06	3.2488E-07	7.6826E-09	8.2294E-07

42	1.5758E-04	9.8484E-05	1.9718E-02	1.1026E-05	4.2560E-06	1.2505E-04	5.9295E-05	3.1760E-05	1.5221E-05	8.4031E-07	1.2729E-08	3.1663E-06	3.6189E-07	8.9986E-09	1.0227E-06

44	1.4345E-04	9.9877E-05	1.9681E-02	1.1616E-05	4.7241E-06	1.2497E-04	6.1374E-05	3.2791E-05	1.6795E-05	8.8307E-07	1.3435E-08	3.6449E-06	3.9911E-07	1.0403E-08	1.2546E-06

46	1.3033E-04	1.0105E-04	1.9644E-02	1.2190E-05	5.2091E-06	1.2478E-04	6.3319E-05	3.3725E-05	1.8412E-05	9.2158E-07	1.4069E-08	4.1564E-06	4.3615E-07	1.1884E-08	1.5211E-06

48	1.1816E-04	1.0203E-04	1.9606E-02	1.2744E-05	5.7087E-06	1.2450E-04	6.5130E-05	3.4565E-05	2.0067E-05	9.5580E-07	1.4629E-08	4.6990E-06	4.7268E-07	1.3426E-08	1.8245E-06

50	1.0692E-04	1.0280E-04	1.9567E-02	1.3277E-05	6.2202E-06	1.2417E-04	6.6810E-05	3.5320E-05	2.1752E-05	9.8578E-07	1.5118E-08	5.2705E-06	5.0836E-07	1.5016E-08	2.1666E-06

52	9.6565E-05	1.0339E-04	1.9528E-02	1.3788E-05	6.7408E-06	1.2378E-04	6.8363E-05	3.5993E-05	2.3463E-05	1.0117E-06	1.5536E-08	5.8687E-06	5.4292E-07	1.6637E-08	2.5494E-06

54	8.7043E-05	1.0381E-04	1.9489E-02	1.4276E-05	7.2679E-06	1.2336E-04	6.9791E-05	3.6591E-05	2.5192E-05	1.0337E-06	1.5888E-08	6.4911E-06	5.7610E-07	1.8273E-08	2.9741E-06

56	7.8314E-05	1.0406E-04	1.9449E-02	1.4739E-05	7.7987E-06	1.2292E-04	7.1101E-05	3.7120E-05	2.6935E-05	1.0520E-06	1.6177E-08	7.1348E-06	6.0769E-07	1.9910E-08	3.4422E-06

58	7.0334E-05	1.0416E-04	1.9408E-02	1.5177E-05	8.3303E-06	1.2248E-04	7.2297E-05	3.7587E-05	2.8685E-05	1.0670E-06	1.6411E-08	7.7973E-06	6.3751E-07	2.1531E-08	3.9543E-06

60	6.3059E-05	1.0411E-04	1.9367E-02	1.5590E-05	8.8601E-06	1.2203E-04	7.3385E-05	3.7997E-05	3.0438E-05	1.0790E-06	1.6593E-08	8.4758E-06	6.6544E-07	2.3123E-08	4.5110E-06

62	5.6443E-05	1.0393E-04	1.9326E-02	1.5976E-05	9.3855E-06	1.2159E-04	7.4370E-05	3.8356E-05	3.2188E-05	1.0882E-06	1.6730E-08	9.1673E-06	6.9140E-07	2.4673E-08	5.1126E-06

64	5.0443E-05	1.0363E-04	1.9284E-02	1.6336E-05	9.9040E-06	1.2117E-04	7.5260E-05	3.8669E-05	3.3931E-05	1.0951E-06	1.6828E-08	9.8692E-06	7.1533E-07	2.6170E-08	5.7589E-06

66	4.5016E-05	1.0321E-04	1.9242E-02	1.6669E-05	1.0413E-05	1.2076E-04	7.6061E-05	3.8941E-05	3.5662E-05	1.0998E-06	1.6892E-08	1.0579E-05	7.3723E-07	2.7605E-08	6.4495E-06

68	4.0117E-05	1.0269E-04	1.9200E-02	1.6976E-05	1.0912E-05	1.2038E-04	7.6779E-05	3.9177E-05	3.7378E-05	1.1029E-06	1.6927E-08	1.1293E-05	7.5710E-07	2.8969E-08	7.1836E-06

70	3.7853E-05	1.0240E-04	1.9179E-02	1.7119E-05	1.1156E-05	1.2020E-04	7.7109E-05	3.9283E-05	3.8229E-05	1.1038E-06	1.6936E-08	1.1652E-05	7.6630E-07	2.9623E-08	7.5666E-06

Table 3 - TVS 40 4 % (245*4.1 %+66*3.7 %) 489.8 kg-UO2

W	U235	U236	U238	Np37	Pu38	Pu39	Pu40	Pu41	Pu42	Am41	Am2m	Am43	Cm42	Cm43	Cm44

0	8.5964E-04	0.0000E+00	2.0291E-02	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00

2	8.0967E-04	9.1156E-06	2.0266E-02	1.2173E-07	1.9239E-09	1.9144E-05	6.2981E-07	5.1676E-08	6.2787E-10	7.7613E-11	1.6926E-13	4.4232E-12	1.4845E-12	1.2712E-15	4.2027E-14

4	7.6271E-04	1.7621E-05	2.0240E-02	3.4704E-07	1.1096E-08	3.6603E-05	2.2757E-06	3.6837E-07	9.3300E-09	1.1407E-09	4.6548E-12	1.3815E-10	4.3736E-11	7.7712E-14	2.7268E-12

6	7.1833E-04	2.5594E-05	2.0214E-02	6.4507E-07	3.0742E-08	5.1417E-05	4.5403E-06	1.0551E-06	4.1523E-08	4.9952E-09	2.8562E-11	9.5969E-10	2.8665E-10	7.8705E-13	2.9267E-11

8	6.7623E-04	3.3088E-05	2.0187E-02	1.0061E-06	6.3543E-08	6.4066E-05	7.1942E-06	2.1043E-06	1.1413E-07	1.3458E-08	9.5996E-11	3.6401E-09	1.0265E-09	3.8578E-12	1.5191E-10

10	6.3619E-04	4.0142E-05	2.0160E-02	1.4219E-06	1.1189E-07	7.4903E-05	1.0101E-05	3.4628E-06	2.4221E-07	2.7909E-08	2.3327E-10	9.9509E-09	2.6522E-09	1.2756E-11	5.3172E-10

12	5.9807E-04	4.6784E-05	2.0132E-02	1.8854E-06	1.7795E-07	8.4203E-05	1.3173E-05	5.0649E-06	4.3791E-07	4.9185E-08	4.6327E-10	2.2165E-08	5.5898E-09	3.2954E-11	1.4538E-09

14	5.6172E-04	5.3037E-05	2.0105E-02	2.3906E-06	2.6368E-07	9.2180E-05	1.6350E-05	6.8473E-06	7.1043E-07	7.7611E-08	8.0225E-10	4.2928E-08	1.0256E-08	7.1909E-11	3.3564E-09

16	5.2705E-04	5.8921E-05	2.0076E-02	2.9317E-06	3.7088E-07	9.9012E-05	1.9589E-05	8.7534E-06	1.0663E-06	1.1308E-07	1.2587E-09	7.5126E-08	1.7024E-08	1.3880E-10	6.8536E-09

18	4.9397E-04	6.4451E-05	2.0047E-02	3.5037E-06	5.0113E-07	1.0485E-04	2.2855E-05	1.0735E-05	1.5099E-06	1.5517E-07	1.8338E-09	1.2176E-07	2.6201E-08	2.4415E-10	1.2751E-08

20	4.6242E-04	6.9642E-05	2.0018E-02	4.1019E-06	6.5585E-07	1.0981E-04	2.6121E-05	1.2753E-05	2.0436E-06	2.0319E-07	2.5219E-09	1.8585E-07	3.8021E-08	3.9927E-10	2.2052E-08

22	4.3237E-04	7.4498E-05	1.9988E-02	4.7219E-06	8.3605E-07	1.1399E-04	2.9348E-05	1.4785E-05	2.6678E-06	2.5636E-07	3.3127E-09	2.7023E-07	5.2612E-08	6.1548E-10	3.5950E-08

24	4.0372E-04	7.9039E-05	1.9958E-02	5.3596E-06	1.0429E-06	1.1750E-04	3.2535E-05	1.6790E-05	3.3830E-06	3.1371E-07	4.1919E-09	3.7774E-07	7.0070E-08	9.0436E-10	5.5856E-08

26	3.7644E-04	8.3274E-05	1.9927E-02	6.0114E-06	1.2771E-06	1.2042E-04	3.5665E-05	1.8748E-05	4.1878E-06	3.7419E-07	5.1424E-09	5.1093E-07	9.0392E-08	1.2767E-09	8.3366E-08

28	3.5047E-04	8.7212E-05	1.9896E-02	6.6736E-06	1.5393E-06	1.2282E-04	3.8725E-05	2.0642E-05	5.0800E-06	4.3678E-07	6.1454E-09	6.7206E-07	1.1350E-07	1.7420E-09	1.2026E-07

30	3.2578E-04	9.0862E-05	1.9865E-02	7.3430E-06	1.8297E-06	1.2476E-04	4.1703E-05	2.2460E-05	6.0567E-06	5.0044E-07	7.1815E-09	8.6308E-07	1.3926E-07	2.3084E-09	1.6848E-07

32	3.0239E-04	9.4222E-05	1.9832E-02	8.0165E-06	2.1477E-06	1.2631E-04	4.4561E-05	2.4211E-05	7.1118E-06	5.6442E-07	8.2342E-09	1.0854E-06	1.6737E-07	2.9805E-09	2.2999E-07

34	2.8022E-04	9.7310E-05	1.9800E-02	8.6904E-06	2.4936E-06	1.2750E-04	4.7322E-05	2.5863E-05	8.2448E-06	6.2772E-07	9.2849E-09	1.3404E-06	1.9770E-07	3.7632E-09	3.0707E-07

36	2.5921E-04	1.0014E-04	1.9767E-02	9.3624E-06	2.8668E-06	1.2838E-04	4.9978E-05	2.7413E-05	9.4514E-06	6.8946E-07	1.0317E-08	1.6290E-06	2.3001E-07	4.6589E-09	4.0203E-07

38	2.3935E-04	1.0270E-04	1.9733E-02	1.0030E-05	3.2666E-06	1.2900E-04	5.2524E-05	2.8860E-05	1.0727E-05	7.4891E-07	1.1315E-08	1.9516E-06	2.6396E-07	5.6671E-09	5.1722E-07

40	2.2060E-04	1.0502E-04	1.9699E-02	1.0690E-05	3.6918E-06	1.2939E-04	5.4956E-05	3.0204E-05	1.2067E-05	8.0543E-07	1.2266E-08	2.3085E-06	2.9925E-07	6.7853E-09	6.5507E-07

42	2.0294E-04	1.0710E-04	1.9664E-02	1.1340E-05	4.1410E-06	1.2958E-04	5.7270E-05	3.1444E-05	1.3466E-05	8.5852E-07	1.3160E-08	2.6994E-06	3.3551E-07	8.0086E-09	8.1797E-07

44	1.8633E-04	1.0895E-04	1.9629E-02	1.1979E-05	4.6127E-06	1.2960E-04	5.9462E-05	3.2583E-05	1.4919E-05	9.0775E-07	1.3988E-08	3.1237E-06	3.7241E-07	9.3297E-09	1.0083E-06

46	1.7075E-04	1.1056E-04	1.9593E-02	1.2603E-05	5.1049E-06	1.2947E-04	6.1533E-05	3.3625E-05	1.6422E-05	9.5285E-07	1.4744E-08	3.5806E-06	4.0960E-07	1.0739E-08	1.2285E-06

48	1.5616E-04	1.1196E-04	1.9557E-02	1.3212E-05	5.6156E-06	1.2923E-04	6.3480E-05	3.4572E-05	1.7969E-05	9.9362E-07	1.5425E-08	4.0690E-06	4.4673E-07	1.2227E-08	1.4808E-06

50	1.4254E-04	1.1315E-04	1.9520E-02	1.3802E-05	6.1425E-06	1.2889E-04	6.5305E-05	3.5428E-05	1.9555E-05	1.0300E-06	1.6028E-08	4.5873E-06	4.8348E-07	1.3779E-08	1.7672E-06

52	1.2984E-04	1.1413E-04	1.9483E-02	1.4373E-05	6.6831E-06	1.2848E-04	6.7007E-05	3.6198E-05	2.1175E-05	1.0619E-06	1.6554E-08	5.1338E-06	5.1955E-07	1.5383E-08	2.0898E-06

54	1.1804E-04	1.1492E-04	1.9445E-02	1.4922E-05	7.2349E-06	1.2801E-04	6.8590E-05	3.6888E-05	2.2823E-05	1.0895E-06	1.7003E-08	5.7068E-06	5.5465E-07	1.7024E-08	2.4503E-06

56	1.0711E-04	1.1553E-04	1.9407E-02	1.5449E-05	7.7950E-06	1.2750E-04	7.0055E-05	3.7502E-05	2.4495E-05	1.1130E-06	1.7380E-08	6.3039E-06	5.8852E-07	1.8687E-08	2.8504E-06

58	9.6999E-05	1.1596E-04	1.9368E-02	1.5952E-05	8.3609E-06	1.2695E-04	7.1405E-05	3.8045E-05	2.6184E-05	1.1324E-06	1.7689E-08	6.9230E-06	6.2096E-07	2.0357E-08	3.2913E-06

60	8.7677E-05	1.1622E-04	1.9329E-02	1.6431E-05	8.9296E-06	1.2639E-04	7.2645E-05	3.8523E-05	2.7886E-05	1.1482E-06	1.7933E-08	7.5618E-06	6.5176E-07	2.2019E-08	3.7742E-06

62	7.9106E-05	1.1633E-04	1.9290E-02	1.6883E-05	9.4984E-06	1.2583E-04	7.3778E-05	3.8942E-05	2.9597E-05	1.1605E-06	1.8118E-08	8.2176E-06	6.8078E-07	2.3659E-08	4.2998E-06

64	7.1245E-05	1.1629E-04	1.9249E-02	1.7310E-05	1.0065E-05	1.2526E-04	7.4810E-05	3.9307E-05	3.1311E-05	1.1698E-06	1.8251E-08	8.8881E-06	7.0790E-07	2.5265E-08	4.8686E-06

66	6.4056E-05	1.1611E-04	1.9209E-02	1.7710E-05	1.0626E-05	1.2471E-04	7.5745E-05	3.9622E-05	3.3023E-05	1.1763E-06	1.8338E-08	9.5707E-06	7.3305E-07	2.6823E-08	5.4809E-06

68	5.7497E-05	1.1580E-04	1.9168E-02	1.8082E-05	1.1179E-05	1.2417E-04	7.6590E-05	3.9894E-05	3.4730E-05	1.1804E-06	1.8384E-08	1.0263E-05	7.5618E-07	2.8323E-08	6.1364E-06

70	5.4442E-05	1.1560E-04	1.9147E-02	1.8259E-05	1.1452E-05	1.2390E-04	7.6979E-05	4.0015E-05	3.5580E-05	1.1816E-06	1.8393E-08	1.0612E-05	7.6698E-07	2.9049E-08	6.4803E-06

Table 4 - TVS 16Z 1.6% (311*1.6%) 489.8 kg-UO2

W	U235	U236	U238	Np37	Pu38	Pu39	Pu40	Pu41	Pu42	Am41	Am2m	Am43	Cm42	Cm43	Cm44

0	3.4258E-04	0.0000E+00	2.0802E-02	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00	0.0000E+00

2	2.9717E-04	7.5742E-06	2.0764E-02	1.4381E-07	3.9992E-09	2.6891E-05	1.8445E-06	2.1962E-07	6.2257E-09	3.3493E-10	1.2518E-12	6.2690E-11	1.2656E-11	1.7308E-14	9.0746E-13

4	2.5967E-04	1.3778E-05	2.0725E-02	3.9814E-07	2.1865E-08	4.6827E-05	5.9011E-06	1.2818E-06	7.6122E-08	4.0988E-09	2.5682E-11	1.6533E-09	3.1087E-10	8.8017E-13	5.0237E-11

6	2.2765E-04	1.9003E-05	2.0687E-02	7.1723E-07	5.7836E-08	6.1032E-05	1.0741E-05	3.0993E-06	2.8751E-07	1.5215E-08	1.2263E-10	9.9058E-09	1.7358E-09	7.5706E-12	4.6908E-10

8	1.9987E-04	2.3459E-05	2.0647E-02	1.0842E-06	1.1467E-07	7.1449E-05	1.5820E-05	5.3709E-06	6.8878E-07	3.5455E-08	3.3247E-10	3.3035E-08	5.4058E-09	3.2109E-11	2.1570E-09

10	1.7555E-04	2.7276E-05	2.0607E-02	1.4862E-06	1.9433E-07	7.9220E-05	2.0882E-05	7.8523E-06	1.3003E-06	6.4674E-08	6.7060E-10	8.0598E-08	1.2344E-08	9.3219E-11	6.7828E-09

12	1.5415E-04	3.0547E-05	2.0567E-02	1.9127E-06	2.9806E-07	8.5083E-05	2.5791E-05	1.0379E-05	2.1237E-06	1.0160E-07	1.1309E-09	1.6206E-07	2.3285E-08	2.1385E-10	1.6840E-08

14	1.3528E-04	3.3343E-05	2.0526E-02	2.3551E-06	4.2654E-07	8.9544E-05	3.0470E-05	1.2846E-05	3.1494E-06	1.4445E-07	1.6938E-09	2.8584E-07	3.8610E-08	4.1799E-10	3.5599E-08

16	1.1862E-04	3.5720E-05	2.0485E-02	2.8061E-06	5.7982E-07	9.2962E-05	3.4875E-05	1.5191E-05	4.3609E-06	1.9132E-07	2.3336E-09	4.5873E-07	5.8365E-08	7.2770E-10	6.6983E-08

18	1.0391E-04	3.7727E-05	2.0443E-02	3.2595E-06	7.5742E-07	9.5599E-05	3.8982E-05	1.7380E-05	5.7386E-06	2.4042E-07	3.0234E-09	6.8561E-07	8.2310E-08	1.1608E-09	1.1540E-07

20	9.0922E-05	3.9406E-05	2.0400E-02	3.7103E-06	9.5832E-07	9.7649E-05	4.2784E-05	1.9398E-05	7.2611E-06	2.9021E-07	3.7385E-09	9.6942E-07	1.0999E-07	1.7292E-09	1.8557E-07

22	7.9483E-05	4.0791E-05	2.0357E-02	4.1537E-06	1.1809E-06	9.9244E-05	4.6263E-05	2.1253E-05	8.9064E-06	3.3948E-07	4.4579E-09	1.3113E-06	1.4079E-07	2.4377E-09	2.8224E-07

24	6.9412E-05	4.1916E-05	2.0313E-02	4.5864E-06	1.4235E-06	1.0051E-04	4.9448E-05	2.2929E-05	1.0655E-05	3.8724E-07	5.1652E-09	1.7106E-06	1.7406E-07	3.2858E-09	4.1020E-07

26	6.0559E-05	4.2810E-05	2.0270E-02	5.0055E-06	1.6839E-06	1.0153E-04	5.2352E-05	2.4437E-05	1.2486E-05	4.3275E-07	5.8472E-09	2.1653E-06	2.0909E-07	4.2668E-09	5.7394E-07

28	5.2788E-05	4.3499E-05	2.0225E-02	5.4086E-06	1.9598E-06	1.0237E-04	5.4990E-05	2.5790E-05	1.4381E-05	4.7554E-07	6.4947E-09	2.6723E-06	2.4519E-07	5.3689E-09	7.7756E-07

30	4.5979E-05	4.4008E-05	2.0180E-02	5.7939E-06	2.2487E-06	1.0308E-04	5.7380E-05	2.7004E-05	1.6323E-05	5.1536E-07	7.1022E-09	3.2275E-06	2.8169E-07	6.5761E-09	1.0247E-06

32	4.0024E-05	4.4358E-05	2.0136E-02	6.1597E-06	2.5477E-06	1.0366E-04	5.9524E-05	2.8103E-05	1.8296E-05	5.5221E-07	7.6669E-09	3.8271E-06	3.1799E-07	7.8682E-09	1.3181E-06

34	3.4820E-05	4.4568E-05	2.0090E-02	6.5051E-06	2.8545E-06	1.0417E-04	6.1459E-05	2.9082E-05	2.0289E-05	5.8604E-07	8.1895E-09	4.4652E-06	3.5366E-07	9.2274E-09	1.6605E-06

36	3.0279E-05	4.4656E-05	2.0045E-02	6.8298E-06	3.1666E-06	1.0464E-04	6.3204E-05	2.9955E-05	2.2289E-05	6.1692E-07	8.6697E-09	5.1365E-06	3.8830E-07	1.0634E-08	2.0538E-06

38	2.6320E-05	4.4639E-05	1.9999E-02	7.1334E-06	3.4816E-06	1.0506E-04	6.4776E-05	3.0735E-05	2.4288E-05	6.4503E-07	9.1093E-09	5.8359E-06	4.2159E-07	1.2069E-08	2.4989E-06

40	2.2873E-05	4.4530E-05	1.9953E-02	7.4159E-06	3.7974E-06	1.0545E-04	6.6193E-05	3.1435E-05	2.6275E-05	6.7056E-07	9.5108E-09	6.5582E-06	4.5328E-07	1.3513E-08	2.9965E-06

42	1.9874E-05	4.4341E-05	1.9907E-02	7.6775E-06	4.1119E-06	1.0583E-04	6.7470E-05	3.2065E-05	2.8244E-05	6.9374E-07	9.8772E-09	7.2985E-06	4.8322E-07	1.4952E-08	3.5465E-06

44	1.7266E-05	4.4085E-05	1.9861E-02	7.9185E-06	4.4232E-06	1.0618E-04	6.8621E-05	3.2632E-05	3.0189E-05	7.1480E-07	1.0212E-08	8.0522E-06	5.1130E-07	1.6370E-08	4.1484E-06

46	1.5001E-05	4.3771E-05	1.9814E-02	8.1395E-06	4.7297E-06	1.0652E-04	6.9659E-05	3.3146E-05	3.2105E-05	7.3396E-07	1.0518E-08	8.8151E-06	5.3750E-07	1.7755E-08	4.8012E-06

48	1.3034E-05	4.3407E-05	1.9768E-02	8.3412E-06	5.0300E-06	1.0685E-04	7.0595E-05	3.3612E-05	3.3988E-05	7.5144E-07	1.0798E-08	9.5834E-06	5.6183E-07	1.9099E-08	5.5035E-06

50	1.1326E-05	4.3002E-05	1.9721E-02	8.5241E-06	5.3228E-06	1.0717E-04	7.1441E-05	3.4036E-05	3.5836E-05	7.6743E-07	1.1056E-08	1.0353E-05	5.8432E-07	2.0392E-08	6.2536E-06

52	9.8434E-06	4.2562E-05	1.9674E-02	8.6890E-06	5.6072E-06	1.0748E-04	7.2206E-05	3.4423E-05	3.7646E-05	7.8210E-07	1.1294E-08	1.1122E-05	6.0506E-07	2.1631E-08	7.0494E-06

54	8.5570E-06	4.2093E-05	1.9628E-02	8.8369E-06	5.8822E-06	1.0777E-04	7.2898E-05	3.4777E-05	3.9417E-05	7.9559E-07	1.1513E-08	1.1887E-05	6.2413E-07	2.2810E-08	7.8888E-06

56	7.4406E-06	4.1600E-05	1.9581E-02	8.9684E-06	6.1473E-06	1.0805E-04	7.3526E-05	3.5102E-05	4.1147E-05	8.0805E-07	1.1717E-08	1.2646E-05	6.4163E-07	2.3929E-08	8.7694E-06

58	6.4719E-06	4.1088E-05	1.9534E-02	9.0845E-06	6.4017E-06	1.0833E-04	7.4095E-05	3.5400E-05	4.2836E-05	8.1958E-07	1.1907E-08	1.3396E-05	6.5768E-07	2.4986E-08	9.6888E-06

60	5.6311E-06	4.0561E-05	1.9488E-02	9.1859E-06	6.6452E-06	1.0858E-04	7.4611E-05	3.5675E-05	4.4483E-05	8.3028E-07	1.2084E-08	1.4136E-05	6.7238E-07	2.5982E-08	1.0644E-05

62	4.9014E-06	4.0021E-05	1.9441E-02	9.2736E-06	6.8774E-06	1.0883E-04	7.5081E-05	3.5928E-05	4.6088E-05	8.4024E-07	1.2250E-08	1.4865E-05	6.8584E-07	2.6917E-08	1.1633E-05

64	4.2679E-06	3.9472E-05	1.9394E-02	9.3483E-06	7.0981E-06	1.0907E-04	7.5507E-05	3.6162E-05	4.7652E-05	8.4953E-07	1.2405E-08	1.5580E-05	6.9818E-07	2.7794E-08	1.2653E-05

66	3.7178E-06	3.8917E-05	1.9347E-02	9.4107E-06	7.3074E-06	1.0929E-04	7.5895E-05	3.6379E-05	4.9175E-05	8.5820E-07	1.2551E-08	1.6282E-05	7.0948E-07	2.8615E-08	1.3701E-05

68	3.2401E-06	3.8357E-05	1.9301E-02	9.4618E-06	7.5051E-06	1.0949E-04	7.6248E-05	3.6579E-05	5.0657E-05	8.6632E-07	1.2687E-08	1.6970E-05	7.1985E-07	2.9383E-08	1.4775E-05

70	3.0253E-06	3.8076E-05	1.9277E-02	9.4833E-06	7.5996E-06	1.0959E-04	7.6412E-05	3.6674E-05	5.1383E-05	8.7018E-07	1.2753E-08	1.7308E-05	7.2471E-07	2.9748E-08	1.5321E-05

Sheet registration changes

| chan. | Page number |  |  |  | Total pages in documents. | № docume nts | Incoming number of accompanying doc. and the date | Signa ture. | date |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | modified | replaced | new | annulled |  |  |  |  |  |

Sheet registration changes (CONTINUE)

| chan. | Page number |  |  |  | Total pages in documents. | № docume nts. | Incoming number of accompanying doc. and the date | Signa ture. | date |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | modified | replaced | new | annulled |  |  |  |  |  |