FEDERAL STATE UNITARY ENTERPRISE VO “SAFETY”

Reg. No. 08/619	"APPROVED"

of 02.11.2016

Deputy Director for Development-

Head of STS Direction of

FSUE VO “Safety”

M. Kuznetsov

" 	 " 	 2017

EXPERT REPORT

on results of review of Chapter 7 “Instrumentation and control systems (I&C)” of

Final Safety Analysis Report. “Bushehr” NPP. Power Unit 1. 
49.BU.1 0.0.ОО.FSAR.RDR001

Agreed by:

Deputy Technical Director for BNPP Project	Director for Development of

FSUE VO “Safety”

T.V. Tetyushina		 E.Yu. Kapralov

" 	 " 	 2017	" 	 " 	 2017

BNPP Project Manager	Head of Review Department

P.V. Medvedev		 V.V. Zorichev

" 	 " 	 2017	" 	 " 	 2017

Chief Expert

E.A. Katkovskiy

" 	 " 	 2017 г.

Moscow 2016

FEDERAL STATE UNITARY ENTERPRISE VO “SAFETY”

Reg. No. 08/619	"APPROVED"

of 02.11.2016

Deputy Director for Development-

Head of STS Direction of

FSUE VO “Safety”

M. Kuznetsov

" 	 " 	 2017

EXPERT REPORT

on results of review of Chapter 7 “Instrumentation and control systems (I&C)” of

Final Safety Analysis Report. “Bushehr” NPP. Power Unit 1. 
49.BU.1 0.0.ОО.FSAR.RDR001

Moscow 2016

Content

1. Introduction	3

1.1 Subject of review	3

1.2 Basis for review	3

1.3 Objective and tasks of review	3

1.4 Expert judgments on the issue	3

List of adopted abbreviations	9

2. Comments to Chapter 7 of FSAR	11

2.1 General comments to the Chapter	11

2.2 Assessment of modifications introduced to Chapter 7 on results of Power Unit commissioning and in connection with the accepted technical decisions	15

2.3 Assessment of correctness of modifications due to comments made during review of the FSAR, revision 0	20

3. Findings and recommendations	371

References	372

i. List of documents considered during review	372

Ii. List of documents, which requirements have been selected as expert assessment criteria	372

# 1. Introduction

## 1.1 Subject of review

Chapter 7 "Instrumentation and control systems (I&C)" of document “Final Safety Analysis Report. Power Unit No. 1. “Bushehr” NPP” 49.BU.1 0.0.ОО.FSAR.RDR001 (revision 2, issued in December 2014).

## 1.2 Basis for review

NNSD Work Order for review of Chapters 3-11, 15, 16 of Final Safety Analysis Report on Power Unit No. 1 of “Bushehr” NPP 49.BU.10.0.OO.FSAR.RDR001 (revision 2 dated March 2015) (hereinafter referred to as the FSAR) corrected on the results of commissioning of BNPP-1 (INRA/NNSD letter No. 2016/07 of 29.02.2016).

## 1.3 Objective and tasks of review

The objective of preliminary review is assessment of sufficiency of safety substantiation for NPP "Bushehr" Power Unit-1 in the stage of operation.

In review of Chapter 7 "Instrumentation and control systems (I&C)" of the FSAR, the following tasks were determined:

- assessment of modifications introduced to Chapter 7 "Instrumentation and control systems (I&C)" of the Final Safety Analysis Report, "Bushehr" NPP, Power Unit No.1, on results of the Power Unit commissioning and in connection with the technical decisions taken in the stage of the Power Unit commissioning;

- assessment of correctness of modifications introduced to Chapter 7 "Instrumentation and control systems (I&C)" of the Final Safety Analysis Report, "Bushehr" NPP, Power Unit No.1, considering the comments made during the review of the FSAR, revision 0.

## 1.4 Expert judgments on the issue

Chapter 7 "Instrumentation and control systems (I&C)" of document Final Safety Analysis Report. Power Unit No.1. NPP "Bushehr" 49.BU.1 0.0.ОО.FSAR.RDR001 (revision 2 issued in December, 2014) represents a description of Automated Process Control System (APCS) that is intended for control and monitoring of the main and auxiliary technological processes of heat and power generation at NPP and for safety assessment under all operating conditions including emergency situations and accidents, as well as NPP efficiency during normal operation.

Total list of all the design modes with operational occurrences and the design-basis accidents requiring automatic action of the I&C systems is given in Sections 15.1 and 15.2 of Chapter 15.

For every accident initiating event, provisions are made for relevant technical and organizational measures to prevent and mitigate consequences of effects on the protective barriers through restricting the normal operation as much as to shut down the NPP.

The safety functions are fulfilled by a number of the APCS parts to provide “defence-in-depth” at different levels in accordance with severity of the caused malfunctions:

1. First level - prevention of the operational occurrences to ensure safe operation of the Power Unit and to minimize probability of accident initiating events. For this, the normal operation I&C are used for control and monitoring for:

- keeping the main technological process;

- maintaining and restricting effect on the barriers within the operational limits;

- monitoring the critical safety functions, safety parameters and preparedness of safety systems;

- ensuring the living environment for personnel;

- restricting radiation effect upon the personnel, public, environment.

- 2. Second level - mitigation of the operational occurrence consequences. For this, the normal operation APCS systems are applied including safety-related systems used for control and monitoring for:

- keeping (restriction, termination) the main technological process;

- maintaining and restricting effects on the barriers within the safe operation limits and conditions;

- monitoring the critical safety functions, safety parameters and preparedness of safety systems;

- ensuring the living environment for personnel;

- restricting radiation effect upon the personnel, public, environment.

- 3. Third level - during design-basis accidents, the safety systems are activated. For this, the control safety systems are used for reactor shutdown and bringing the NPP to a safe condition. NPP safety is provided due to:

- reliable termination of the main technological process;

- maintaining and restriction of effects on the barriers within maximum design limits;

- monitoring of RP sub-criticality,  safety parameters and operation of safety systems;

- providing the living environment for personnel;

- restricting radiation effect upon the personnel, public, environment.

- 4. Fourth level - restriction of the beyond design-basis accident consequences. For this, any accessible I&C systems are used, as well as additional systems intended to maintain the living environment for the shift personnel and to protect the containment system against effects arising, inter alia, from possible failure of the rest barriers as well.

- In this situation, the I&C systems and organizational measures shall ensure:

- termination of the main technological process;

- maintaining and restriction of effects on the barriers for potential reduction of the maximum design limit on the containment system;

- ensuring the living environment for personnel;

- restriction of radiation effects upon the personnel, public, environment.

- To fulfil all the tasks assigned for the APCS, it consists of the following:

- sensors;

- pulse tube laying downstream the shut-off devices or the root valves;

- racks and elements to install the sensors;

- remote control tools for interlocks and protections;

- software & hardware for information processing, storage and transmission;

- information display and recording tools (secondary instruments, displays, panels, indicators, etc.);

- local boards and central control boards with on-line command elements;

- means for input and output of the information and control discrete signals for the actuating  switchgear devices;

- cables, cable lines and penetrations;

- tools of power supply to APCS hardware complex from  the auxiliary switchgear busbars including low-voltage devices;

- automation tools to be delivered together with the process equipment;

- radiation monitoring tools;

- instrumentation, racks, equipment and tools to ensure maintenance, repair and metrological support of  the APCS tools.

The structure of the automated process control system  (APCS) has a hierarchical principle of integration as per the Power Unit  break down into process functional areas and groups where hardware of low-level automatics provide implementation of tasks of communication with a process control object (data collection and generation of commands), as well as implementation of tasks pertaining to protections, interlocks, self-regulation, alarm and control of the valves, mechanisms, solenoids, etc.

The APCS engineered tools of the Power Unit include the RP monitoring, control and protection systems, which fulfill specific functions for reactor protection, reactor power restriction and regulation through effect on actuators, diagnostics functions of equipment and reactor core condition, coolant leaks detection, they perform functioning analysis and ensure self-diagnostics of auxiliary engineered tools and communication lines.

Expert judgment on algorithms of protections and interlocks of safety systems

Assessment of algorithms for compliance with the safety requirements

Assessment of algorithms for compliance with the safety requirements is based on the principle that an algorithm, as a design product, is a control tool to be implemented in the software-and-hardware complex.

Reliability of CSS safety functions fulfillment fully depends on both design properties of the algorithm and the engineered tools implementing it.

In review, since CSS has a four-train structure, YZ algorithm is considered as consisting of four separate algorithms, i.e.: algorithm YZ 20 - 1 YZ 20, 2 YZ 20, 3 YZ 20, 4 YZ 20.

Compliance of software-and-hardware tools implementing the control algorithms with the requirements of regulatory documents

The description of control system of safety systems activation (Section 7.3 of FSAR) contains the developer’s information that the CSS and its engineered tools are in full compliance with the requirements of OPB-88/97 and recommendations specified in the regulatory documents, at that:

- S&HW are capable of fulfilling safety functions in case of a single failure, failure on an initiating event cause and during maintenance. Requirement of item 1.2.12 of OPB-88/97 is fulfilled.

- Classification of the system and S&HW, accordingly, is in compliance with the provisions specified in Section 2 of OPB-88/97.

- S&HW are capable of fulfilling functions under internal and external impacts. Requirement specified in item 4.1.5 of OPB-88/97 is fulfilled.

- Measures for prevention and protection of S&HW against a common cause failure (functional and physical independence, manual control during PIE, control from two control boards) are taken. Requirement specified in item 1.4.6 of OPB-88/97 is fulfilled.

- Continuous automatic and periodic diagnostics of S&HW functioning in accordance with the algorithm are envisaged. Requirement specified in item 4.4.5.8 of OPB-88/97 is fulfilled.

At the same time, it is mentioned that the description of SS activation system does not contain the information that continuous automatic and periodic diagnostics of manual control signal operability (from buttons at MCR and ECR, via RCD up to the input to the algorithm) are envisaged. This concerns algorithms YZ 10, YZ 20 and YZ 30, wherein the manual control is envisaged.

There is neither no information about continuous automatic and periodic diagnostics of input signal "Gamma-background" in algorithm YZ 60 and, generally, about a possibility to control the detector of this signal during normal operation.

- YZ CSS automatically performs the function of SS activation; and with it, CSS SS also automatically performs control functions for the process safety system. Requirement specified in item 4.4.5.2 of OPB-88/97 is fulfilled.

- A possibility of remote control over SS (on algorithms of a specific system) is also envisaged in the design. Failure in the circuit of automatic switch-on (on YZ) does not impede the remote activation. Requirement specified in item 4.4.5.4 of OPB-88/97 is fulfilled.

Compliance of YZ (YZ 10-60) algorithms properties with the requirements and recommendations of documents on NPP safety

The regulatory documents used during the review do not contain the requirements directly referring to the algorithms – the requirements do not specify that this particular requirement is related to the algorithm, but not to the whole control system. The fact that the requirement or recommendation is related to the control algorithm can be derived only from their meaning content.

Assessment of algorithm properties for compliance with the requirements of OPB-88/97 concerning algorithms:

- Requirements specified in item 1.2.12 – safety.

All groups of algorithms are implemented in four trains and are capable of performing the control function during a single failure, an initiating event failure and a maintenance failure. As for impact to FSIV, YZ 20 does not fail in case of a single failure and an initiating event failure.

The algorithms are in compliance with the requirement specified in OPB-88/97.

- Requirements specified in item 4.4.5.2 – automatic fulfillment of a function.

All groups of YZ algorithms perform functions automatically on PIE signals, and three groups of YZ on operator’s command as well. The algorithms are in compliance with the requirement of OPB-88/97. Manual activation by the operator with YZ priority is not governed in OPB-88/97.

- Requirements specified in item 4.4.5.3 – blocking of operator’s actions.

YZ algorithms block the operator’s actions till full completion of the safety function, as it is required in item 4.1.11 of OPB-88/97. This design decision does not contradict the requirement for blocking within 10-30 min.

The design is in compliance with the requirement of OPB-88/97.

- Requirements of item 4.1.8 – availability of tools preventing personnel single errors.

Tools to prevent personnel single errors "pushing the buttons at MCR or ECR" for actuation of algorithms of YZ10, YZ20 and YZ30 groups are not envisaged in the design.

These groups of algorithms are not in compliance with the requirement of OPB-88/97.

- There is no requirement for blocking of actions of equipment protections on YZ commands in OPB-88/97.

Failure of the equipment protection during SS activation on YZ command should be considered as "a single failure" corresponding to the requirement of item 1.2.12 in OPB-88/97. If we consider the protection failure in the design as additional and as required according to item 1.2.12, in this case we would have a greater reliability redundancy than it is required by the standards.

Compliance of ТН algorithms properties with the requirements and recommendations related to NPP safety

The main difference of the design decisions related to the control algorithms for ТН system is that the algorithms for control over pumps ТН1040D001 and gate valves (four in each train, 16 altogether) on the water supply pipelines to RP, envisage the interruption of YZ command and performance of actions by the operator (disabling the pump or closing the gate valves), which is not in compliance with the safety requirements.

The command interruption process is followed by alarm "Warning" and "Non-conformity".

This design decision is not in compliance with the following requirements of OPB-88/97, if the operator used the button and disabled all ТН trains:

- The started protective action is not brought to the full completion. Requirement specified in item 4.1.11 is not fulfilled.

- Measures to prevent personnel single errors during the interruption of YZ commands are not taken – the operator can disable the only one activated pump ТН10 or ТН15, or cut off water supply to the reactor from the only one activated pump. Requirement specified in item 4.1.8 is not implemented.

- The operator can remove the blocking by his actions on TH system in less than 10-30 min. Requirement specified in item 4.4.5.3 is not implemented.

- In general, the operator’s right to interrupt the command for safety systems actuation could lead the operator by mistake or intentionally to stop performance of the safety function – removal of decay heat from the reactor core, and to transfer the design-basis accident into the beyond-design-basis accident.

This means that the requirement specified in item 1.2.12 about assuring safety during "a single error of personnel independent on an initiating event" is not implemented and the safety assurance concept is violated, item 4.1.2.

- OPB-88/97 does not prohibit the interruption of YZ command, but it prohibits stopping  the protective action by the operator.

The protective action is interrupted only if the operator erroneously puts out of work all the activated trains or the last operating train of the SS, only in this case the design decision proposed for the control system of "Bushehr-1" NPP would not comply with the requirements of items 4.1.11, 1.2.12 and 4.1.2 of OPB-88/97.

If the operator does not make a mistake, then there is only one deviation from the requirements of OPB-88/97 on item 4.4.5.3 – the ban can be canceled earlier than it should last (10-30 min.).

Analysis of permissibility on safety conditions of design decision for interruption of control safety system commands by the operator

1. BNPP-1 Power Unit is designed in such a way that the operator’s intervention in protective actions till full deactivation of the protection function is unnecessary. However, in order to prevent the operator’s erroneous actions after actuation on YZ, in accordance with the requirement specified in item 4.1.8 of OPB-88/97 ("the design shall provide for tools to mitigate the personnel single errors"), the ban of operator’s actions is envisaged.

At the same time, to manage the consequences of false activation, i.e. when there is no PIE and normal operation is underway, the algorithms of individual elements of systems assuring the safety function - emergency heat removal, envisage interruption of the false protection command and, respectively, interruption of its action.

This action, as performed on a false command, is not protective.

2. Interruption of YZ protection commands by the operator and, as a result, termination of protective actions till their full completion are implemented in the design in such a way that the operator can erroneously deactivate the last or the only one safety system train activated on PIE. Apparently, in order to prevent an error, the operator’s actions are regulated in "special instructions for remote control over mechanisms in emergency modes" (i.7.3.1.2 FSAR).

But the operator can make "a single error" and deactivate the only operating train of the SS.

The design, with regard to interruption management, shall exclude a possibility of disabling the last operating train, which is a condition for safety assurance during the design initiating event of an accident.

3. The draft of algorithms, with regard to interruption of YZ commands for individual SS elements, shall be supplemented with measures to minimize false impact on the button for commands cancelation. For this purpose, besides "special instructions" and alarm "Warning" and "Non-conformance", it is necessary to arrange for alarm "Manual control is permitted" and "Manual control is prohibited".

Sufficiency of the measure proposed should be confirmed by the probabilistic analysis of safety function fulfillment.

# List of adopted abbreviations

AFPS	-	automatic fire protection system

APCS	-	automated process control system

ARPC	-	automatic reactor power controller

ATPC	-	automatic turbine power controller

AWS	-	automated workstation

CAS	-	complex analysis system

CPSE	-	control and protection system equipment

CSE	-	control system electronics

CSS	-	control safety system

CV	-	control valve

DDLH	-	data display and logging hardware

DG	-	diesel generator

ECC	-	emergency command cabinet

ECCS	-	emergency core cooling system

ECR/SCR	-	emergency control room/standby control room

EMC	-	electromagnetic compatibility

EP	-	emergency protection

ERM	-	emergency radiation monitoring

ESFAS	-	engineered safety feature actuation system

ESFIP	-	engineered safety feature initiating part

ISPE	-	industrial seismic protection equipment

FCC	-	facility communication complex

FSAR	-	Final Safety Analysis Report

FSIV	-	fast-acting steam isolation valve

GDC	-	general design criteria

GMP	-	generalized mimic panel

HP	-	high pressure

ICIS	-	in-core instrumentation system

ICSE	-	initial cause signaling equipment

I&C	-	instrumentation and control system

IOPRS	-	important operation parameters registration system

LAN	-	local area network

LCB	-	local control board

LCC	-	local crisis center

LP	-	low pressure

LSS	-	limit stop switch

MCDS	-	monitoring, control and diagnostics

MCR/UCB	-	main control room/unit control board

NFME	-	neutron flux monitoring equipment

NNSD 	-	National Nuclear Safety Department

NPP	-	nuclear power plant

PICS	-	programmable instrumentation and control system

PIE	-	postulated initiating event

PLC	-	power limitation controller

PP	-	preventive protection

PPPE	-	process parameter protection equipment

PSA	-	Probabilistic Safety Analysis

PSAR	-	Preliminary Safety Analysis Report

PSLE	-	power setback and limitation equipment

RB	-	regulatory body

RC	-	reactor compartment

RCD	-	remote control device

RCP	-	reactor coolant pump

RMI	-	reactivity monitoring instrumentation

RMS	-	radiation monitoring system

RO	-	reactor operator

RP	-	reactor plant

SG	-	steam generator

SGIC	-	system of group and individual control

S&HWC	-	software-and-hardware complex

S&HWC ICND	- soft-and-hardware complex of in-core acoustic diagnostics

S&HWC-P	-	software-and-hardware complex of protections

SLPE	-	signal logical processing equipment

SS	-	safety system

SW	-	software

TLS-U	-	top level system of the power unit

TO	-	turbine operator

USS	-	unit shift supervisor

WS	-	workstation

# 2. Comments to Chapter 7 of FSAR

## 2.1 General comments to the Chapter

2.1.1 Substantiation presented in Chapter 7 of the FSAR should confirm that the control systems are capable of maintaining the system variables within the limits of design operating parameters in transients and during normal operation occurrences such as power variation of reactor, turbine, occurrences in feedwater systems and steam bypasses.

The Chapter is missing the following to carry out the full analysis:

- information on turbine and generator protections;

- information about main regulation systems and Power Unit regulators: turbine regulation system, system of coolant level regulation in the pressurizer, pressure regulator in the primary circuit, level regulator in the steam generator, regulator BRU-А, regulator BRU-К (regulation laws, synchronization modes, redundancy, bringing to automatic mode and switchover to the remote control mode, failures, etc.);

- information about reduction of turbo-generator and RP power balances when disabling the turbine hall equipment and unsuccessful ASBE.	(2.1-1)

2.1.2 Main regulation systems shall control the reactor and turbine power in such a way that the primary and secondary circuits be able to operate in power and material balance at the selected power level, which shall be confirmed by the analysis (non-conformance with i. 4.4.4 of OPB-88/97).	(2.1-2)

2.1.3 Information about control loops stability is missing (non-conformance with i. 4.4.4 of OPB-88/97).	(2.1-3)

2.1.4 Information confirming implementation of the "defense-in-depth" principle for the secondary circuit equipment is missing.	(2.1-4)

2.1.5 Since Section 7.7 of FSAR describes instrumentation and control systems not related to safety systems, all the descriptions related to S&HWC-P shall be shifted to the respective Section of the FSAR (Section 7.2).	(2.1-5)

2.1.6 Chapter 7 of FSAR requires serious updating to confirm observance of safe operation limits and conditions (a fuller analysis for substantiation of the design compliance with the design general criteria and safety criteria), a thorough analysis of potential operator’s intervention before the expiry of the time ban after safety systems actuation, full observance of requirements of regulatory documentation and other supporting documents (including manufacturers’ documentation), as well as with account of the comments given in the present report.                                                     (2.1-6)

2.1.7 Additional materials and modifications described in Appendix 1 to the PSAR have not been included to Chapter 7 of the FSAR, which resulted in degradation of some sections of the FSAR as compared to the PSAR.	(2.1-7)

2.1.8 The modifications introduced into APCS design after issuance of the FSAR, as well as the results of acceptance tests of APCS subsystems of the Power Unit and software-and-hardware complexes have not been reflected in Chapter 7 of the FSAR.	(2.1-8)

2.1.9 The information and, correspondingly, analysis of radiation monitoring and "black box" subsystems (important operation parameters registration system) are missing from Chapter 7 of the FSAR.	(2.1-9)

General comments related to algorithms

2.1.10 The description of "Systems of actuation …" does not contain full information about acceptability of manual operations: there is no data on sufficiency and clarity of the presented information, about necessity for manual operations, sufficiency of time for performance of necessary actions. The operator is provided with the manual and tools for implementation only (buttons at MCR and ECR).	(2.1-10)

2.1.11 False actuation of safety systems.

Main principles:

- false actuations minimization;

- false actuation shall not affect safety;

- more than one false actuation shall not be at any time.

The control system shall be designed as resistant to false actuations of this system and shall not activate safety systems or devices when it is not necessary and process parameters do not comply with PIE. The following requirement to the design of algorithms results from this recommendation: the activation conditions shall be assigned in such a way that they could occur only in case of an accident and could not occur in any other condition of the Power Unit or its operating mode during normal operation and operational occurrences.

Conditions of SS activation in YZ10 group and containment isolation in YZ30 group on Δts<10°C signal do not comply with the recommendation, since Δts<10°C could occur at the shutdown and cooled down reactor during violation of heat removal mode (the coolant in the reactor can be heated up to 90°С), during erroneous pressure drop in the RP after performance of hydraulic testing for leak-tightness and during  pressure regulator failure in the pressurizer.

In these cases, all trains of ТН system (HP and LP) are activated, the gate valves on the pipelines from ECCS hydraulic accumulators to the reactor open, and the containment is isolated, the operator is discharged from control until he comprehends to use YZ signal interruption button (there is no such button in the hydraulic accumulator system).

False actuation of high pressure pumps (ТН1545D001) and opening of valves on water supply pipelines to the reactor from ECCS hydraulic accumulators affect safety, because pressure could occur in the RP, which exceeds permissible one with regard to conditions for reactor vessel metal cold brittleness.

Summary:

- number of false actuations is not minimized in the design – the algorithms in two groups actuate for all the trains;

- false actuation on YZ10 group affects safety;

- more than two failures are possible at the same time (YZ10 and YZ30).	(2.1-11)

Additional comments to the algorithms

2.1.12 It is mentioned in the ESFAS description that manual control of SS activation is designed for three protections, including the containment localization. But the algorithms of this group – YZ30 have no input signal "operator’s command", only PIE signals are present.	(2.1-12)

2.1.13 The protective action on group of YZ60 algorithms for control over TW system is automatic, but in the description (table 7.3.1.3-2) – manual by the operator.	(2.1-13)

2.1.14 There is no condition for algorithm actuation on Δts signal in algorithms of group YZ10 (primary circuit leak). Hence, false actuation is possible, since Δts<10°C could occur during normal operation occurrences, at that, all the trains of ТН system are activated and the containment is isolated on YZ30 algorithms.	(2.1-14)

2.1.15 As for groups of algorithms YZ10, YZ20 and YZ30, wherein manual operation is envisaged, there is no information that measures are taken to prevent erroneous putting SS to operation, if the operator erroneously pushes the start buttons.	(2.1-15)

2.1.16 Algorithms YZ10 "Primary circuit leak" and YZ30 "Containment isolation" are different in output signals only, and actuation signals in both algorithms are the same. The necessity for two algorithms for protection under the same PIE is not clear. It would be logic to unite these protections and isolate the containment on В1 commands from YZ10 algorithms.	(2.1-16)

2.1.17 The source of input signal р>30kPa in groups of YZ10 and YZ30 algorithms is designated as YCS05ER105, i.e. designated with the reactor symbols YC, but not with the containment symbols XQ, wherein these pressure sensors are located.	(2.1-17)

2.1.18 "Technology" for interruption of YZ command by the operator is not in compliance with the requirement of item 4.1.8 of OPB-88/97 – no tools to prevent the operator’s single error.	(2.1-18)

2.1.19 Comments on RA system:

- There is no possibility for transition of BRU-A to "Cooldown" mode after temperature rise in the primary circuit <200°С/h in algorithms of control SG PSD 11RAS10BA001, 12RAS20BA001, 13RAS30BA001, 14RAS40BA001 when protection signal "Primary–to-secondary leak" is present, which contradicts document 49.BU1 0.0.00.FSAR.RDR001.	(2.1-19)

- According to FSAR 49.BU1 0.0.00.FSAR.RDR001, item 15.2.3.5.2.3, table 15.2.3.5-2, the cooldown of SG (primary circuit) through BRU-A is envisaged with the rate of 15°С/h in mode "Primary–to-secondary leak within steam generator" under temperature in the primary circuit lower than 200 °С. In respect of functionality of BRU-A regulator, the cooldown rate of 30°С/h is envisaged in this case.    	(2.1-20)

- In algorithms 11RAS10EE001, 12RAS20EE001, 13RAS30EE001, 14RAS40EE001, during actuation of set point РSG<6.27 МPа and the following remote opening of CV RAS1040AS003 by the operator, their "suspension" in half-open condition (escape from LSS) takes place, because the blocking for CV closing is given to input Р (protective closing) of mask CV irrespectively of the command given for the valve opening. The command for opening will be at the mask input until CV opens >6%, and the command for closing will be until the limit stop switch is actuated. Since both commands are given to protective inputs of CV mask and the logic of their priority processing (in case of blocking Р<6.27 МPа) is missing from the algorithm, the above described situation takes place. 	(2.1-21)

- The algorithms of BRU-A control 11RAS10EE001, 12RAS20EE001, 13RAS30EE001, 14RAS40EE001 envisage the ban of remote control over BRU-A regulators from ECR and  MCR in disabled mode "Cooldown" and pressure in SG being lower than 6.27 МPа. This would not allow to provide the "natural circulation" mode of the primary coolant in case of deactivation of all RCPs. In order to eliminate this fault, it is necessary to envisage a possibility for BRU-A remote control in "Cooldown" mode and envisage an interlock that would prevent a possibility of exceeding the cooldown rate by the operator in the remote mode more than 60°С.	(2.1-22)

- In algorithms 11RAS10AS005, 12RAS20AS005, 13RAS30AS005, 14RAS40AS005, when cooling down via BRU-A in case of actuation of protection "Primary–to-secondary leak" to gate valve RAS10-40AS005, two equivalent commands stand for opening and closing and, as a result, the gate valve would remain in open position.	(2.1-23)

- Algorithms 12YZS60EY001A, 12YZS60EY002A, 12YZS60EY003A, 12YZS60EY004A for formation of protection "Primary–to-secondary leak" for BRU-А 1-4 in the third and fourth safety systems are different from the process algorithms for setting and implementation of these algorithms in functional plans of the first and second safety systems.	(2.1-24)

2.1.20 The value of nominal level in SG (2450 mm or 2400 mm) should be clarified for RS system.	(2.1-25)

2.1.21 As for TH system, the selection of cooldown mode at the rate of "30°С/h" and "60°С/h" is envisaged in the functional layouts of primary circuit scheduled cooldown regulators in algorithms 11THS10DT001, 12THS20DT001, 14THS40DT001 in automatic mode. As it comes from the pre-commissioning experience on the similar system of commercial Power Unit V-230, the cooling down at the temperature of the primary circuit being lower than 200°С shall be performed at the rate not more than 30°С/h (as per requirement of OKB Gidropress, the cooldown mode at the rate of 60°С/h was excluded). 	(2.1-26)

2.1.22 While using the developed algorithms, it is impossible to use pump unit TH18(28,38,48)D001 for removal of cooling pond decay heat in all Power Unit operating modes as it is envisaged in FSAR 49.BU.1 0.0.ОО.FSAR.RDR001 (Ch. 6.3.1.1.5.5 "Functioning of the system" of the FSAR):

- it is impossible to supply chilled water from the cooling pond through heat exchanger ТН10(20,30,40)В003, because control valve ТН10(20,30,40)S007 cannot be opened in the remote mode. The ban on disabled condition of TH10(20,30,40)D001 is applied to it;

- it is not possible to open ТН10(20,30,40)S011 in order to return water to the cooling pond at the required flow rate. The ban on disabled of TH10(20,30,40)D001 is applied to it.	(2.1-27)

2.1.23 The design does not envisage interlocks that would prevent the joint operation of pump units TH18(28,38,48)D001 and TH10(20,30,40)D001. (The joint operation of pump units TH18(28,38,48)D001 and TH10(20,30,40)D001 leads to operation of TH18(28,38,48)D001 in  "non-flow" mode).	(2.1-28)

2.1.24 The position of control valve TH10(20,30,40)S008 in "standby" mode is not clearly defined. Depending on operator’s actions, the situation is possible when the valve turns out to be closed. Besides, the closed position of valve is accepted for initial condition of the subsystem according to the FSAR (Chapter 6, Table 6.3.1.1.3.6-1). The command for the valve opening is envisaged only on actuation of YZ10 protection.	(2.1-29)

2.1.25 While preparing TH10(20,40) train for operation in scheduled cool down mode of the primary circuit (connection to the primary circuit and heat up of the train prior to the coolant injection to the circuit), the situation is possible when the pump flow rate can be reduced to lower than 240 m3/h because of the operator’s error. Flow rate reduction of the operating pump with open TH90S001, TH90S002, TH90S005, TH90S006, TH10,20,40S006, TH91(92,94)S001 will lead to opening of TH10(20,40)S013,014 and ingress of the primary coolant to tank 
TH10(20,40)B001,002.	(2.1-30)

2.1.26 De-energization and activation of the step-wise startup during the cool down of the primary circuit also initiates the situation when the ingress of "hot" coolant from the primary circuit to TH10(20,40)B001,002 occurs.	(2.1-31)

2.1.27 Implementation of YZ60 protection ("Primary–to-secondary leak") is distinctly different from the design algorithm and as a result it is impossible to cool down the RP through BRU-A during management of the emergency situation.	(2.1-32)

## 2.2 Assessment of modifications introduced to Chapter 7 on results of Power Unit commissioning and in connection with the accepted technical decisions

| SHEET OF ISSUES 1 |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue number | 2.2-1 |
|  |  | Section number | - 7.4 |
|  |  | Page | 7-154 |
| Facility | "Bushehr-1" NPP |  |  |
| Issue title | Management of mode "pressure rise restriction in the primary and secondary circuits" |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1 Technical decision description |  |  |  |
| Use of BRU-K is added for mode "pressure rise restriction in the primary and secondary circuits" |  |  |  |
| 2.2 Assessment of modifications introduced |  |  |  |
| - It is considered in Revision 2 of the FSAR and introduced to Table 7.4-3 "List of systems required to bring the Unit to a safe condition during operational occurrences" |  |  |  |
| 2.3 Recommendations |  |  |  |
| To consider in the final SAR |  |  |  |
| 2.4 References |  |  |  |
| Register of changes of FSAR Chapter 7 Section 7-4 Revision 2 |  |  |  |

| SHEET OF ISSUES 2 |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue number | 2.2-2 |
|  |  | Section number | 7.3.1.3 |
|  |  | Page | absent |
| Facility | "Bushehr-1" NPP |  |  |
| Issue title | Compliance of MCR and ECR boards, WD package 34.BU.1 0.0.AP. PZ. RDR005 |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1 Technical decision description |  |  |  |
| Compliance of MCR and ECR boards, WD package 34.BU.1 0.0.AP. PZ. RDR005 |  |  |  |
| 2.2 Assessment of modifications introduced |  |  |  |
| Not introduced. |  |  |  |
| 2.3 Recommendations |  |  |  |
| Give Table 7.3.1.3-1 in subsection 7.3.1.3 and introduce the modification |  |  |  |
| 2.4 References |  |  |  |
| Register of changes of FSAR Chapter 7 Section 7-4 Revision 2 |  |  |  |

| SHEET OF ISSUES 3 |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue number | 2.2-3 |
|  |  | Section number | 7 |
|  |  | Page | no |
| Facility | "Bushehr-1" NPP |  |  |
| Issue title | Dismantling of control rod boards of reactor plant control and protection system in building ZE, elevation 0.00, room Е0336 |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1 Technical decision description |  |  |  |
| 1. Dismantle the equipment specified in Appendix to the Technical Decision (Appendix 1). 2. The equipment subject to dismantling shall be handed over to warehouse storage. |  |  |  |
| 2.2 Assessment of modifications introduced |  |  |  |
| List of equipment subject to dismantling is specified in Appendix 2 to "TECHNICAL DECISION No. CS.1.TAG.BAS.ZE.1L.0222" |  |  |  |
| 2.3 Recommendations |  |  |  |
| Perform the above-mentioned actions |  |  |  |
| 2.4 References |  |  |  |
| TECHNICAL DECISION No. CS.1.TAG.BAS.ZE.1L.0222 |  |  |  |

| SHEET OF ISSUES 4 |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue number | 2.2-4 |
|  |  | Section number | 7 |
|  |  | Page | no |
| Facility | "Bushehr-1" NPP |  |  |
| Issue title | Use of digital circuits for transmission of control and alarm commands to APCS ESFAS S&HWC of "Bushehr-1" NPP |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1 Technical decision description |  |  |  |
| The transmission of control commands for safety systems through potential signals via wire communications between the functional modules was envisaged in the design of APCS ESFAS S&HWC of "Bushehr-1" NPP. Decided: Use digital data transmission circuits (input-output busbar and fast exchange busbar) in ESFAS S&HWC (circuits 1 - 4) for transmission of control and alarm commands. Use wire communications for data transmission to adjacent complexes only. |  |  |  |
| 2.2 Assessment of modifications introduced |  |  |  |
| The analysis carried out by VNIIA has shown that transmission of commands within ESFAS S&HWC via input-output busbar (within instrumentation rack) and fast exchange busbar (between instrumentation racks) has a number of advantages as compared to the option envisaged in the design, in particular: - use of basic diagnostics function is more efficient than the diagnostics of wire communications envisaged in the design; - possibility of false activation of actuating mechanisms during a single failure is excluded; - time necessary for transmission of commands via digital circuits does not exceed the time of transmission via wire communication taking into account the delays necessary for operation of the control algorithm; - reliability properties of S&HWC are practically identical for both options of commands transmission; - operating documentation on ESFAS S&HWC is simplified; - a uniform approach to I&C-RC S&HWC and ESFAS S&HWC is implemented; - procedures for introduction of modifications to ESFAS S&HWC at NPP Site are considerably simplified. |  |  |  |
| 2.3 Recommendations |  |  |  |
| 1. FSUE "Atomenergoproekt" should reflect the present technical decision when issuing the BNPP-1 final safety analysis report. 2. FSUE VNIIA should ensure manufacture of the ESFAS S&HWC equipment (circuits 1 - 4) for BNPP APCS with account of the present technical decision. |  |  |  |

2.4 References

APCS, equipment of ESFAS S&HWC (circuits 1 - 4). Technical decision No. CS.ТАG.АSE.00.00.0653

# 2.3 Assessment of correctness of modifications due to comments made during review of the FSAR, revision 0

NNSD comments on Appendix C (to MoM to FSAR-7 (Rev. 0) dated 03-13.03.07, Tehran)

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 3 | FSAR SECTION: 7 FSAR Section 7.1 (4.4.1.3) |
| Recommendation: Table 7.1.1-1 contains classification of APCS sub-systems and MCR safety panels, but not APCS elements In particular, it is necessary to classify all elements being a part of each sub-system (primary transducers for measurement of neutron flux, temperature, pressure, level, flow rate, etc.); primary transducer rigs; penetrations; junction boxes, pulse lines, cables, local boards and panels of MCR, generalized mimic panel, etc. Notes to the Table are of no sense. The Table should be completely altered |  |
| Reply 3 | FSAR SECTION: 7 FSAR Section 7.1 (4.4.1.3) |
| Reply: Comment is accepted partially. Table 7.1.1-1 corresponds to classification, given in Chapter 3, and accepted in Appendix 1 to PSAR. Table 7.1.1-1 will be added and given as follow: Table 7.1.1-1 Name of the system; Class as per OPB (safety class); Equipment design; Note. As per OPB; As per seismic categories. 1; 2; 3; 4; 5. 1. CPS-ESFIP. - transducers*; 2NC; 2; 1. - ISPE; 2 NC; 2; 1. - NFME; 2 NC; 2; 1. -PPPE; 2 NC; 2; 1. - SLPE; 2 NC; 2; 1. - DDRH; 3 NC; 3; 2b; Performs information and service functions only. 2. CPS EE. - ECC; 2NC; 2; 1. - ShPUI PCC; 2NC; 2; 1. - ShP6MPSC6M; 2NC; 2; 1. -ShP6M1; 2NC. 3. ESFAS. - transducers *; 2 NC; 2; 1. - RCD; 2 NC; 2; 1. - PPPE; 2 NC; 2; 1. - SLPE; 2 NC; 2; 1. Table 7.1.1-1 continued - TPTS52, TPTS53; 2 NC; 2; 1. - TPTS gateway; 3 NC; 3; 1; Performs information and service functions only. 4 MCR, ECR consoles and boards with installed monitoring, control and alarm hardware; 2 NC; 2 3; 1 2b; For safety panels For normal operation panels. 3NC. 5. PP (PP1, PP2, APP3, power limitation controller); Equipment class is enhanced since it is implemented in the same cabinets as the emergency protection system. - transducers *; 3 NC; 3; 2б. - NFME; 3 NC; 2; 1. - PPPE; 3 NC; 2; 1. - SLPE; 3 NC; 2; 1. 6. MCDS***. - SHW-P; 2C; 2; 1; Сlass is enhanced, since ICND is arranged in ZK building and has an interface with SHW. - SHW - ICND; 4N; 2; 1. - SHW- IC, SHW - UL; 3N; 3; 2б. - SHW - LMS; 3N; 3; 2б. - SHW-VMS; 4N; 4; 2б. 7. SGIC, APC, ShSR; 3N; 3; 2b. 8. I&C - RC, I&C - TC,* I&C - V, I&C - AWT, I&C - TG, I&C - T, AFPS, I&C-E.. - transducers**; 3N; 3; 2a,b; For process systems important to safety. 4N; 4; 3; For individual systems Normal system. - TPTS 52, TPTS 53; 3N; 3; 2b; The equipment class is determined by fact that both functions are implemented in the same cabinets.. 4N; 3; 2b. 9. RMS; 3N; 3; 2 a,b. 10 TLS-U***; 3N; 3; 2b. 11 IOPRS; 3N; 3; 1; IOPRS is not referred to safety systems but shall be serviceable during the earthquake. * - Process systems are referred to Class 3 or 4 as per their classification and cable links ** - Term "transducer" includes instrumentation lines, installation components, containment penetrations, cable links. *** - Software corresponds to the system classification. |
| DECISION No 3 | FSAR SECTION: 7 FSAR Section 7.1 (4.4.1.3) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment was discussed and reply is accepted. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is considered in respect to classification of the elemets of the MCR subsystems and panels. Additionally, the following should be noted: - Reference to Appendix 1 of PSAR is not valid, as it does not contain classification of systems and elements. - The assigned safety class of equipment in accordance with OPB-88/97 and classification designation (in the column “equipment design” should comply with each other in items: 5. PP; 6. MCDS. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 4 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.4) |
| Recommendation: In Table 7.1.1-2, i. 5, all elements of fire alarm and fire fighting control for rooms with equipment of safety-related systems, as well as equipment itself, are referred to safety class 4 and seismic resistance category 2, which contradicts the requirements of OPB-88/97 and NPB 113-03 (NPP Fire Safety. General Requirements). OPB-88/97, i. 2.19, states that “to the elements referred to safety class 4 the requirements of general-industrial regulatory documents are imposed”, and in NPB 113-03, i.20, it is said that “fire safety requirements stated in general-industrial norms and rules can be used for NPPs being decommissioned only after fuel unloading from reactor plant core, removal of spent fuel assemblies, radioactive liquids and waste from the industrial site and after decontamination of buildings, structures and components to ultimately allowable values”. In addition, fire fighting systems both in OPB-88/97 (i.4.7) and NPB 113-03 (i.36) are referred to auxiliary safety systems. |  |
| Reply 4 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.4) |
| Reply: Comment is not accepted. Classification of fire alarm and fire fighting equipment was approved at PSAR matching. This equipment has been manufactured, accepted by the Principal, delivered and installed at the BNPP. In this connection, it is not reasonable to raise this issue at FSAR review. |  |
| DECISION No 4 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.4) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: According to Chapter 7 PSAR and design documents, fire detection equipment was referred to class 4N as per OPB 88/97. Additional discussion will be held in Moscow between VO "Safety" and ZAO ASE regarding seismic categories of AFPS and the results will be sent to NPPD/NNSD by the end of April. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 6 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.6) |
| Recommendation: Item 7.1.1 The content of the 1st paragraph on referring system elements to safety class 3 does not correspond to OPB-88/97, the paragraph textual body is arbitrary and unclear. |  |
| Reply 6 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.6) |
| Reply: Comment is accepted The text will be given as follow: "To safety class 3 the following NPP elements relate: - systems important to safety, are not included in classes 1 & 2" |  |
| DECISION No 6 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.6) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 7 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.7) |
| Recommendation: Item 7.1.1 In additional symbols of the elements classification designation it is necessary to include symbol L – localizing element, since cable penetrations within APCS are localizing elements. |  |
| Reply 7 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.7) |
| Reply: Comment is accepted The text will be added as follow: "L – localizing element of the operation" |  |
| DECISION No 7 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.7) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 8 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.8) |
| Recommendation: Item 7.1.1.1, 1 (reactor trip). It is not clear what is meant under words “reactor trip breakers”, since there is no such equipment in the reactor trip system. |  |
| Reply 8 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.8) |
| Reply: Comment is accepted The wording "reactor trip breakers" will be replaced by "breaking contactors". |  |
| DECISION No 8 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.8) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 9 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.9) |
| Recommendation: Item 7.1.1.4 The purpose of interlock for “protection against cold water slug injection” is not clear. In the following text, to which a reference is given (Section 7.6) this notion is not used |  |
| Reply 9 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.9) |
| Reply: Comment is not accepted. The wording "Cold water slug injection" is used as per Guide 1-70 item 7.6.2. |  |
| DECISION No 9 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: - The English version is corrected. - The Russian version will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 10 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.10) |
| Recommendation: Item 7.1.1.5. The CPS equipment being a part of the equipment participating in EP formation is not clearly indicated. |  |
| Reply 10 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.10) |
| Reply: Comment is accepted. The text of hyphen 4 will be added as follow: "control cabinets, power supply cabinets". |  |
| DECISION No 10 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.10) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 11 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.11) |
| Recommendation: Item 7.1.1.6.1, Fig. 7.1.1-1 - specify connection of the I&C electrical part port (the port shall be connected to Turbine Hall switchboard, but not to Normal Operation I&C System); - specify coding of the diagram elements (there is no coding of the I&C electrical part, 2 and 3-letter coding is used, coding of MCR and ECR panels is not correct); - the diagram does not contain technical support WS to be located in the MCR; - the ECR uses external WS, but not automated workstation; - presented image of automated workstations for reactor control senior engineer, turbine control senior engineer and unit shift supervisor does not give a clear representation of number of workstations being a part of automated workstations. In the description of the structural diagram it is necessary to indicate how sub-systems shall be connected to TLS-U unit network if they have no ports. |  |
| Reply 11 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.11) |
| Reply: Comment is accepted Figure 7.1.1 –1 is replaced (See the figure) |  |
| DECISION No 11 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 12 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.12) |
| Recommendation: Item 7.1.1.6.1 - in the emergency protection description there is no generation of EP signal on seismic parameters, it is either incorrectly said that the ECC takes off power from CRs. Actually, the EP actuator proper are cabinets ShP6M with breaking contactors that de-energize the CR drive mechanisms on direct and alternating current, as well as de-energization from manual control keys of MCR and ECR. - in the description of standard software-hardware tools a regulation function is missing. |  |
| Reply 12 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.12) |
| Reply: Comment is accepted. The description of emergency protection will be added: "…in industrial seismic protection equipment (ISPE) for seismic sensors.". |  |
| DECISION No 12 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.12) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 13 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.13) |
| Recommendation: Item 7.1.1.6.1 The MCDS diagnostic functions are not clearly and fully listed |  |
| Reply 13 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.13) |
| Reply: Comment is accepted. The fourth bullet will be added as follow: "and also leak control of primary circuit" |  |
| DECISION No 13 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.13) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 14 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.14) |
| Recommendation: Item 7.1.1.6.1 There are no requirements for implementation of functions on contrivance of protections, interlocks and operator commands in the IOPRS (contradicts OPB-88/97, i. 4.4.6, and PBYa RU AS-89, i. 2.4.6) |  |
| Reply 14 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.14) |
| Reply: Comment is accepted. The following will be deleted: "- man-caused accidents", "- natural disasters". |  |
| DECISION No 14 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.14) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The following text will be added to the FSAR Rev. 1: “recording of protections and interlocks, operator commands.” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 15 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.15) |
| Recommendation: Item 7.1.1.6.1 The purpose of electrical part I&C is absolutely unclear from the description |  |
| Reply 15 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.15) |
| Reply: Comment is accepted. The following will be added: "and also automatics and information representation" |  |
| DECISION No 15 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.15) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 16 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.16) |
| Recommendation: Item 7.1.1.6.2 - control of the power unit is not only control within man-machine interface framework, for example, control from safety panels; - the power unit is not controlled from the LCC, only WS being a subscriber of Power Unit LAN is located in the LCC. |  |
| Reply 16 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.16) |
| Reply: Comment is accepted. From item 7.1.1.6.2 the following will be deleted: " - Local Crisis Centre (LCC)". |  |
| DECISION No 16 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.16) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted and the following text will be introduced in the FSAR Rev. 1: “LCC is provided for NPP monitoring.” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 18 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.18) |
| Recommendation: Item 7.1.1.6.2 Description of the ECR is incorrect and does not contain necessary information: - the ECR has a different design from that of MCR safety panels; - there are significant differences in CPS panels of the MCR and ECR; - the ECR provides for external WS, but not an automated workstation; - it is necessary to indicate which software is to be installed on the ECR WS to ensure access to all operational systems |  |
| Reply 18 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.18) |
| Reply: Comment is accepted. The design of the ECR panels is similar to the MCR panels. The last para of item 7.1.1.6.2 will be added by the following: "… Reactor and Turbine buildings". |  |
| DECISION No 18 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.18) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: See reply 169. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 20 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.21) |
| Recommendation: Page 24, item 5 An incorrect statement that the magneto-optic memory is used for record of speech messages of the operational personnel. This memory is used for arrangement of a long-term archive of APCS information at the level of Power Unit |  |
| Reply 20 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.21) |
| Reply: Comment is not accepted. See the text of para 5. |  |
| DECISION No 20 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.21) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: - The English version is correct. - The Russian version will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 22 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.23) |
| Recommendation: Page 26, item 12 - inconsistency with GOST R 50746-2000. Design group TS for safety class 2 for noise resistance shall be IV, function quality criteria – A. - delete Table 7.1.1.3 as it contains a requirement for noise resistance for noise of one type only. There shall be a reference to the a.m. GOST |  |
| Reply 22 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.23) |
| Reply: Comment is accepted. In the text the following will be indicated: "TPTS passed the tests on noise resistance as per category IV, function quality criteria – A." The mentioned Table in page 25 will be deleted |  |
| DECISION No 22 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.23) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 23 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.24) |
| Recommendation: Item 7.1.1.6.4 This item contains a lot of excessive information on TPTS not related to safety substantiation (description of busbar lines, list of service modules, etc.). At the same time there is nothing said about software, substantiation of its application in SHC of safety class 2. Safety related information on TPTS would be reasonable in Section 7.3 |  |
| Reply 23 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.24) |
| Reply: Comment is not accepted. In Note to Table 7.1.1-1 the following is indicated: "Software (SW) corresponds to subsystem classification". By the technical solution CS.TAG.ASE.00.00.0653 the respective SW was accepted for application at TPTS means for Engineered safety feature actuation system (ESFAS) functions. |  |
| DECISION No 23 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.24) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The conclusions from the VNIIA Technical Report on TPTS verification will be added in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 24 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.25) |
| Recommendation: Item 7.1.1.7 The thesis "APCS is designed on the basis of hardware examined at industrial enterprises to a certain degree" is very general for reference substantiation. From presented reference substantiation it is impossible to understand an existing situation with reference of system decisions, software, engineered tools. The table should also contain information on references for the main subsystems such as ARMS, TLS-U, PSCS, RCU, and MCR/ECR hardware. Besides, there should be information on testing of the software/hardware on the APCS test site. |  |
| Reply 24 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.25) |
| Reply: Comment is accepted Table 7.1.1-7 will be added as follow: Table 7.1.1-7 Hardware; Identification designation as per OPB-88/97; Reference. CDS; SHW IC; 3N; Available within the framework of operating ICIS. Upper unit SHW (Local computer network included); 3N; Аvailable. SHW SVM; 4N; Аvailable. SHW SLM; 3N; Аvailable. SHW LPMS; 4N; No available. MSR/ECR; Consoles Boards; 2NC, 3NC; Available. RCD; RCD01,02,03; 2NC; Available. |
| DECISION No 24 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.25) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 27 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.28) |
| Recommendation: Item 7.1.2, page 7-39 The presented regulatory basis lacks the following regulatory documents: - Russian standards for software; - Russian standards for radiation monitoring; - methodical instructions MU 7.4-01; - IEC standards: 60964; 60965; 60960; 61771. |  |
| Reply 27 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.28) |
| Reply: Comment is accepted Item 7.1.2 will be added by IEC standards: 964, 965, 960, 1771 |  |
| DECISION No 27 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.28) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: MU 7.4-01 will be added in the reply and will be included in FSAR Rev 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 29 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.30) |
| Recommendation: Item 7.1.2.4 (SC4) Transfer the text "Operating condition for APCS software” from the analytical part of the Section to the descriptive part, which would correspond to its purpose |  |
| Reply 29 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.30) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 29 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.30) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 30 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.31) |
| Recommendation: Item 7.1.2.7 (SC7) Incorrect use of notion “the isolating devices” in this context. Probably, “routing devices” should be used |  |
| Reply 30 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.31) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 30 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.31) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 31 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.32) |
| Recommendation: Item 7.1.2.7 (SC7) The purpose of the text after the second paragraph is not clear with regard to SC7 |  |
| Reply 31 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.32) |
| Reply: Comment is not accepted. Both wordings may be accepted. |  |
| DECISION No 31 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.32) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 32 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.33) |
| Recommendation: Item 7.1.2.9 (SC9): - inaccurate title of the Section; - FSAR shall contain description of specific methods selected in the design, but not reasoning about potential method |  |
| Reply 32 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.33) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 32 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.33) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 33 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.34) |
| Recommendation: Item 7.1.2.10 (SC10) After the word “signal” it is necessary to insert specifying “EP and Process Safety Control Systems”, otherwise it is not clear which systems are under consideration |  |
| Reply 33 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.34) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 33 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.34) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 34 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.35) |
| Recommendation: Item 7.1.2.11 (SC11) It is unclear why the note in this item is needed with regard to channels of Process Safety Control Systems. |  |
| Reply 34 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.35) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 34 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.35) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 35 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.36) |
| Recommendation: Item 7.1.2.12 (SC12) The second sentence of this item should end with the words “in accordance with this criterion”, otherwise it is unclear what is meant |  |
| Reply 35 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.36) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard |  |
| DECISION No 35 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.36) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 36 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.37) |
| Recommendation: Item 7.1.2.13 (SC13) Incorrect title for SC13. It is necessary to delete “Completion of protective action, if begun”. |  |
| Reply 36 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.37) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 36 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.37) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 37 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.38) |
| Recommendation: Item 7.1.2.13 (SC13) It is necessary to accurately call the room when bypass indication is displayed |  |
| Reply 37 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.38) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard |  |
| DECISION No 37 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.38) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 38 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.39) |
| Recommendation: Item 7.1.2.15 (SC15) Initially the content of criterion SC15 is incorrectly worded. It should be worded as “multiple settings”, but not “multiple assigned conditions”. Due to this the text of the present item should be modified |  |
| Reply 38 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.39) |
| Reply: Comment is not accepted. The text given in Chapters 7.1 of PSAR & FSAR corresponds completely to IEEE-279 Standard. |  |
| DECISION No 38 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.39) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 39 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.40) |
| Recommendation: Item 7.1.2.17 (SC17) The text of the first sentence is technically incorrect using such notions as “reactor startup”, “fuel insertion into the core”. Probably they should be “reactor startup”, “CR insertion into reactor core” (comment on the Russian version only) |  |
| Reply 39 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.40) |
| Reply: Comment is accepted The text in brackets will be given as follow: "(reactor trip, containment isolation, boron injection into reactor core, etc.)". |  |
| DECISION No 39 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.40) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 40 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.41) |
| Recommendation: Item 7.1.2.17 (SC18) This item deals with access to equipment, not retreating from it (comment on the Russian version only) |  |
| Reply 40 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.41) |
| Reply: Comment is accepted The text will be given as follow: "…administrative control of access …". |  |
| DECISION No 40 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.41) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 41 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.42) |
| Recommendation: There is no table with the list of software to be used in sub-systems with classification by safety. At that, specialized codes of SSHC functional modules with envisaged restricting measures on their change in the course of operation can be conditionally referred to the software. It is necessary to present the list of software to be procured. It is also necessary to describe the software verification and validation processes |  |
| Reply 41 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.42) |
| Reply: Comment is not accepted. In Note to Table 7.1.1-1 the following is indicated: "Software (SW) corresponds to sub-system classification". By the technical solution CS.TAG.ASE.00.00.0653 the respective SW was accepted for application at TPTS means for Engineered safety feature actuation system (ESFAS) functions |  |
| DECISION No 41 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.42) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The conclusions from the VNIIA Technical Report on TPTS verification will be added in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 45 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.46) |
| Recommendation: There is no description of system of universal time needed for process and investigation into accidents |  |
| Reply 45 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.46) |
| Reply: Item 7.1.1.9.5 should be added by the following: The special server connected to astronomical clock, having the satellite aerial is the universal time source in the I&C. All sluice computers are connected to a synchronizing server through local common station network, cooperating on NTP protocol. Interaction is performed by an exchange of timing sendings and an estimation of a divergence of hours with use of a statistical filtration. Accuracy of time synchronization in sluice computers is ± 5 ms. Time correction in sluice computers is made with the specified periodicity. The server independently from each other synchronizes each sluice computer. Sluice computers intended for TPTS synchronization, periodically send synchronizing telegrams through the system trunk. Synchronizing telegrams are transmitted in a broadcasting mode simultaneously to all TPTS racks, connected with sluice computer through TPTS system trunk. Synchronizing telegrams are sent with the set periodicity (each 16 s). Thus, the accuracy of hour’s synchronization in control modules of TPTS 53.1332 interfaces is ± 5 ms. Cyclic character of collecting and processing of entering signals in functional modules of SHW I&C NOS (on TPTS base) results in an error of a time label assignment to events in TPTS 53.1332. This error is actually equal to a cycle time of the functional module and makes for the discrete signals the time from 10 ms up to 130 ms at acyclic signals transmitting. At registration of the sequence of events (discrete signals) the assignment of different time labels is guaranteed, allowing to establish the sequence of events, if time between them is not more than 130 ms |  |
| DECISION No 45 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.46) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 47 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.48) |
| Recommendation: There are no integral reliability parameters: - average parameter of EP actuation flow due to APCS failures; - probability of safety functions non-fulfilment due to CSS failures to be determined at the interval of 1 year and maintenance (testing) for 720 hours for protective and isolating functions. At that, references to respective calculations confirming fulfilment of these parameters should be given. Confirmation of calculation data is assured by collection of Power Unit operation parameters starting from the second year of operation. |  |
| Reply 47 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.48) |
| Reply: The reply to the given comment is presented in Reply 2.11 of PSAR Supplement No.1. Item 7.2.1.6 FSAR shall be supplemented with the following text: "On the basis of calculations given in PSA (18.BU.1 0.0.00.VAB.PR) probability of failure of EP electric part to actuate by demand is 6,7х10-8. On the basis of calculations given in PSA (18.BU.1 0.0.00.VAB.PR) the maximum value of probability of failure within one safety channel is less than, than 1х10-4 per one demand". The calculations were performed on the basis of statistical data on reliability of accessories, obtained by the results of tests and operation experience |  |
| DECISION No 47 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.48) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 48 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.49) |
| Recommendation: There are no numerical parameters for: - time for EP signal generation (from signal generation by a sensor till de-energization of CR drive mechanisms); - time for actuation CSS if a respective requirement occurs; - time for passage of process operator’s commends from WS to actuator; - time for passage of signals from sensors till display at process operator’s WS. (inconsistency with OPB-88/97, items 4.4.4, 4.4.5, 4.4.6) |  |
| Reply 48 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.49) |
| Reply: Comment is not accepted. We consider that clarification of this data at present is prematurely. At commissioning the special tests on time for passage of signals are planned, following which they will be introduced in FSAR |  |
| DECISION No 48 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.49) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Data from TA will be added to the text in FSAR Rev 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 49 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.50) |
| Recommendation: Table 7.1.1-1: - specify the document based on which the seismic classification is done; - safety class as per OPB-88/97 is 3NU not 2NU. |  |
| Reply 49 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.50) |
| Reply: See item 4.4.1.3 |  |
| DECISION No 49 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.50) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is taken into account in respect to systems elements classification. Additional comments correspond to the comments to Issue No. 3 (see page 20). |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 50 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.51) |
| Recommendation: Item 7.1.1.5 For accelerated preventive protection only one group of CRs is used |  |
| Reply 50 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.51) |
| Reply: Comment is accepted Text in item 7.1.1.5 will be replaced by "dropping of one group of CRs " |  |
| DECISION No 50 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.51) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 52 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.53) |
| Recommendation: Page 7-24 The expression "lowering of all CPS CR to the end-pieces of the core bottom" is not correct |  |
| Reply 52 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.53) |
| Reply: Comment is not accepted. Comment is not clear. It requires additional explanation |  |
| DECISION No 52 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.53) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The wording will be changed as follows: “bottom limit switches” and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 53 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.54) |
| Recommendation: Item 4 Incorrect wording of the 1st sentence. |  |
| Reply 53 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.54) |
| Reply: Comment is not accepted. Comment is not clear. It requires additional explanation |  |
| DECISION No 53 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.54) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The 1st sentence will be as follows: “SHC of the TLS-U includes:”. It will be corrected in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 55 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.56) |
| Recommendation: Item 12 The code of GOST R 50746-2000 is incorrect |  |
| Reply 55 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.56) |
| Reply Comment is accepted The text will be corrected by "GOST R 50746-2000" |  |
| DECISION No 55 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.56) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. The require correction will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 57 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.58) |
| Recommendation: Item 7.12.4, operation conditions of APCS hardware The protection degree of engineered tools is incorrect, it should be IP (20, 54, 65) not 1P (20, 54, 65) |  |
| Reply 57 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.58) |
| Reply: Comment is not accepted. The text is correct |  |
| DECISION No 57 | FSAR SECTION: 7 FSAR Section 7.1. (4.4.1.58) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 58 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.1) |
| Recommendation: Classification by safety (Table 7.2-1) is to be separately for initiating and actuating parts, since the initiating part is classified as 2NU, and actuating part – 2U |  |
| Reply 58 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.1) |
| Reply: The comment is accepted. Classification designation in Table 7.2-1 will be given separately for initiating (2NC) and actuating (2C) parts |  |
| DECISION No 58 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.1) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 60 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.3) |
| Recommendation: The arrangement of sensors in Table 7.2-3 should be more accurate depending on their purpose |  |
| Reply 60 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.3) |
| Reply: We consider that Table 7.2-3 gives a representation on arrangement and the number of neutron sensors over channels in the concrete cavity. Detailed description of the range of measurement and purpose of t h e neutron sensors is presented further on in the text in the section of NFME. |  |
| DECISION No 60 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.3) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: A clarification text will be added in the NFME section in the Rev. 1 of FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 61 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.4) |
| Recommendation: Item 7.2.1.5 (basic principles) It is necessary not just to declare independence of instrumentation channels, but to word independence principles according to which the channels can be considered independent. For example, such principles can be as follows: - individual pulse lines; - individual sensors; - separation of signals by different cables; - separate routes for cables laying; - special grounding; - power supply; - physical separation of equipment; - absence of links between channels; - possibility of one channel bringing out for testing; - galvanic separation inside EP set with the equipment not participating in generation of emergency protection signal. |  |
| Reply 61 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.4) |
| Reply: Item 7.2.1.5 will be given in the following wording: “The basic principle of monitoring the process parameters, used in the emergency protection system, is a principle of independence of the protection system instrumentation channels. Independence of the instrumentation channels inside a set is assured by: - individual sensors for each channel; - individual cable communication lines; - special grounding; - separate power feeders; - separation of signals by different cables; - power supply; - absence of links between instrumentation channels; - possibility of one channel bringing out for testing; - galvanic separation inside EP set with the equipment not participating in generation of emergency protection signal” |  |
| DECISION No 61 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.4) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 62 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.5) |
| Recommendation: The scheme of temperature measurement (fig. 7.2-2) carries little information. A detailed scheme should be given as follows: "TTT – CDC TTT – penetration – converting device – processing device – comparison with set point – coincidence – alarm – control," and it should be shown that the requirements to error values are satisfied under all operating conditions |  |
| Reply 62 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.5) |
| Reply: The scheme given in Figure 7.2-2 (as well as in Figures 7.2-3, 7.2-4, 7.2-5) is the enlarged scheme. The scheme of signal processing in ECPS is given in Figure 7.2-14. No presentation of more detailed information in Section 7.2 FSAR is required according to RG 1.70 |  |
| DECISION No 62 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.5) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Additional materials will be provided during the commissioning license stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. The results of pre-commissioning activities are not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 63 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.6) |
| Recommendation: Fig. 7.2-3, 7.2-4 Same as the previous comment |  |
| Reply 63 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.6) |
| Reply: The scheme given in Figure 7.2-2 (as well as in Figures 7.2-3, 7.2-4, 7.2-5) is the enlarged scheme. The scheme of signal processing in ECPS is given in Figure 7.2-14. No presentation of more detailed information in Section 7.2 FSAR is required according to RG 1.70 |  |
| DECISION No 63 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.6) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Additional materials will be provided during the commissioning license stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. The results of pre-commissioning activities are not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 66 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.9) |
| Recommendation: Page 7-60 Main decisions on coolant level in reactor monitoring equipment are mentioned in the FSAR, but they are not described anywhere (safety class, seismic resistance category, resistance to external effecting factors, arrangement, external interfaces, etc.) |  |
| Reply 66 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.9) |
| Reply: Description of the emergency level gauge for the reactor coolant is given in Section 7.5 FSAR |  |
| DECISION No 66 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The text of section 7.5 will be expanded in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 67 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.10) |
| Recommendation: Bring in conformity Tables 7.2-5, 7.2-6, 7.2-7, 7.2-8 between each other as for the following parameters: - neutron flux change period; - minimal critical heat flux ratio; - linear energy release |  |
| Reply 67 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.10) |
| Reply: The mentioned missing parameters will be included into Tables 7.2-5, 7.2-6, 7.2-7 and 7.2-8 |  |
| DECISION No 67 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.10) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 68 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.11) |
| Recommendation: It is not clear why Table 7.2-6 lacks in-core monitoring sensors on parameters of neutron flux change period and minimal critical heat flux ratio |  |
| Reply 68 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.11) |
| Reply: The neutron flux change period is determined by calculation in NFME as per the data obtained from the neutron sensors arranged in IC channels of the rector concrete cavity. The second part of the comment is accepted. Table 7.2-6 will be supplemented with the data on NTMC in-core instrumentation sensors |  |
| DECISION No 68 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 70 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.13) |
| Recommendation: Table 7.2-8 There should be a commentary made to the table to explain the impact of inertial property on the error of protection actuation on monitored parameters |  |
| Reply 70 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.13) |
| Reply: The following commentary will be made to Table 7.2-8: “Sluggishness of the instrumentation channel is considered in performing the safety analysis” |  |
| DECISION No 70 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.13) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 71 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.14) |
| Recommendation: Fig. 7.2-12 - connection of neutronic and process parameter sensors to NFME, SHC-3, EPPS and signal logic processing equipment is incorrectly shown; - outputs of adjacent channels of one EP set are not shown from SHC-3 to signal logic processing equipment |  |
| Reply 71 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.14) |
| Reply: Figure 7.2-12 will be corrected |  |
| DECISION No 71 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.14) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 72 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.15) |
| Recommendation: Page 7-67, last paragraph but one The MCR has no operating display of NFME, therefore it is not clear how change of settings is controlled |  |
| Reply 72 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.15) |
| Reply: The NFME information is represented on the displays of TLS-U. The text will be corrected according to the comment |  |
| DECISION No 72 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.15) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 73 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.16) |
| Recommendation: The schemes in fig. 7.2-12, 7.2-13, 7.2-14 do not reflect the concrete approaches to transmittal of EP signals from the equipment of the initiating part to the actuating one. Therefore it is necessary to provide a diagram (functional and/or schematic) of signal generation and transmittal from the signal logic processing equipment (separately for EP, preventive protections and accelerated preventive protections) by channel and by set (indicating their location) and their path through all cabinets of the actuating part of EP (preventive protections and accelerated preventive protections), including that for power supply |  |
| Reply 73 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.16) |
| Reply: A set of Figures 7.2-12, 7.2-13 and 7.2-14 presents a sufficient scope of the information for understanding of interaction of the reactor shutdown system main components. Presentation of the more detailed information in 7.2 FSAR is not required according to RG 1.70 |  |
| DECISION No 73 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.16) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Fig. 7.2-12 (English version) will be corrected and included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 74 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.17) |
| Recommendation: Page 7-77 When describing schemes of trip signals generation it is necessary to indicate action of signals of EP, accelerated preventive protection, PP-1, PP-2 (tripped/not tripped) after signal of initial cause is cancelled |  |
| Reply 74 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.17) |
| Reply: The following sentence will be added into item 7.2.13: “Action of the reactor emergency protection in response to the trip command is brought to an end irrespective of presence of the signal of initial cause. Description of action of APP, PP-1, PP-2 under removal of the signal of initial cause is presented in ii 7.7.1.2.1 FSAR |  |
| DECISION No 74 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.17) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 75 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.18) |
| Recommendation: Page 7-69, last paragraph Contents of the paragraph shall be specified (where the signal is generated, which is to be transmitted to the turbine control system, and how it is being transmitted) |  |
| Reply 75 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.18) |
| Reply: Content of the paragraph will be supplemented with the information on the fact that the signal for turbine trip is transmitted from ECC (emergency command cabinets) through the galvanically decoupled communication lines |  |
| DECISION No 75 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.18) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 77a | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.21) |
| Recommendation: The following is missing in the description of the in-core instrumentation system SHC-3: - data on software to be used for generation of emergency signals on local parameters, including fulfillment of requirements of IEC 60880; - information on bringing out for testing of channels of emergency signals generation on local parameters; - description of the in-core instrumentation system function in case of failure/maintenance of one channel of one set and one set (for example, due to loss of a channel); algorithm of function program of a SHC-3 channel (considering all exchangers) and calculation formula |  |
| Reply 77a | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.21) |
| Reply: The description of SHC-3 will include the following information: "The software of in-core instrumentation system SHC-3 was elaborated in accordance with recommendations of IEC-60880 using the approved translator of the computer-oriented language Assembler for single-chip micro-controllers Intel MCS-51. The software debugging on target boards was performed with the use of in-circuit emulator Project-51 of Phyton firm. The following was carried out: - check of codes for compliance with the requirements for their elaboration (compliance with the requirements of TA); - software testing; - software testing with its operation as a part of the equipment during equipment tests at the Manufacture; - check of the SHC-3 software functioning as a part of ICIS during preliminary independent tests of ICIS on the Manufacture site and I&C testing ground for Bushehr NPP; - check of software with its operation as a part of the equipment during independent tests of ICIS and during integration tests of MCDS and it is performed during putting into operation at NPP". Bringing of SHC-3 to the mode of testing is performed simultaneously with testing of the whole set of EP. Testing is carried out in turn with check of signal passage of each SHC-3 channel to SLPE boxes. Functioning of SHC-3 in case of malfunction/maintenance is described in Chapter 7.7 of FSAR (item 7.7.1.4.3.6) to which the reference will be given in this section. RG 1.70 has no requirement of presenting this information in Chapter 7.2. |  |
| DECISION No 77a | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.21) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 77b | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.22) |
| Recommendation: Page 7-82. For case of failure of one of SHC-3 sets it is necessary to indicate the value of increased error for determination of design parameters and in the in core instrumentation system computational center and evaluate from the view point of trustworthiness of protection signals to be generated on in-core local parameters |  |
| Reply 77b | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.22) |
| Reply: With failure of one set of SHC-3 the ICIS provides a generation of reactor core protection signals by in-core local parameters with the help of the second set of SHC-3 and in this case a high mistake from the viewpoint of protection signals validity doesn’t occur. The error of calculated parameters in CC UL will not exceed the permissible design value |  |
| DECISION No 77b | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.22) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed and introduced in the FSAR Revision 1: Since during failure of one SHC-P set, the remaining SHC-P set is working with old adjustment coefficients, the error of local parameters calculation in it will not change. Additional information on the changes of the local parameters calculation error in case of one SHC-P failure will be provided in response to additional request from FTO Safety |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 78 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.23) |
| Recommendation: Page 7-84 Indicate the time for actuation of EP actuating part for the following 2 cases: - on receipt of EP signals from signal logic processing equipment; - on initiation of EP signal from MCR, ECR |  |
| Reply 78 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.23) |
| Reply: The time for actuation will be given. 0,3s – from EP initiating part; 0,2s – from EP buttons in MCR, ECR |  |
| DECISION No 78 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.23) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 79 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.24) |
| Recommendation: Item 7.2.1.7 (reference) The design of WWER-640 has not been implemented up to now; therefore the reference to it is incorrect. Substantiation of reference of NFME, EPPS, signal logic processing equipment is cursory, since the word “prototype” does not say anything about actual difference or similarity of earlier used tools with the equipment to be used for the Bushehr NPP power unit |  |
| Reply 79 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.24) |
| Reply: The reference to the design of WWER-640 will be deleted and replaced with the following wording: “…similar NFME, PPPE, SLPE operated at Unit 3 of Kalinin NPP” |  |
| DECISION No 79 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.24) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 80 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.25) |
| Recommendation: Item 7.2.1.8 (arrangement of reactor trip system equipment) According to Table 7.2-10 the cabinets of EP actuating part ShPU, ShP6M, ShP6M1 (safety class 2U) of both sets of the reactor trip system are arranged in the rooms with normal operation equipment (inconsistency with PBYa RU AS-89, item 2.3.2.14) |  |
| Reply 80 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.25) |
| Reply: The sets of the EP actuating part are located in different parts of RCIS room and at a sufficient distance from one another. They cannot suffer the common cause failure, i.e. the requirement of i. 2.3.2.14 PBYa RU AS-89 is met |  |
| DECISION No 80 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.25) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. - Normal operation equipment arranged in this room is designed for MDE by its mechanical strength. - The rooms are separated with fire-proof doors |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 81 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.26) |
| Recommendation: Item 7.2.1.9 (check of the system): - indicate which tools display malfunctions of primary transducers and communication lines; - phrase “continuous in-service observation for the state of units and devices…” is of no technical sense; - if testing and check means the same, then it is necessary to use a single term. If these processes are different, then it is necessary to describe their differences. This item should be supplemented with a system check diagram; this would allow clear understanding completeness of the system check as a whole using individual stages and areas of overlapping of individual checks |  |
| Reply 81 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.26) |
| Reply: 1. In case the difference in sensor readings is more than 2Δосн (where Δосн is the base measuring error) the indications appear on panels 30LBT11 and 30LBT12 in MCR. 2. The term “continuous in-service observation” should be understood as the equipment examination once a shift. 3. The term “testing” will be deleted. 4. The presented description of checks is sufficient for the given FSAR Section. Presentation of more detailed information is not required according to RG 1.70 |  |
| DECISION No 81 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.26) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The text of the FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 82 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.27) |
| Recommendation: Page 7-88 (power supply) The power supply schemes to which the reference is given in this item are missing from Section 7.1 |  |
| Reply 82 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.27) |
| Reply: The last sentence in the description of electric power supply will be given in the following wording: “Detailed power supply schemes for the reactor trip system are presented in Chapter 8 FSAR and Appendix C Book 3 of Chapter 7 FSAR” |  |
| DECISION No 82 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.27) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The text of the FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 83 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.28) |
| Recommendation: Page 7-88 (climatic conditions) Specify the values of all indicators (see supplement to PSAR). Indicate which types of the system tools are used inside the containment |  |
| Reply 83 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.28) |
| Reply: The comment is accepted. The necessary changes will be made |  |
| DECISION No 83 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.28) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 84 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.29) |
| Recommendation: Page 7-100 After the paragraph "Requirements for seismic stability," specify that all tolls have passed qualification tests (including seismic stability, electromagnetic compatibility, climatic testing, etc.) and are able to perform the required functions under all designed modes and under all external factors at all stages of the lifecycle |  |
| Reply 84 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.29)) |
| Reply: The comment is accepted. The necessary changes will be made |  |
| DECISION No 84 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.29) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 85 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.30) |
| Recommendation: Page 7-100 (reliability indices, actuation time) The actuation time is missing from the mentioned item. |  |
| Reply 85 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.30) |
| Reply: The comment is accepted. The actuation time (0,3 s) will be given |  |
| DECISION No 85 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.30) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 86 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.31) |
| Recommendation: Item 7.2.2.2 This wording does not mean that the reactor shutdown system provides the diversity criteria (see the IAEA comments) |  |
| Reply 86 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.31) |
| Reply: The diversity in the reactor emergency shutdown system hardware is not provided in the design and not required according to the NTD of RF and Iran. According to PBYa RU AS-89 two systems of the reactor shutdown are realized constructed by different actuation principles (see i. 2.3.1.4 of PBYa RU AS-89) |  |
| DECISION No 86 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.31) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In the FSAR Rev. 1, the text will be completed with information from item 7.2.1.6 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 88 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.33) |
| Recommendation: Item 7.2.2.4 This item declared review of two safety criteria SC3 and SC4, however only safety criterion SC3 was reviewed. There is no SC4 (equipment qualification assessment). (Inconsistency with NUREG-0800) |  |
| Reply 88 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.33) |
| Reply: The text will be supplemented with the following: “Equipment was subjected to qualification tests for mechanical, seismic, climatic impacts and electromagnetic compatibility, and meets the requirements stated for the equipment of class 2” |  |
| DECISION No 88 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.33) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 90 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.35) |
| Recommendation: Item 7.2.2.8 It is necessary to introduce supplement in this item “Exceptions are critical heat flux ratio and linear energy release, which are calculated by indices of in-core instrumentation sensors” |  |
| Reply 90 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.35) |
| Reply: The indicated text will be included into FSAR |  |
| DECISION No 90 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.35) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 91 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.36) |
| Recommendation: Item 7.2.2.11 At the FSAR stage there should already be exact instructions, which information an operator receives on condition of bypasses and in which form, or it is necessary to give respective clarifications, if there is no need for this. OKP21 has nothing to do with this item |  |
| Reply 91 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.36) |
| Reply The text of i.7.2.2.11 will be supplemented with the following sentence: “Information on condition of bypasses (values of process parameters) is represented on the displays of TLS-U and indicating instruments on the MCR panel” |  |
| DECISION No 91 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.36) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 92 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.37) |
| Recommendation: Item 7.2.2.12 SC18 (access to setting set-points) is not considered, though it was declared. OKP21 has nothing to do with this item |  |
| Reply 92 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.37) |
| Reply: The first part of the comment – the second sentence will be given as follows: “Administrative, managerial and technical measures provide for authorization of the access to setting set-points”. The second part of the comment – the comment is accepted, OKP 21 will be deleted from the given item |  |
| DECISION No 92 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.37) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 93 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.38) |
| Recommendation: Item 7.2.2.13 OKP21 has nothing to do with this item |  |
| Reply 93 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.38) |
| Reply: OKP21 will be deleted from the given item |  |
| DECISION No 93 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.38) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 94 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.39) |
| Recommendation: Item 7.2.2.15 OKP15 “General designing criteria applicable to Chapter 7” is missing from Table 7.1.2-1. |  |
| Reply 94 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.39) |
| Reply: ОКП15 will be deleted from the given item |  |
| DECISION No 94 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.39) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 95 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.40) |
| Recommendation: Item 7.2.2.16 It is necessary to specifically indicate which display tools are used for information representation, but not about actuation of the set breakers |  |
| Reply 95 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.40) |
| Reply: The following will be included into the text: “… on information panels of MCR and ECR…” |  |
| DECISION No 95 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.40) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 96 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.41) |
| Recommendation: Item 7.2.2.17 The reference to the previous item is incorrect |  |
| Reply 96 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.41) |
| Reply: The last sentence will be given as follows” “In the preceding item the data are given on the presentation of information on the initial cause of actuation” |  |
| DECISION No 96 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.41) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 97 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.42) |
| Recommendation: Item 7.2.2.19 OKP21 has nothing to do with this item |  |
| Reply 97 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.42) |
| Reply: OKP21 will be deleted from the given item |  |
| DECISION No 97 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.42) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 98 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.43) |
| Recommendation: Provide diagrams of power supply of the equipment of the channels and EP sets |  |
| Reply 98 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.43) |
| Reply: The last sentence in the description of electric power supply will be given in the following wording: “Detailed power supply schemes for the reactor trip system are presented in Chapter 8 FSAR and Appendix C Book 3 of Chapter 7 FSAR” |  |
| DECISION No 98 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.43) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be completed according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 100 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.45) |
| Recommendation: It is necessary to delete words “shall be” from item 7.2.1.3 (the last paragraph) |  |
| Reply 100 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.45) |
| Reply: The comment is accepted. The mentioned words will be deleted |  |
| DECISION No 100 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.45) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 101 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.46) |
| Recommendation: In Table 7.2-2, the omission in line “Corresponding section of FSAR chapters” is not clear for initiating events “Decrease of network frequency below 46 Hz”, “seismic effect” |  |
| Reply 101 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.46) |
| Reply: The comment is accepted. During revision in Table 7.2-2 instead of omissions the reference will be indicated to Chapter 15 FSAR and Chapter 3 FSAR, respectively |  |
| DECISION No 101 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.46) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 102 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.47) |
| Recommendation: In Table 7.2-2, for criterion “Excessive pressure in containment more than 0.029 MPa” the initiating event is not indicated |  |
| Reply 102 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.47) |
| Reply: The comment is accepted. For the criterion “Excessive pressure in containment more than 0.029 MPa” the initiating events will be indicated: “SB LOCA (break of pipeline Dnom less than 100), LB LOCA (break of pipeline Dnom more than 100), spectrum of steamline break inside and outside the containment” |  |
| DECISION No 102 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.47) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 103 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.48) |
| Recommendation: Page.7-59, the 2nd paragraph from below It is not clear which system cable rooms are in question where conversion devices are arranged |  |
| Reply 103 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.48) |
| Reply: The comment is accepted. The conversion devices are arranged in the inter-envelope space in building ZB |  |
| DECISION No 103 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.48) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 104 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.49) |
| Recommendation: Clarify Table 7.2-4 The purpose of the table continued is unclear (page 7-54) except two last lines |  |
| Reply 104 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.49) |
| Reply: In the Table continuation the list is presented for the thermal converters related to SHC-3, included into the set of MCDS. In the Table continuation the MCDS will replaced with SHC-3 |  |
| DECISION No 104 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.49) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 105 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.50) |
| Recommendation: Page 7-74, last bullet Information being recorded in protection set rooms shall be transmitted to TLS-U for storage in common-plant archive, but not for representation to the operators, since it is not operative anymore |  |
| Reply 105 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.50) |
| Reply: The information recorded in the system rooms is: - transmitted to TLS-U for representation and archiving; - archived in the rooms of sets |  |
| DECISION No 105 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.50) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 107 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.52) |
| Recommendation: Table 7.2-9 The table does not present algorithms, but actually lists of signals and logics of emergency protection generation |  |
| Reply 107 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.52) |
| Reply: The given presentation of the algorithms in the form of formalized logic structure gives a visual presentation of the emergency protection actuation logic and was agreed earlier in РSAR |  |
| DECISION No 107 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.52) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The following text will be added in the reply: “ Algorithms are provided in Appendix D to Chapter 7 of the FSAR Rev. 1” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 108 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.53) |
| Recommendation: Page 7-78, DPE, 1st paragraph It is not clear what the last sentence of the paragraph has to do with the above text |  |
| Reply 108 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.53) |
| Reply: The first sentence of the first paragraph describes the task of data collection on the parameters monitored. The second sentence describes the second task – data collection on equipment diagnostics |  |
| DECISION No 108 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.53) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 109 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.54) |
| Recommendation: Page 7-87, In-Core Instrumentation System SHC-3 The second paragraph deals with reference and shall be placed in the respective Section |  |
| Reply 109 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.54) |
| Reply: The second paragraph will be transferred into i. 7.2.1.7 |  |
| DECISION No 109 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.54) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 109a | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.55) |
| Recommendation: When describing the SHC-3 of the in-core instrumentation system the signals being generated for transmission of the signal logic processing equipment are called relay signals (page 7-87), binary signals (page 7-88), discrete signals (7-90). The same name for same signals shall be used |  |
| Reply 109a | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.55) |
| Reply: The comment is accepted. The text will be revised |  |
| DECISION No 109a | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.55) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 110 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.56) |
| Recommendation: Item 7.2.2.2 In the Russian text the safety class shall be designated as 2U not 2S |  |
| Reply 110 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.56) |
| Reply: The comment is accepted. In Russian text the safety class will be designated as 2U |  |
| DECISION No 110 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.56) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text of FSAR Rev.1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 111 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.57) |
| Recommendation: Item 7.2.1.9 (check of the system) The text on APCS maintenance shall be deleted, since the reactor trip system is in question here |  |
| Reply 111 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.57) |
| Reply: The term APCS in item 7.2.1.9 will be replaced with the word “systems” |  |
| DECISION No 111 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.57) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian text of FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 112 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.58) |
| Recommendation: Page 7-97 (initiating events of accidents) There is no list of algorithms in Table 7.2-2 to which the reference is given |  |
| Reply 112 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.58) |
| Reply: The last sentence in the paragraph will be as follows: "The list of accident initiating events and the corresponding actuation conditions is presented in Table 7.2-2" |  |
| DECISION No 112 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.58) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 113 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.1) |
| Recommendation: Item 7.3.1.2.1: - group the listed systems in 3 groups – separately protective, isolating and auxiliary systems; - clarify the relation of the fuel storage and transport system (the last bullet) to the systems started from the MCR |  |
| Reply 113 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.1) |
| Reply: The comment is accepted partially. - Classification of the systems, given in item 7.3.2.1, is presented in FSAR Chapters 3, 6, 8, 9 and it is not expedient to repeat it in Chapter 7. - System GY will be deleted from the list |  |
| DECISION No 113 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.1) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 117 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.5) |
| Recommendation: Page 104, 3rd bullet The phrase “uncertainty of three signals is displayed” has not technically completed sense |  |
| Reply 117 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.5) |
| Reply: Comment is not accepted. The other wording is given in the text |  |
| DECISION No 117 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.5) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian version will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 119 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.7) |
| Recommendation: Page 104, last paragraph but one The phrase “buttons duplicating main safety functions” is not clear |  |
| Reply 119 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.7) |
| Reply: Comment is not accepted. In the last para on page 104 the detailed description of the given buttons functioning is given |  |
| DECISION No 119 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.7) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian version will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 121 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.9) |
| Recommendation: Item 7.3.1.2.9 There is no “Warning” indicator on the SS panels |  |
| Reply 121 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.9) |
| Reply: Comment is accepted. In the latest version of MCR/ECR the "Warning" indicator is presented |  |
| DECISION No 121 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 123 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.11) |
| Recommendation: Item 7.3.1.2.12, page 114 It is necessary to describe how the sensors are powered if they are not fed by the modules of analog signals receipt |  |
| Reply 123 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.11) |
| Reply: Comment is accepted. Item 7.3.1.2.13 will be added by the following: "In cases, when the sensors are used, which could not be power supplied from TPTS, for example, bar meters, they are provided with personal power supply sources" |  |
| DECISION No 123 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 124 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.12) |
| Recommendation: Item 7.3.1.2.16 - there is no description of channel check on the whole, only a description of initiating part check (inconsistency with OPB-88/97). -RCD on MCR and ECR is connected to the safety panels only, and no signals from it can be transmitted to the CPS display |  |
| Reply 124 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.12) |
| Reply: Bullet 1 is accepted. Item 7.3.1.2.16 will be added by the following: "- TPTS means have self-diagnostic system, which performs serviceability control in continuous mode" Bullet 2 is not accepted. The design provides RCD connections with the MCR panels |  |
| DECISION No 124 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.12) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 125 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.15) |
| Recommendation: Table 7.2-8 There should be a commentary made to the table to explain the impact of inertial property on the error of protection actuation on monitored parameters |  |
| Reply 125 | FSAR SECTION: 7 FSAR |
| Reply: The following commentary will be made to Table 7.2-8: “Sluggishness of the instrumentation channel is considered in performing the safety analysis” |  |
| DECISION No 125 | FSAR SECTION: 7 FSAR Section 7.2 (4.4.2.13) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 126 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.16) |
| Recommendation: Table 7.3.1.3.7-1 - why this Section contains data on MCDS; - which I&C is in question; - what is the relation of humidity parameters, values of PH, electric conductivity, oxygen concentration to the Section under review. The Table shall contain data on accuracy norms of the whole channel for control and information display, including value of additional error |  |
| Reply 126 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.16) |
| Reply: Comment is accepted. From Table 7.3.1.3.7-1 the data on CMS, MCDS, oxygen concentration, electric conductivity, values of PH, humidity will be deleted |  |
| DECISION No 126 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.16) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed as per reply 148 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 127 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.17) |
| Recommendation: Item 7.3.1.3.8 The first sentence mentions the time for ICSS only (without PSCS) not for the system on the whole. This item should specify complete time of system initiation in accordance with implemented technical decisions (without possible options). |  |
| Reply 127 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.17) |
| Reply: Comment is not accepted. We consider that clarification of this data at present is prematurely. At commissioning, the special tests on time for passage of signals are planned, following which they will be introduced in FSAR |  |
| DECISION No 127 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.17) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the data from TA |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 128 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.18) |
| Recommendation: Item 7.3.1.3.9 No analysis of general design criteria GDC. The text only states that the design shall meet them (inconsistency with NUREG-0800) |  |
| Reply 128 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.18) |
| Reply: Comment is accepted. Item 7.3.1.3.9 will be deleted. In the names of the following items will be added 7.3.2.1; GDC 20. 7.3.2.2; GDC 23. 7.3.2.5; GDC 22. 7.3.2.6; GDC 22. 7.3.2.7; GDC 24. 7.3.2.8; GDC 13. 7.3.2.9; GDC 13. 7.3.2.10; GDC 21. |
| DECISION No 128 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.18) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 129 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.19) |
| Recommendation: It is unclear what emergency protections are meant |  |
| Reply 129 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.19) |
| Reply: Comment is accepted In the item 7.3.2.4 the following: "Prior to the unit commissioning or after outage for more than a week protection systems and safety devices of the emergency cooling system shall be tested." will be deleted |  |
| DECISION No 129 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.19) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 130 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.20) |
| Recommendation: Item 7.3.2.11 (SC12) The description of SC12 to justify the decision of operator's intervention in the actions of the safety systems is apparently insufficient (inconsistency with OPB-88/97, item 4.4.5.3). To resolve the issue of removal of prohibition of the operator's intervention in the actions of the safety systems earlier than 30 minutes after their initiation, it is necessary to: 1. Determine a list of safety systems for which prohibition of the operator's intervention is removed. 2. Work out justification for the operator's intervention in the actions of selected safety systems. 3. Analyse consequences of possible erroneous operator's actions. 4. Work out special instructions on exact state of the power unit after initiation of the safety systems and operator's actions. 5. Validate special instructions applying a mathematic model of the power unit. 6. If necessary, equip the MCR and ECR with additional monitoring and control tools based on results of the aforementioned work |  |
| Reply 130 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.20) |
| Reply: Comment is accepted. As per item 1. The list of systems is given in Table 7.3.1.2-1. Items 2-6 do not relate to the materials considered in the FSAR |  |
| DECISION No 130 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.20) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed as follows: “The operator’s actions procedures to remove the inhibition are provided in item 7.3.1.2.9”, and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 135 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.25) |
| Recommendation: Item 7.3.2.17 It is unclear what displays of SS channels installed nearby automated workstation of the reactor control senior engineer are in question |  |
| Reply 135 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.25) |
| Reply: Comment is accepted. In para 2 of item 7.3.2.17 the wording “placed near SERC AWS” will be replaced by “placed at SERC AWS” |  |
| DECISION No 135 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.25) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 136 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.26) |
| Recommendation: Page 138, the last paragraph Safety class is 2U not 2S. |  |
| Reply 136 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.26) |
| Reply: Comment is not accepted. 2S – denotes the elements of the control safety system |  |
| DECISION No 136 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.26) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The English version is correct and Russian version needs to be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 137 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.27) |
| Recommendation: The number of item 7.3.1.2.12 is inserted in the middle of item 7.3.1.2.11 |  |
| Reply 137 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.27) |
| Reply: Comment is not accepted. See the English version |  |
| DECISION No 137 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.27) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The English version is correct and Russian version needs to be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 143 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.33) |
| Recommendation: The section should include error calculations with due account for operating conditions, errors of sensors of signals of all types (including gamma-radiation, hydrogen, measured levels, flux and temperature thimbles, etc.). |  |
| Reply 143 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.33) |
| Reply: Comment is not accepted. From Table 7.3.1.3.7-1 the data on CMS, MCDS, hydrogen concentration, electric conductivity, values of PH, humidity will be deleted |  |
| DECISION No 143 | FSAR SECTION: 7 FSAR Section 7.3 (4.4.3.33) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Additional materials will be provided during the commissioning license stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 145 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.2) |
| Recommendation: Section 7.4 completely lacks information on the local control boards (LCB) which are classified as per OPB-88/97 by classes 2 and 3, and, as stated in Table 7.4-2, are part of the safety systems and safety important systems (inconsistency with OPB-88/97, item 4.4.5.4) |  |
| Reply 145 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.2) |
| Reply: Comment is accepted Item 7.1.1.6.2 will be added by the following: "The local control boards (LCB) are intended to control small autonomous process systems, which are as a rule constantly in operation (for example, ventilation, cleaning from mussels, ball cleaning)". The LCBs do not require the presence of the operative personnel. The LCB dimensions, structure, front panels are selected for each LCB particularly and depend on number of the sensors, actuators, control from the panel and its functional designation |  |
| DECISION No 145 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.2) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 146 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.3) |
| Recommendation: Table 7.4-3: - for the modes (see items 1.2, 1.4, 1.7, 1.12-1.15, 1.17), the participation in operation of the secondary circuit regulators is necessary, since any load change without the secondary circuit regulators is progress of transient and a possibility of EP actuation; - specify the list of automation tools (the 2nd column) participating in power restriction or reactor trip. For example, i.1.1 should be supplemented with EP, accelerated preventive protection, PP-1; items 1.5-1.7 should be supplemented with power control device, etc.; - purpose of the 4th and 5th columns of the Table is unclear |  |
| Reply 146 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.3) |
| Reply: Comment is not accepted. In those modes, where it is required, the participation in operation of the BRU-K (BRU-A) secondary circuit regulators is indicated |  |
| DECISION No 146 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.3) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 147 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.4) |
| Recommendation: Table Item 7.4.1.3 There is no description of NI CMS check (TH CMS is described in item 7.4.1.5) |  |
| Reply 147 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.4) |
| Reply: Comment is accepted In items 7.4.1.5 & 7.1.1.6 the "I&C-RC" will be added |  |
| DECISION No 147 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.4) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 148 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.5) |
| Recommendation: Page 141, 2nd paragraph from top. To assess the quality of the measuring channel functions, it is necessary to specify characteristics of the measuring channels (accuracy, fast operation) for the systems involved in safe shutdown |  |
| Reply 148 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.5) |
| Reply: Comment is accepted In item 7.4.1.6 the following will be added: "The accuracy requirements are given the Table 7.4-5" Table 7.4-5 Parameter; Value of main error, %. 1. Temperature; ± 0.7 (± 0.9 for ТSM). 2. Pressure, level, difference in pressure; ± 0.8. 3. Flow rate; ± 1.3. 4. Boron concentration; ± 2.8. 5 Hydrogen concentration; ± 4.3. 6 Oxygen concentration; ± 4.4. 7 Electric conductivity; ± 3.3. 8 РН value; ± 0.7. 9 Humidity; ± 2.8. |
| DECISION No 148 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.5) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 149 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.6) |
| Recommendation: Page 143 (Protections and interlocks) The purpose of "Links between the units for highly essential protections are performed both via input/output busbar and by the wire communications" is unclear |  |
| Reply 149 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.6) |
| Reply: Comment is accepted The sentence will be added by the following: "for reliability improvement" |  |
| DECISION No 149 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.6) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 152 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.9) |
| Recommendation: There is no analysis of general design criteria GDC 13, 19 and 24 (inconsistency with NUREG-0800) |  |
| Reply 152 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.9) |
| Reply: Comment is accepted From item 7.4.2.1 GDC 19, GDC 24 will be deleted. In item 7.4.2.2 "Sensors monitoring" "GDC 13" and the following sentence will be added: "In case the sensor signal overrunning behind the permissible limits (<4 mА, >20mА), the information is given to the operative personnel on its failure |  |
| DECISION No 152 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be completed as follows: “Parametric failure of sensors is also indicated” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 153 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.10) |
| Recommendation: Criterion SC9 (Sensors monitoring) There is no analysis of parameter and equipment failures |  |
| Reply 153 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.10) |
| Reply: Comment is accepted From item 7.4.2.1 GDC 19, GDC 24 will be deleted. In item 7.4.2.2 "Sensors monitoring" "GDC 13" and the following sentence will be added: "In case the sensor signal overrunning behind the permissible limits (<4 mА, >20mА), the information is given to the operative personnel on its failure |  |
| DECISION No 153 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.10) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 154 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.11) |
| Recommendation: There no analysis of safety criteria SC13, SC14; there are only titles (inconsistency with NUREG-0800) |  |
| Reply 154 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.11) |
| Reply: Comment is not accepted. As per the Table 7.1.2-2, section 7.4 is not evaluated as per SC13, SC14 |  |
| DECISION No 154 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. - In Table 7.1.2-2, SC-13, 14 the word “go-around” will be changed to “bypass” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 156 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.13) |
| Recommendation: Page 7-145 Reactor safe trip is a process not a state |  |
| Reply 156 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.13) |
| Reply: Comment is accepted The first sentence will be added by the following: "… means reactor transfer in …" |  |
| DECISION No 156 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.13) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 157 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.14) |
| Recommendation: Table 7.4-1: - the wording of item 1 is incorrect. Probably, it should be “systems required for reactor maintenance in hot trip condition during de-energization”; - 2nd column. There is not a notion of “safety category.” Instead of it, it could be “functional purpose of systems by effect on safety” |  |
| Reply 157 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.14) |
| Reply: : Comment is accepted The Table 7.4-1 will be given as follow: Item 1 "Systems required for reactor transfer in "hot condition" under the de-energization conditions" Item 2 "Systems required for reactor transfer in "cold condition" under the de-energization conditions" Item 3 "Systems required for reactor transfer in "hot condition" under the conditions without de-energization" Item 4 "Systems required for reactor transfer in "cold condition" under the conditions without de-energization" The text of the second column will be replaced by the "System designation" |  |
| DECISION No 157 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.14) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 158 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.15) |
| Recommendation: Item 7.4.1.3 The wording of the heading is incomplete and therefore uncertain |  |
| Reply 158 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.15) |
| Reply: Comment is accepted The wording of the heading will be added by "I&C-RC" |  |
| DECISION No 158 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.15) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 159 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.16) |
| Recommendation: Page 7-166 The title “Description of Turbine Hall I&C” lacks numbering |  |
| Reply 159 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.16) |
| Reply: Comment is not accepted. See the text |  |
| DECISION No 159 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.16) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The English version of FSAR is correct. The Russian text will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 160 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.17) |
| Recommendation: Page 7-166 If item 7.4.1.5 refers only to Turbine Hall I&C, there should be a respective item on check of Nuclear Island I&C |  |
| Reply 160 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.17) |
| Reply: Comment is accepted In items 7.4.1.5 & 7.1.1.6, "I&C-RC" will be added |  |
| DECISION No 160 | FSAR SECTION: 7 FSAR Section 7.4 (4.4.4.17) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 164 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.2) |
| Recommendation: The section is not structured by description of information provided on various hardware. Item 7.5.1.1 (Instrumentation of safety panels) describes presentation of information on the mimic panels and display screens as well |  |
| Reply 164 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.2) |
| Reply: Comment is accepted. The heading of item 7.5.1.1 will be changed by: "MCR panels and boards including safety panels" |  |
| DECISION No 164 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.2) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 166 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.4) |
| Recommendation: The list of safety systems (Table 7.5.1.1-1) does not correspond to the list in Section 7.3, in accordance with which I&C tools for ESFAS systems at the safety panels should be determined |  |
| Reply 166 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.4) |
| Reply: Comment is accepted. In first column of Table 7.5.1.1-1, ТН15, 25, 35, 45 will be replaced by TH18, 28, 38, 48 respectively. In Table 7.5.1.1-1 the following will be added: "ХР – hydrogen concentration monitoring and removal – localizing valves of normal operation system". |  |
| DECISION No 166 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.4) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 167 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.5) |
| Recommendation: Page 177, 1st paragraph The safety panels lack lighting indicators of the red colour listed in the text: - break of the primary circuit; - break of the secondary circuit; - pressure in containment not higher than 0.03 MPa; - stepwise startup of proper mechanisms |  |
| Reply 167 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.5) |
| Reply: Comment is accepted. |  |
| DECISION No 167 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.5) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be as follows: “The information is available, but on the yellow lighting indicator. In the text of the FSAR Rev. 1, the word “red” will be changed with “yellow”. The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 168 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.6) |
| Recommendation: Item 7.5.1.2, 1st and 3rd bullets The wide-frame displays and small-sized monitors mentioned in the text are not on the console. |  |
| Reply 168 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.6) |
| Reply: Comment is accepted partially. From item 7.5.1.2 the following will be deleted: "two small sized monitors for indication of parameters of PPPE, NFME, for each CPS set" |  |
| DECISION No 168 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.6) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 169 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.7) |
| Recommendation: Since the areas of MCR and ECR CPS have differences influencing safety, these differences should be described (inconsistency with OPB-88/97, item 4.4.3.2). |  |
| Reply 169 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.7) |
| Reply: Comment is accepted. Last para of item 7.5 will be added by the following: "Due to absence of the panels at the ECR, the NFME and also EP pushbuttons are located at the CPS panel. Besides, the safety panels of the ECR are provided with MCR/ECR selection keys" |  |
| DECISION No 169 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.7) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 170 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.8) |
| Recommendation: Item 7.5.1.2, page 178 The CPS panels lack indicator board “CPS channels actuation” mentioned in the text (inconsistency with PBYa RU AS-89, item 2.4.13) |  |
| Reply 170 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.8) |
| Reply: Comment is accepted. The indicator board "CPS channels actuation" is replaced by "EP actuation" |  |
| DECISION No 170 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.8) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 171 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.9) |
| Recommendation: Item 7.5.1.2, page 178 The CPS panels lack emergency instrumentation mentioned in the text |  |
| Reply 171 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.9) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 171 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: After the correction is completed, the materials will be submitted to the Principal and introduced in the FSAR after the commissioning stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 172 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.10) |
| Recommendation: Item 7.5.1.3, 1st paragraph On the CPS panel there is no equipment with broadened monitoring range for post-accident monitoring |  |
| Reply 172 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.10) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 172 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.10) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: After the correction is completed, the materials will be submitted to the Principal and introduced in the FSAR after the commissioning stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 173 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.11) |
| Recommendation: Table 7.5.1.3-1 The table specifies 4 signals of level measurement in the reactor are mentioned, whereas there are 5 signals on the safety panels |  |
| Reply 173 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.11) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 173 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: After the correction is completed, the materials will be submitted to the Principal and introduced in the FSAR after the commissioning stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 174 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.12) |
| Recommendation: Table 7.5.1.3-1 There are no indicating instruments for the parameter “radioactive radiation inside containment” on the safety panels |  |
| Reply 174 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.12) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 174 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.12) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: After the correction is completed, the materials will be submitted to the Principal and introduced in the FSAR after the commissioning stage |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 175 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.13) |
| Recommendation: The text after Table 7.5.1.3-1 should be significantly expanded and placed in the respective section of Chapter 7 |  |
| Reply 175 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.13) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 175 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.13) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be as follows “the paragraph after Table 7.5.1.3-1 will be expanded and include a description of equipment, its structure and functioning”. The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 176 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.14) |
| Recommendation: Table 7.5.2.3-1 (post-accident monitoring instrumentation): 4.4.5.14.1 The design does not determine parameters of group A, which are missing from RG 1-97 since they are specific for each NPP. 4.4.5.14.2. The form of the table on post-accident monitoring instrumentation does not correspond to RG 1-97 (division of the table by parameter groups, use of sub-titles in the column of parameters), this significantly impedes its review for compliance with this document. 4.4.5.14.3. Page 189, 3rd and 5th lines and further in the table At the FSAR development stage, it is necessary to indicate the accurate measurement range, but not “from above downwards.” 4.4.5.14.4. Pages 189, 190 and further in the table The instruments (digital and pointer indicators) located on the safety panels and indicating flow rate have dimension of m³/h whereas the table gives kg/s. 4.4.5.14.5. The table and, respectively, safety panels lack parameters recommended in RG 1-97: - Т in the cold legs; - Т in the bubbler tank |  |
| Reply 176 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.14) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 176 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.14) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 179 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.17) |
| Recommendation: The section does not contain information on check of the alarm tools in the MCR and ECR |  |
| Reply 179 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.17) |
| Reply: Comment is accepted. Item 7.3.1.2.16 will be added by the following para: "RCD is provided with the device for mechanisms position lamps checking and annunciation windows in the MCR and ECR" |  |
| DECISION No 179 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.17) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 181 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.19) |
| Recommendation: The section lacks information about power supply of the MCR/ECR instrumentation and control |  |
| Reply 181 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.19) |
| Reply: Comment is accepted. Item 7.5.1.1 will be added by the para: "I&C devices are power supplied with 24 V from TPTS 52 cabinets located in the MCR/ECR" |  |
| DECISION No 181 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.19) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 183 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.21) |
| Recommendation: The section shall contain a structural diagram of information entry to the safety panels, generalized mimic, consoles, TLS-U monitors (with obligatory display of all engineered tools and communication channels/lines through which information comes to the MCR) (inconsistency with OPB-88/97, item 4.4.2.3) |  |
| Reply 183 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.21) |
| Reply: Comment is accepted. See Figure 7.3.1.2-6 |  |
| DECISION No 183 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.21) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed: “and Fig. 7.4-1”, and FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 184 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.22) |
| Recommendation: The section shall include a structural diagram of MCR/ECR power supply |  |
| Reply 184 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.22) |
| Reply: Comment is accepted. Item 7.5.1.1 will be added by the para: "I&C devices are power supplied with 24 V from TPTS 52 cabinets located in the MCR/ECR" |  |
| DECISION No 184 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.22) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 185 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.23) |
| Recommendation: Section has been analysed in a cursory manner without substantiation of correspondence to each criterion of designing and safety as it was performed, for example, in Sections 7.2, 7.3 |  |
| Reply 185 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.23) |
| Reply: Comment is accepted. MCR/ECR conformity to each criterion of designing and safety will be advanced and added |  |
| DECISION No 185 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.23) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 186 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.24) |
| Recommendation: Since Table 7.1.2-1 (general design criteria) as for Section 7.5 does not correspond to standard analysis plan NUREG-0800, the Section was not analysed for compliance with the following design criteria: - OKP1 Standards and quality reports - OKP19 Control room - OKP24 Separation of protection and control systems The references to compliance of Section 7.5 with design criteria OKP21, OKP22 are not rightful since these criteria (reliability and possibility to perform tests of protection systems, independence of protection systems) refer to Sections 7.2 and 7.3 |  |
| Reply 186 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.24) |
| Reply: Comment is accepted. MCR/ECR сonformity to each criterion of designing and safety will be advanced and added |  |
| DECISION No 186 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.24) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 189 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.27) |
| Recommendation: Radioactivity monitoring function is missing in the critical functions (item 7.5.2.1) |  |
| Reply 189 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.27) |
| Reply: Comment is accepted. The text will be added by: "As per radioactivity monitoring function the devices of neutron flux monitoring, reactivity and also control rods position monitoring аre provided in the MCR/ECR" |  |
| DECISION No 189 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.27) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The radioactivity monitoring is available in the MCR. The details are provided in Chapter 11 of the FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 190 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.28) |
| Recommendation: Page 181 Indicator boards of availability of the safety systems (SS function) are missing on the safety panels (inconsistency with item 4.4.5.8) |  |
| Reply 190 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.28) |
| Reply: Comment is not accepted. Control safety system elements have advanced self-testing system, moreover the system periodical tests are carried out |  |
| DECISION No 190 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.28) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed as follows: “SS function is performed by the TLS-U. The information is displayed on the TLS-U monitors.”, and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 191 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.29) |
| Recommendation: Page 181, 3rd paragraph Indicator boards for implementation of stepwise startup scheme are missing on the safety panels |  |
| Reply 191 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.29) |
| Reply: Comment is accepted. In the latest version of the MCR/ECR the indicator board “Stepwise startup is completed” is added" |  |
| DECISION No 191 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.29) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 192 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.30) |
| Recommendation: Page 181, last paragraph but one The digital indicator boards mentioned in the text are missing on the operator’s panel |  |
| Reply 192 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.30) |
| Reply: Comment is accepted. The text will be corrected |  |
| DECISION No 192 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.30) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 193 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.31) |
| Recommendation: Pages 182, 183 The description of refuelling monitoring system (RMS) equipment and reactivity monitoring equipment (RME) has nothing to do with the analysis of Section 7.5 |  |
| Reply 193 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.31) |
| Reply: Comment is accepted. The text will be corrected |  |
| DECISION No 193 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.31) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 194 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.32) |
| Recommendation: Justification of safe operation of the unit based on design approaches for the MCR shall be confirmed by validation of the MCR (inconsistency with IEC 61771) |  |
| Reply 194 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.32) |
| Reply: Comment is accepted. The MCR has been validated at the I&C testing ground |  |
| DECISION No 194 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.32) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed: “ …which will be continued at the commissioning stage”, and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 195 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.33) |
| Recommendation: Item 7.5.1.2 There are EP and PP buttons not keys on the panel (comment on the Russian version only) |  |
| Reply 195 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.33) |
| Reply: Comment is accepted |  |
| DECISION No 195 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.33) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian version will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 196 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.34) |
| Recommendation: The text of the paragraph does not correspond to Table 7.5.1.3-1: - the text states that the equipment with an extended range is located on the CPS panel, however as seen from the Table that it is located on the safety panels; - 7 items are mentioned in the text whereas there are 8 items in the table |  |
| Reply 196 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.34) |
| Reply: Comment is accepted. The following text: "… on the CPS panel…" will be replaced by: "… on the safety panels…". In the text 8 items will be indicated |  |
| DECISION No 196 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.34) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 197 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.35) |
| Recommendation: Item 7.5.2.3, 2nd paragraph The comment on the equipment with an extended range is similar to the comment from the previous item. The reference given in the FSAR to the basic design stage is incorrect |  |
| Reply 197 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.35) |
| Reply: Comment is accepted. The following text: "… on the CPS panel…" will be replaced by: "… on the safety panels…". In the text 8 items will be indicated |  |
| DECISION No 197 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.35) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 198 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.36) |
| Recommendation: Table 7.5.2.3-1: - pages 7-194 – 7-196 only include table headings without a text; - on pages 7-192; 7-198 – 7-207 the table has no title |  |
| Reply 198 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.36) |
| Reply: Comment is not accepted. Comment is not clear. It requires additional explanation |  |
| DECISION No 198 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.36) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian version will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 199 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.37) |
| Recommendation: The form of numbering of pages of Section 7.5 differs from the numbering of other sections of Chapter 7 |  |
| Reply 199 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.37) |
| Reply: Comment is not accepted. Comment is not clear. It requires additional explanation |  |
| DECISION No 199 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.37) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian version will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 200 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.38) |
| Recommendation: The scale of temperature measurement in the reactor (Table 7.5.1.3-1) does not correspond to the instrument scale on the safety panels |  |
| Reply 200 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.38) |
| Reply: Comment is accepted. At present the information displayed at I&C panels and PC is being corrected and will be specified in future |  |
| DECISION No 200 | FSAR SECTION: 7 FSAR Section 7.5 (4.4.5.38) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 201 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.1) |
| Recommendation: Item 7.6.1.2 Clarify at what coolant temperature value the protection signal is generated 7 |  |
| Reply 201 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.1) |
| Reply: Comment is not accepted. The English version is correct |  |
| DECISION No 201 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.1) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Russian version will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 203 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.3) |
| Recommendation: Schematic diagram (Fig.7.6.1.7-1): - communication channels between SSHC process safety control systems and safety panels of MCR and ECR are incorrectly shown; - it is unclear whether tools of SSHC process safety control systems are duplicated or not; - the purpose of the additional sets of communication with the facility at the lower level is unclear; - distribution cabinets 10JBW mentioned in the text are not shown |  |
| Reply 203 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.3) |
| Reply: Comment is accepted partially. - Communications between ESFAS (TPTS) in the MCR/ECR are described in details in section 7.3, the same section states that ESFAS (TPTS) means are not duplicated. - The text will be added by the following: "Special equipment set provides the information exchange between low level facilities (controllers) and communication of special equipment set of the unit level; - 10JBW cabinets mentioning will be deleted from the text" |  |
| DECISION No 203 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.3) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 205 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.5) |
| Recommendation: Safety criteria SC3, SC10 (see Table 7.1.2-2) and general design criterion OKP13 (see Table 7.1.2-1) are not considered. Analysis shall be performed as per the criteria mentioned in the comments on Section 7.1 (inconsistency with NUREG-0800) |  |
| Reply 205 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.5) |
| Reply: Comment is accepted. Item 7.6.2 will be added as follow: "SC3. Quality of components and modules. Observation of SC3 requirements is provided with the following measures: - Development of fire alarm and automation was performed as per the requirements of the ISO-9001-904 standard; - Equipment manufacturing was performed as per the "Quality assurance program at AFPS manufacturing for the BNPP in the IRI (QAP (M)" SC10. Possibility of calibration and testing. Observation of SC10 requirements is provided with the following measures: - At factory tests the system equipment passes the check under the authorized program to demonstrate that it adequately provides the performance of all the functions stipulated by the design; - At commissioning the system passes complex tests at the NPP, which purpose is to confirm serviceability of all the system as a whole; - During the operation, it passes periodic checks at work of the power unit.". The naming of item 7.6.2.2.2 will be added by: "OKP13" |  |
| DECISION No 205 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.5) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 206 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.6) |
| Recommendation: During consideration of SC2 (single failure criterion) the condition of fire alarm during NPP de-energization is not described" |  |
| Reply 206 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.6) |
| Reply: Comment is accepted. Item 7.6.2.2.4 will be added as follow: "All the AFPS means have two power supply inputs from inverter circuit" |  |
| DECISION No 206 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.6) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 207 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.7) |
| Recommendation: Criterion SC20 Specify what recommendations for the fire fighting personnel are meant. FSUE VO “Safety” which the special task “Automated fire protection system supervisor” should be agreed with knows nothing about its implementation in the TLS-U |  |
| Reply 207 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.7) |
| Reply: Comment is accepted. From item 7.6.2.2.6 the following wording will be deleted: "Recommendations can be issued on the operator’s enquiry to the personnel that provide firefighting" |  |
| DECISION No 207 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.7) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 209 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.9) |
| Recommendation: Page 181, second bullet from bottom Make the text of the paragraph clearer |  |
| Reply 209 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.9) |
| Reply: Comment is accepted. The wording "…- transferring the process equipment operation parameters and …" will be replaced by: "…- monitoring of the process equipment operation parameters and …" |  |
| DECISION No 209 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 211 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.11) |
| Recommendation: Page 184 The term “manual annunciator” is not clear |  |
| Reply 211 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.11) |
| Reply: Comment is not accepted. The wording "manual annunciator" will be replaced by "handheld fire annunciator" |  |
| DECISION No 211 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The term “manual annunciator” will be changed by “call point” in the English version. The FSAR Rev. 1 will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 212 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.12) |
| Recommendation: Page 185 Marking of fire fighting controller JBW is wrong |  |
| Reply 212 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.12) |
| Reply: Comment is accepted. Marking "JBW" will be replaced by "JBВ" |  |
| DECISION No 212 | FSAR SECTION: 7 FSAR Section 7.6 (4.4.6.12) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 213 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.1) |
| Recommendation: Page 217, 1st paragraph: - specify how the CRs are lifted from the lower mechanical stops (to the lower limit switch); - at what malfunctions of the group and individual control system it is possible to use the mentioned mode and for what purposes (Power Unit is shutdown, what is the purpose of lifting CRs at failed group and individual control system) |  |
| Reply 213 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.1) |
| Reply: The procedure of CRs lifting from the lower mechanical stops is performed in the following way: - under the mode of manual group/individual control the operator in MCR, using the button “Removal from the stop”, makes lifting of the selected group/selected CRs of one group from the lower stop to the lower limit switch. The more detailed description of the procedure is given in the operation regulations. The above-mentioned mode is used for reducing the mechanical wear of the CPS drives |  |
| DECISION No 213 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.1) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 214 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.2) |
| Recommendation: Page 218, paragraph after the table The wording of this paragraph lacks any technical sense |  |
| Reply 214 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.2) |
| Reply: In the given paragraph the wording “ensures the single error” will be replaced with the wording “prevents operator’s error” |  |
| DECISION No 214 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.2) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 215 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.3) |
| Recommendation: Item 7.7.1.1.10 Since during loss of normal operation power supply the set continues operation from the storage battery, it is necessary to indicate time of the set operation in this mode |  |
| Reply 215 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.3) |
| Reply: The comment is accepted. The scheme of the backup power supply makes it possible to provide the power supply to the CRs position control equipment under accident conditions during 1 h under complete loss of a.c. power supply (see Chapter 8) |  |
| DECISION No 215 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.3) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 216 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.4) |
| Recommendation: Item 7.7.1.2.4 A scheme of channel-by-channel check of signals PP-1, PP-2, APP shall be given (inconsistency with OPB-88/97, item 4.1.10) |  |
| Reply 216 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.4) |
| Reply: The comment is accepted. PP checks are performed simultaneously with checks of the reactor shutdown systems. The order of checks of PP initiating part is similar to that given in i. 7.2.1.9 “System checks”. The text of section 7.7.1.2.4 FSAR will be corrected |  |
| DECISION No 216 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.4) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 217 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.5) |
| Recommendation: Item 7.7.1.3 This item shall contain the ARM algorithm and information on verification of its software |  |
| Reply 217 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.5) |
| Reply: The text of i. 7.7.1.3 and Figure 7.7-5 contain the information on APC algorithms. Verification and validation have been made for the APC software. The scope of the presented information corresponds to RG 1.70. No FSAR revision is needed |  |
| DECISION No 217 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.5) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The following sentence will be added in the text of FSAR Rev. 1: “Verification and validation have been made for the APC software” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.6) |
| Recommendation: Item 7.7.1.3.6 Presentation of information on ARM is described in general words. Where the information goes to and what sort of information goes to the operator shall be described |  |
| Reply 218 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.6) |
| Reply: The text of i. 7.7.1.3.6 will be supplemented with the following information: “For APC control the following is arranged on the MCR panel 30LBT01 for the operator: - switch of mode selection and putting the APC into operation and the corresponding indicators; - indicators of APC serviceability; - buttons of APC mode selection with the corresponding indicators; - key for APC on/off for individual channel, for control of the selected group of CPA CRs by APC commands; - buttons for correction of setpoints by MSH pressure |  |
| DECISION No 218 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.6) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218a | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.7) |
| Recommendation: Page 242, 1st paragraph What specialized equipment is meant, where is it described? |  |
| Reply 218a | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.7) |
| Reply: The specialized equipment represents a complex of level and temperature indication equipment and it consists of four independent channels |  |
| DECISION No 218a | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.7) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The description of level monitoring will be included in FSAR Rev. 1 section 7.5 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218b | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.8) |
| Recommendation: Item 7.7.1.4.3.7 This item shall reflect the issue of procedure of changing the ICIS adjustment parameters |  |
| Reply 218b | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.8) |
| Reply: Adjustment parameter variation is not provided for SHC-IC |  |
| DECISION No 218b | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.8) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The description of level monitoring will be included in FSAR Rev. 1 section 7.5 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218c | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.9) |
| Recommendation: Item 7.7.1.4.3.9 It is necessary to substantiate arrangement of the in-core noise diagnostics SHC together with SHC-3 |  |
| Reply 218c | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.9) |
| Reply: ICNDE-SHC is purposed for SPND signals variable component processing and analysis with the purpose of coolant local boiling detection within the core scope. The necessity of ICNDE-SHC arrangement in close vicinity to SHC-P in rooms ZK1 and ZK2 is caused by the reason that the signals of SPND signal variable components have the level 10-10 – 10-11 A and should be transferred from SHC-P to ICNDE-SHC without signal intermediate processing and amplification (otherwise all necessary noise data can be lost). ICNDE-SHC is tested and referred to seismic category 1 as per PNAE G 006-97 to prevent ICNDE-SHC influence to SHC-P, IV group of hardware design version as per GOST P 50746 of electromagnetic compatibility (communications between ICNDE-SHC and SHC-P have no galvanic coupling, the protocol of data transfer from SHC-P to ICNDE-SHC is unidirectional, ICNDE-SHC hardware are supplied from reliable power sources) |  |
| DECISION No 218c | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.9) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Seismic category will be corrected to 1. The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218d | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.10) |
| Recommendation: .7.7.1.4.4.9; The statement saying that Operation with VMS SHC is performed from WS placed in the technical support center is not reflected in the design documents and appears to be arguable |  |
| Reply 218d | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.10) |
| Reply: Working station for VMS is not provided within MCDS. The data are transferred into TLS-U via ICIS CCUL (signals of controlled equipment exceeded vibration (thermal displacements under heat-up – cooldown conditions), generalized signals of hardware failures). In case of such signals, the personnel can receive detailed information and analyse the situation directly in the monitor displays incorporated into VMS racks |  |
| DECISION No 218d | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.10) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. The wording of item 7.7.1.4.4.9 will be corrected in the FSAR revision 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218e | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.11) |
| Recommendation: Item 7.7.1.4.7.3 There shall be information what SIA programs are performed periodically and with what cycle, who initiates the startup of the programs (for example, the program “Reactor Simulator” is started by the physical engineer who also analyzes obtaining results once a month; the program control of residual cyclic life of the main equipment of RP V-446” is also started periodically once a month, etc.) |  |
| Reply 218e | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.11) |
| Reply: All SIA codes are started during SIA initiation by the personnel. Separate functions of these codes are initiated by the personnel periodically (calculation of residual life, calculation –prediction of the code “Reactor Simulator” etc.). The codes operate continuously and automatically for acquisition of required operating data, updating of parameters in formats (in the course of CCUL data receiving). “Reactor Simulator” code operates as under on-line so off-line modes. SAKOR calculations can be provided just every month so every three days, i.e. SIA code functions are not cyclic but random, by the personnel demand. SIA codes do not require round-the-clock operation of the shift personnel, but personnel actions are required for SIA code functions (except ICNDE applied software functions which are initiated automatically during software loading, personnel can follow the results of the code operation by demand |  |
| DECISION No 218e | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.11) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. The text will be included in the FSAR, Revision 1 in item 7.7.1.4.7.3 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218f | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.12) |
| Recommendation: Page 262, 1st paragraph This wording has no technical sense. Besides, individual tasks of this function are performed by the physical engineer on the basis of accumulated information |  |
| Reply 218f | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.12) |
| Reply: In addition to the wording presented: All required parameters for the analysis are provided for the personnel in visual representation with the help of specially developed code of data presentation (graphic shell). The personnel can plot the curves using selected parameters, provide the protocols for the comparison as current so archival parameters (values), operate with ICIS CCUL databases, etc. I.e. it is not just data acquisition, but the personnel has a convenient opportunity of RP operation integrated analysis, parameter variation for the core and controlled ICIS, including the detection of the tendencies at an early stage of the process course |  |
| DECISION No 218f | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.12) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. The text will be included in the FSAR, Revision 1 in item 7.7.1.4.7.3 instead of the wording to which the comment has been given |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 218g | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.15) |
| Recommendation: Item 7.7.2.5.3, 2nd paragraph It is necessary to indicate the value of accuracy decrease during RP power determination under failures of the sensors |  |
| Reply 218g | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.15) |
| Reply: In RG 1.70 (see i. 7.7.2) there are no requirements for presentation of this information in i. 7.7.2.5.3 FSAR. From the analysis of the recommendations contained in NUREG-0800 (see i. 7.7.) it is seen that there is also no necessity to present the information of such character |  |
| DECISION No 218g | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.15) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. The text will be included in the FSAR, Revision 1 as follows: “The value of the reactor thermal power measurement accuracy reduction in case of failure of the sensors whose signals are used in the calculation of this power will be provided in the Operation Procedures” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 221 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.16) |
| Recommendation: Page 207, 2nd sentence from bottom Indicate which adjacent systems information is transmitted to |  |
| Reply 221 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.16) |
| Reply: The sentence will be changed for the following: "transmittal of the information on position of all reactor CRs into MCDS, on position of CRs of groups 8…10 into NFME;" |  |
| DECISION No 221 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.16) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 222 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.17) |
| Recommendation: Fig.7.7-1 has no title. |  |
| Reply 222 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.17) |
| Reply: The comment is accepted. The title of the Figure "Structural diagram of GC PCPI" will be given |  |
| DECISION No 222 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.17) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 223 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.18) |
| Recommendation: Page 218, 1st paragraph It is written "assure" whereas it should be "prevent" |  |
| Reply 223 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.18) |
| Reply: The text of FSAR in English will be corrected in the given paragraph |  |
| DECISION No 223 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.18) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 225 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.20) |
| Recommendation: Tables 7.7-4, 7.7-5 No logics of preventive protection signal generation is described |  |
| Reply 225 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.20) |
| Reply: In Tables 7.7-4 and 7.7-5 the formalized form is given for the algorithms of PP-1 and APP. The straight lines in the column “Logic” mean processing of signals by “2 out of 3” logic |  |
| DECISION No 225 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.20) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 226 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.21) |
| Recommendation: Table 7.7-6 Signal on position 5 is not used |  |
| Reply 226 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.21) |
| Reply: The comment is not accepted. The given signal is available in the list of APP signals |  |
| DECISION No 226 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.21) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the following: The Russian and English version of the table will be corrected. The word “system’ will be changed by “grid” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 227 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.22) |
| Recommendation: Page 207, last paragraph but one Specify transmission of signals on the condition of RCP and feed water pump, RCP power supply frequency (i.e. from EPPS or primary transducers) |  |
| Reply 227 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.22) |
| Reply: The sentence will be corrected proceeding from the fact that no signals are transmitted into PG from the primary transducers |  |
| DECISION No 227 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.22) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 (item 7.7.1.2.3) will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 228 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.23) |
| Recommendation: Page 227, 2nd paragraph The wording of this paragraph is not readable |  |
| Reply 228 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.23) |
| Reply: In our opinion the sense of the given text is clear |  |
| DECISION No 228 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.23) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The English wording on page 208, 2nd paragraph, will be corrected as follows: instead of “…when it is decreased…. “ the text will be: “….if it is decreased to 47 Hz, the power should be proportionally decreased by 2% for each 1 Hz of frequency decrease” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 229 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.24) |
| Recommendation: Item 7.7.1.3 For the reactor power control mode, different abbreviations are used: “H” and “N” |  |
| Reply 229 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.24) |
| Reply: For the reactor power control mode the designation “N” will be used in English version, and “H” – in Russian version |  |
| DECISION No 229 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.24) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 230 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.25) |
| Recommendation: Fig.7.7-5 has no title |  |
| Reply 230 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.25) |
| Reply: The title will be added “APC functional diagram” |  |
| DECISION No 230 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.25) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 230a | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.26) |
| Recommendation: Item 7.7.1.4.3.1, 6th bullet; Provide the list of the APCS systems, which the in-core instrumentation system exchanges information with |  |
| Reply 230a | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.26) |
| Reply: ICIS has communications with TLS_U, CPS equipment (EP-PP), RCIS, ESFAS and power unit process systems (I&C of reactor and turbine compartments) |  |
| DECISION No 230a | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.26) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and the text will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 231 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.27) |
| Recommendation: Item 7.7.2.5.7. It should be: "hot state" mode not "hot heat-up" mode |  |
| Reply 231 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.27) |
| Reply: comment is accepted. The text will be corrected |  |
| DECISION No 231 | FSAR SECTION: 7 FSAR Section 7.7 (4.4.7.27) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 232 | FSAR SECTION: 7 FSAR Section 7 (4.4.8) |
| Recommendation: Expert assessment of protection and interlocking algorithms of safety systems |  |
| Reply 232 | FSAR SECTION: 7 FSAR Section 7 (4.4.8) |
| Reply: Comment is accepted. The issues related to operation algorithms of safety systems equipment we suggest to be discussed at FSAR Chapter 6 review |  |
| DECISION No 232 | FSAR SECTION: 7 FSAR Section 7 (4.4.8) |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: See reply 15 to OCE letter LTR-13070-63479 dated 14.12.05. Updated algorithms will be included in Appendix D to Chapter 7 of the FSAR, Revision 1. The final version of the algorithms will be included in the FSAR after completion of commissioning |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

OCE comments on Appendix B1 (to MoM to FSAR-7 (Rev. 0) dated 03-13.03.07, Tehran)

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 1 | FSAR: 7 Item 7.4.1.4 |
| Recommendation: While time of development of FSAR-07, the TAs for instrumentation cabinets of I&C-TС, I&C-TG was not finalized, please specify how the reiative section of FSAR –07 was developed without correct/final information |  |
| Reply G-1 | FSAR: 7 Item 7.4.1.4 |
| Reply: Comments are not accepted. FSAR gives general description of the I&C-TС, I&C-TG functions and structure principles which have not changed since the РSAR stage. Guide 1-70 does not require more detailed information |  |
| DECISION No 1 | FSAR: 7 Item 7.4.1.4 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In Revision 1 of the FSAR it will be mentioned that I&C-TC and I&C-TG have a similar architecture with I&C-RC, and a reference to item 7.4.1.3 will be provided |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No.2 | FSAR: 7 General comments |
| Recommendation: Please be noted that within the period of РSAR –07 and Chapter 7 FSAR many changes have been introduced to APCS and in this respect, it is kindly requested to foresee all the changes in FSAR accordingly |  |
| Reply G-2 | FSAR: 7 General comments |
| Reply: Comments are not accepted To the moment of the FSAR Chapter 7 (Revision 0) issue all the changes as compared with the PSAR were reflected. It is evident that this process will be continued and accomplished after completing of commissioning and power unit test running |  |
| DECISION No 2 | FSAR: 7 General comments |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Comments are accepted. (See agreement No. 25) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 3 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Recommendation: In table 7.2-2 “List of design initiating events of accidents determined by the specific accident signals” it seems that “difference between saturation temperature and maximum temperature in any hot leg less than 10°C” is related to the “Decrease of boric acid concentration, but it is not mentioned in table. Please clarify |  |
| Reply 1 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Reply: Signal "Difference between saturation temperature and maximum temperature in any hot leg less than 10°C" is a condition of reactor scram under the accidents pertained to primary pressure decrease (false injection into PRZ, PORV false opening, a spectrum of MCP breaks). This clarification will be introduced in FSAR during its correction |  |
| DECISION No 3 | FSAR SECTION: Введение |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Comments are accepted and the reply will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No.5 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Recommendation: In table 7.2-2, it seems that “large leaks with loss-of-coolant” and “primary-secondary leak within SG” also are initiating event causing actuation for “pressure above the core is below 14,7MPa at reactor power exceeding 75%Nnom” |  |
| Reply 3 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Reply: For criterion "pressure above the core is below 14,7Mpa at reactor power exceeding 75%Nnom" in columns " large leaks with loss-of-coolant" and "primary-to-secondary leak within SG " of Table 7.2-2 the respective revisions will be introduced |  |
| DECISION No 5 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 6 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Recommendation: In table 7.2-2, it seems that “small leaks with loss-of-coolant” and “large leaks with loss-of-coolant” are initiating event causing actuation for “excessive pressure in the containment is more than 0,029MPa”. Please clarify |  |
| Reply 4 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Reply: For criterion "excessive pressure in the containment is more than 0,029MPa" in columns " small leaks with loss-of-coolant” and “large leaks with loss-of-coolant” of Table 7.2-2 the respective revisions will be introduced |  |
| DECISION No 6 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 7 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Recommendation: In table 7.2-2 “small leaks with loss-of-coolant” is initiating event for “pressure above the core more than 17,5MPa”. Please clarify |  |
| Reply 5 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| Reply: We confirm that PI signal more than 17,5 MPa is referred to the initiating event “small leaks with loss-of-coolant” |  |
| DECISION No 7 | FSAR: 7 FSAR 7.2, table 7.2-2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted and will be corrected in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 10 | FSAR: 7 FSAR 7.2, table 7.2-9 |
| Recommendation: In table 7.2-9 “logic of generation of emergency protection”. In item 10, in order to have EP signal, how many RCP are needed to be in status “started up” |  |
| Reply 8 | FSAR: 7 FSAR 7.2, table 7.2-9 |
| Reply: It is probably the comment is referred to item 10. The attribute of RCP status will be excluded |  |
| DECISION No 10 | FSAR: 7 FSAR 7.2, table 7.2-9 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NNSD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In item 10 of table 7.2-9, the attribute of RCP status will be excluded from FSAR Rev. 1. 1st bullet- include "A given RCP" |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No.11 | FSAR: 7 FSAR 7.2, table 7.2-9 |
| Recommendation: In table 7.2-9 “logic of generation of emergency protection”. Set point for “Seismic impact” item No.20 and “local power rate” item No.23 are different from the value given in PSAR. Please clarify |  |
| Reply 9 | FSAR: 7 FSAR 7.2, table 7.2-9 |
| Reply: We confirm the correctness of the setpoint value as to item 20. Regarding linear heat rate (item 23) the reply is given in the enclosure |  |
| DECISION No 11 | FSAR: 7 FSAR 7.2, table 7.2-9 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The following information will be included in FSAR Rev. 1: Table 7.2-9 regarding linear heat rate shall be changed as follows 23 Local power, W/cm (depends on the height of SPND location and the number of operating RCP sets), more than; 105 % qLinstalled. Note. The setpoint value as to item 23 is determined in percentage of the absolute value of PP-2 setpoint corresponding to ultimate heat rate for the fuel rod QLadd. Its value depends on the number of operating RCP sets and is determined by the formula qLinstalled=QLadd.·К1,2,3 where QLadd.=448 W/cm at Х < 177,5 and QLadd.=(596 - 0,8338·Х) W/cm at 177,5<Х<355,0; Х- height from the core bottom, cm; К1=1 (4 RCP sets in operation); К2=0,46 (2 RCP sets in operation); К3=0,76 (3 RCP sets in operation).. |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 13 | FSAR: 7 FSAR Section 7.3.1.2.6 |
| Recommendation: In chapter No. 7.3.1.2.6 of PSAR, the 9th paragraph has been eliminated in FSAR |  |
| Reply 11 | FSAR: 7 FSAR Section 7.3.1.2.6 |
| Reply : The text of para 9 of 7.3.1.2.6 of the PSAR repeats the of para 6, so it was deleted from the FSAR |  |
| DECISION No 13 | FSAR: 7 FSAR Section 7.3.1.2.6 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In revision 1 of the FSAR paragraph 9 of the PSAR will be restored |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 14 | FSAR: 7 FSAR Section 7.3.1.2.9 |
| Recommendation: In chapter No. 7.3.1.2.9 FSAR, please clarify the meaning of 2nd paragraph |  |
| Reply 12 | FSAR: 7 FSAR Section 7.3.1.2.9 |
| Reply: Comments are not accepted The issue requires clarification, as the 2nd paragraph in chapter No. 7.3.1.2.9 of FSAR corresponds completely to the similar PSAR text |  |
| DECISION No 14 | FSAR: 7 FSAR Section 7.3.1.2.9 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: the English wording of the paragraph will changes in FSAR Rev. 1 as follows: “The protection actions for the main safety functions are memorized, and the inhibition is introduced for both automatic and manual actions that are directed against safety until the plant cooldown” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 15 | FSAR: 7 FSAR Section 7.3.1.3 |
| Recommendation: In the 3rd row of the table No. 7.3.1.3-2 (page No. 120), the pressure set-points for opening and closing BRU-A are mentioned 7,17 and 6,3 МPа, whereas in algorithm Nos. RAS10EE001 to RAS40EE001 (page Nos. 7D-118 to 7D-129) the a.m. values are 7,15 и 6,27 МPа |  |
| Reply 13 | FSAR: 7 FSAR Section 7.3.1.3 |
| Reply: Comments are accepted. Table 7.3.1.3-2 has been revised and attached |  |
| DECISION No 15 | FSAR: 7 FSAR Section 7.3.1.3 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Reply is accepted and will be introduced in the FSAR Rev. 1 as per attached table. - Table 7.3.1.3-2 continued Initial events; Safety functions provided; Actuated systems; Automatic actuation; Remarks. primary pressure decrease;;  additional boron supply system, TW;  emergency gas removal system, YR;; Operator control. *— RP cooldown through the secondary circuit;; emergency cooldown system: RS, RA;; Operator control. *— residual heat removal through the secondary circuit;; emergency cooldown system: RS, RA;; - BRU-A opening Р2>7,15 MPa; - BRU-A closing Р2<6,27 MPa; - pump start-up, valves opening in the line of emergency feedwater LSG<-900 mm.. 3 Secondary leak (prior or after MSIV); RP cooldown through the primary system;; LP ECCS and ТН10-40 line of smooth cooldown;; Operator control. RP cooldown through the secondary system;; emergency cooldown system RS,RA;; Operator control. *— residual heat removal through the secondary system;; emergency cooldown system RS,RA;; - BRU-A opening Р2>7,15 MPa; - BRU-A closing Р2<6,27 MPa; - SG safety valve opening Р2>8,23 MPa; - SG safety valve closing Р2<6,86 MPa; pump start-up and opening of emergency feedwater line valves LSG<-900 mm.. |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 17 | FSAR: 7 APPENDIX D |
| Recommendation: in the following algorithms of book 5 FSAR, the output signals have not been specified TFS21EZ001, TFS30EZ001, TFS31EZ001, TFS40EZ001 (page.7D-20, 7D-27, 7D-31, 7D-37) |  |
| Reply 15 | FSAR: 7 APPENDIX D |
| Reply: Comments are not accepted At present the process algorithms are being checked on the mathematical model of the power unit. Then the algorithms check up is planned on the BNPP-1 power unit actual equipment during the functional testing and hot running-in. Based on these activities results the actual algorithms variant will be developed, which will be introduced in to the final FSAR version |  |
| DECISION No 17 | FSAR: 7 APPENDIX D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 18 | FSAR: 7 APPENDIX A |
| Recommendation: In page No.7А-249 of FSAR, the level transducers TWNOL001 A, B have been specified as redundant, whereas in the following algorithms, it has not been specified which of those level transducers have been used in this algorithm. If all redundant transducers have been sued, the respective preliminary signals processing logic ("And", "OR", "MEAN Value", "2 out of 3" …) shall also be specified. TWS10EE007. TWS20EE007. TWS30EE007. TWS40EE007. TWS10EE014. TWS20EE014. TWS30EE014. TWS40EE014 |  |
| Reply 16 | FSAR: 7 APPENDIX A |
| Reply: In all cases of application of excessive number of transducers - А, В or А, В, С – the signals processing logic is selected as "MEAN Value" |  |
| DECISION No 18 | FSAR: 7 APPENDIX A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: A reference to the Fig. 7.4-5 together with the reply will be added to FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered.. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 19 | FSAR: 7 FSAR Section 6.3.1 |
| Recommendation: According to the page No. 6.3.1.85 FSAR (chapter No. 6.3.1.2.3) set-points for alarming of transducer Nos. TWNOL001 are 25, 216 and 231whereas in page Nos. 7.А-250 to 259 the a.m. set points have not been specified |  |
| Reply 17 | FSAR: 7 FSAR Section 6.3.1 |
| Reply: Comments are accepted. The set-points for alarming of TW tanks level and the transducers coordinates will be given in the FSAR Chapter 7 |  |
| DECISION No 19 | FSAR: 7 FSAR Section 6.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 20 | FSAR: 7 APPENDIX A |
| Recommendation : In page Nos. 7.А-250 to 254, coordinates for transducers TWNOL001А, В have not been specified |  |
| Reply 18 | FSAR: 7 APPENDIX A |
| Reply: Comments are accepted. The set-points for alarming of TW tanks level and the transducers coordinates will be given in the FSAR Chapter 7 |  |
| DECISION No 20 | FSAR: 7 APPENDIX A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Reply is accepted and will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 21 | FSAR: 7 APPENDIX D |
| Recommendation: according to the algorithm Nos. TWS10EE001. YZS40EY001, YZS41EY001 and 1YZS60EY005, the primary condition of pumps operation is operation of diesel generator, whereas there are some operational status that the DG could be turn-off and pumps should be turn-on. For example, when there is any leakage in primary circuit, consumers will be supplied by external network, without any supplies from network power station or DG. In the other hand, DG should be turned-on when we could not supply, our electrical consumers from nuclear power station on external network |  |
| Reply 19 | FSAR: 7 APPENDIX D |
| Reply: At present the process algorithms are being checked on the mathematical model of the power unit. Then the algorithms check up is planned on the BNPP-1 power unit actual equipment during the functional testing and hot running-in. Based on these activities results the actual algorithms variant will be developed, which will be introduced in to the final FSAR version |  |
| DECISION No 21 | FSAR: 7 APPENDIX D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1. (see reply 15) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 22 | FSAR: 7 APPENDIX D |
| Recommendation: In stage 0 of algorithm No. YZS40EY001 (cascade actuation) The input signal "А04" of algorithm No. TWS10EE001 comes to status "1"and pump No. TW10D001 turns-on immediately whereas in stage 3 of algorithm No. YZS40EY001, the input signal "А06" of algorithm No. YZS40EY001 comes to status "1" after 30s delay. As a result, the output signal "В09" of algorithm No. 1YZS41EY001 comet to status "0" and at the same time if the input signals А03, А01 or А05 of algorithm No. TWS10EE001 come to status "1", the pump No. TW10D001 turns-on |  |
| Reply 20 | FSAR: 7 APPENDIX D |
| Reply: At present the process algorithms are being checked on the mathematical model of the power unit. Then the algorithms check up is planned on the BNPP-1 power unit actual equipment during the functional testing and hot running-in. Based on these activities results the actual algorithms variant will be developed, which will be introduced in to the final FSAR version |  |
| DECISION No 22 | FSAR: 7 APPENDIX D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1 (see reply 15) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 23 | FSAR: 7 APPENDIX D |
| Recommendation: To check the operation of the valve TH15S012, in the condition that: the pump No. TH15D001 is on and the flow of the a. m. Pump is less than 35 m3/h, now if the water level in tank TH10В001 is more than 0,25 m, the valve No. TH15S012 will be open (algorithm No. TНS15EE010). In the other view of the valve No. TH15S012 operation, this valve shall be closed based on algorithm No. TНS15EE013 when the water level is lower than 0,25 m. These common set-points (0,25 м) for valve open and close conditions will actuate this valve in open/close status frequently. We believe that a trigger is necessary here to avoid that |  |
| Reply 21 | FSAR: 7 APPENDIX D |
| Reply: At present the process algorithms are being checked on the mathematical model of the power unit. Then the algorithms check up is planned on the BNPP-1 power unit actual equipment during the functional testing and hot running-in. Based on these activities results the actual algorithms variant will be developed, which will be introduced in to the final FSAR version |  |
| DECISION No 23 | FSAR: 7 APPENDIX D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1 (see reply 15) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 24 | FSAR: 7 APPENDIX D |
| Recommendation : In order to provide the suction flow of the residual heal removal pump TH30D001 from the reactor coolant loop, it seems that a branch including a control valve (namely TH93S001) shall be used to connect the down-stream of the check-valve TH38S005 to upstream of the control valves TH91, 92, 94 S001 |  |
| Reply 22 | FSAR: 7 APPENDIX D |
| Reply: At present the process algorithms are being checked on the mathematical model of the power unit. Then the algorithms check up is planned on the BNPP-1 power unit actual equipment during the functional testing and hot running-in. Based on these activities results the actual algorithms variant will be developed, which will be introduced in to the final FSAR version |  |
| DECISION No 24 | FSAR: 7 APPENDIX D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1 (see reply 15) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 25 | FSAR: 7 APPENDIX A |
| Recommendation: In the "List of systems connected with ТН", (page No. 7.А-191) the TD and TH50-70 systems are not included whereas in the P&I drawing the a.m. systems are connected to ТН. Moreover, according to page No. 6.3.1-7 of FSAR (Ch. 6), the ТН system is interacting with the ТА and ТК systems and not interacting with the "TB, TD, TG, TP, YC, TP, TZ" systems. In contrast to page No. 6.3.1-7, the P&I (page No.7.А-191) "TB, TD, TG, TP, YC,TP,TZ" systems are connected to ТН. Also ТА and ТК systems are not connected to ТН |  |
| Reply 23 | FSAR: 7 APPENDIX A |
| Reply: Comments are not accepted. The purpose of functional diagrams is to indicate the number and location of the I&C transducers. Therefore some ancillary processing lines are not given at P&I diagrams |  |
| DECISION No 25 | FSAR: 7 APPENDIX A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated P&I diagrams (in order to match them with Chapter 6) will be provided in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 26 | FSAR: 7 FSAR Section 6.3.1 |
| Recommendation : According, to the table No. 6.3.1.1.2.3-2, three following conditions are necessary for closing ТН15-45S021 gate valves automatically - Level in tanks Nos. ТН10-40В001 and ТН10-40В002 should be lower than 0,25м. - ТН10-40S001 gate valves should be opened - Primary pressure should be higher than 1,0 МPа Whereas, in algorithm No. THSNOEE010. The 3rd condition is not required for closing the gate valve Nos. ТН15-45S021 |  |
| Reply 24 | FSAR: 7 FSAR Section 6.3.1 |
| Reply: At present the process algorithms are being checked on the mathematical model of the power unit. Then the algorithms check up is planned on the BNPP-1 power unit actual equipment during the functional testing and hot running-in. Based on these activities results the actual algorithms variant will be developed, which will be introduced in to the final FSAR version |  |
| DECISION No 26 | FSAR: 7 FSAR Section 6.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be submitted in Appendix A, B, C and D to chapter 7 of the FSAR Rev. 1 (see reply 15) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 27 | FSAR: 7 FSAR 7.7.1.4.2.1 |
| Recommendation: The subsystem of MCDS should correctly and completely be listed, as - In-core instrumentation system ICIS; - Vibration monitoring subsystem VMS; - Primary coolant leak monitoring subsystem LMS, consisting of the followings: - Acoustic leak monitoring subsystem ALMS - Moisture leak monitoring subsystem HLMS - Loose and loosely parts detection system; - Complex analysis server CAS; Finally, clarification should be made if "secondary leak monitoring system" is a part of MCDS or not. Figure 7.7-7 "Functional structure of the MCDS" cannot be accepted and so it is rejected. The figure should be in accordance with the last revision of the functional structure of MCDS (copy is attached). All the coding should be indicated |  |
| Reply 25 | FSAR: 7 FSAR 7.7.1.4.2.1 |
| Reply: The comment is accepted. This paragraph will be given in the following wording "The MCDS includes the following systems: - in-core instrumentation system (ICIS); - vibration monitoring subsystem (VMS); - primary coolant leak monitoring system (LMS) consisting of the following: - acoustic leak monitoring subsystem (ALMS); - humidity leak monitoring subsystem (HLMS); - loose and loosely parts detection system (LPDS); - system of integrated analysis (SIA); - secondary leak monitoring system (SLMS-2)"; Functional structure of the MCDS as given in figure 7.7-7 will be replaced according to Appendix |  |
| DECISION No 27 | FSAR: 7 FSAR 7.7.1.4.2.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comments are accepted and all the changes will be applied in the FSAR Rev. 1. It will be specified that "secondary leak monitoring system (SLMS-2)" belong to what system of APCS in the FSAR Rev. 1 Appendix to Reply No. (subsection: 7.7.1.4.2.1) Помещение систем безопасности – Safety system room ШКО – SHKO ПТК НУ – SHC-LL ЛС НУ – LN-LL ПТК ВРШД – SHC-ICND АСУЗ- УСБИ – ECPS - ESFAS ПТК-З (1 компл.) (2У) – SHC-P (set 1) (2У) ПТК-З (2 компл.) (2У) – SHC-P (set 2) (2У) Датчики для формирования ……- Sensors to generate the protection signals by in-core parameters. Safety class - (2У) 1 канал – Channel 1 Помещение систем нормальной эксплуатации – Normal operation system room СВБУ (коммутатор РО) – TLS-U (RC commutator) СК-НУ- SC-LL Коммутаторы – СВРК (3Н) – Commutators ICIS (3Н) Клеммный шкаф – Terminal cabinet ПТК-ИУ (3Н) –SHC-IC (3Н) ВК (3Н) – CC (3Н) КЭ СУЗ (СГИУ) – CPS ES Датчики Технологического ….Sensors of RP process control, signals from interfacing systems СВРК – ICIS Коммутаторы – СКУД (3Н) – Commutators – MCDS (3H) СОТТ-2 – SLMS-2 СКВ – VMS СКВ ГЦНА – RCPS VMS СКТ –LMS САКТ (ЗН) – ALMS (3H) СКТВ (ЗН) – HLMS (3H) СОСП – LPDS СКА – SIA АКНП - NFME АК (ВКУ) – ME(Internals) Датчики – Sensors Системы диагностики – Diagnostic systems Примечания: Notes: 1) communication lines of class 2 2) SHC of VMS, LPDS, SIA, SC-LL, SHC-ICND relate to safety class 4 as per OPB 88/97. 3) MCDS LN consists of MCDS commutators and communication lines from them to the commutators of ICIS, VMS, LPDS, SIA. 4) SC-LL shall be connected to ICIS during commissioning work as well as during operation (if needed) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 29 | FSAR: 7 FSAR 7.7.1.4.3.1, 2nd paragraph |
| Recommendation : The valves indicated as 30 up to 100% of nominal power are in contradiction with those indicated in document "Materials on design revision", page 3 (letter 7717-12/04-5270 dated 03.09.04), please clarify |  |
| Reply 27 | FSAR: 7 FSAR 7.7.1.4.3.1, 2nd paragraph |
| Reply: The comment is accepted. A range of generating the signals of core protection by local parameters for the EP-PP system (DNBR on fuel rod surface is below the permissible value, maximum linear heat rate on fuel rod surface is above the permissible value) will be written down as “ from 40 up to 102 % ” |  |
| DECISION No 29 | FSAR: 7 FSAR 7.7.1.4.3.1, 2nd paragraph |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments.. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 30 | FSAR: 7 FSAR 7.7.1.4.3.2, Item 2 |
| Recommendation : UI-174P03 should be changed to UI-174R03 |  |
| Reply 28 | FSAR: 7 FSAR 7.7.1.4.3.2, Item 2 |
| Reply: The comment is accepted. "UI-174P03" will be changed to "UI-174R03" |  |
| DECISION No 30 | FSAR: 7 FSAR 7.7.1.4.3.2, Item 2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted and will be included in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 31 | FSAR: 7 FSAR 7.7.1.4.3.3, page 7-222, second paragraph |
| Recommendation : The explanation’s given in this section concerning types of NTMCs cannot be found in APCS contract design documents, please clarify |  |
| Reply 29 | FSAR: 7 FSAR 7.7.1.4.3.3, page 7-222, second paragraph |
| Reply: Design of reactor plant V-446 makes provision for installation of 54 NTMCs of three types. All the 54 NTMCs incorporate 7 SPNDs as the neutron indicators and differ only in the number of thermocouples (from 3 to 5 pieces) and their arrangement (to measure coolant temperature in different points along the FA height and under the reactor top head). The NTMC of the first type (46 pieces) there are 3 thermocouples. One thermocouple is intended to measure coolant temperature at the FA inlet and two other – to measure coolant temperature at the FA outlet. In the NTMC of the second type (4 pieces) there is the fourth thermocouple to measure coolant temperature under the reactor top head. In the NTMC of the third type (4 pieces) there are 5 thermocouples intended to signal that water-steam mixture is forming under the reactor top head and temperature is coming to 1200 С under accident conditions (the signals from these thermocouples arrive into the specialized devices which are not a part of the MCDS). 2 thermocouples are reference thermocouples. |  |
| DECISION No 31 | FSAR: 7 FSAR 7.7.1.4.3.3, page 7-222, second paragraph |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Reply is discussed and accepted. The information and full description with respect to level measurement including 2 reference thermocouples will be included in the FSAR Rev. 1 section 7.5 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 32 | FSAR: 7 FSAR 7.7.1.4.3.5 |
| Recommendation : In this section, 6U height, IOU and “PSCD” in figure 7.7-8 should be clarified. What are they? |  |
| Reply 30 | FSAR: 7 FSAR 7.7.1.4.3.5 |
| Reply: Height 6U is 245,35 mm. IOU - input-output unit. PSCD - power supply control device. The device UI-174R has been implemented using a principle "master-slave" and consists of two control units CU (master), each of them ensures control of separate trunk, input-output unit with an IOU object (slave) that have an interface with redundant trunk |  |
| DECISION No 32 | FSAR: 7 FSAR 7.7.1.4.3.5 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Comment was discussed and reply accepted and it will consider in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 33 | FSAR: 7 FSAR, 7.7.1.4.3.6, Page 224, last paragraph |
| Recommendation : “It ensures a delay of more than 0.3 S” shell be clarified, and please include “RTT” in the list of abbreviations |  |
| Reply 31 | FSAR: 7 FSAR, 7.7.1.4.3.6, Page 224, last paragraph |
| Reply: The comment is accepted. It should be written down "not more than 0,3 s". RTT - resistance temperature transducer |  |
| DECISION No 33 | FSAR: 7 FSAR, 7.7.1.4.3.6, Page 224, last paragraph |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 34 | FSAR: 7 FSAR, Page 7-230 |
| Recommendation : The technical characteristics of pressure pulsation sensor should be verified. Referring to the technical characteristic of high-temperature piezo accelerometer, please indicate the following parameters: Working range of sensor measurement Mode of operation Time taken for signal receiving |  |
| Reply 32 | FSAR: 7 FSAR, Page 7-230 |
| Reply: The comments are accepted. Technical characteristics of pressure oscillation transducer: Number of transducers; 12. Conversion factor, mV/V/MPa; 0,16. Range of working frequencies, Hz; from 0 to 250. Range of working pressure, MPa; from 0 to 25. Range of pressure oscillations measured, MPa; from 0,02 to 0,10. Allowable relative deviation of conversion factor under static condition, %, not more than; ± 3. Range of working temperatures, °С; from 5 to 320. Length of cable communication lines up to the carrier frequency amplifier, m; not more than 200. Technical characteristics of high-temperature piezoaccelorometer: Sensitivity, pC/m/s2; 100. Frequency range (non-uniformity ±1dB), Hz; from 2 to 3000. Resonance frequency, kHz, more than; 9. Working range of temperatures, °С; to 400. Amplitude range, g; ± 1000. Protection extent; IP 68. |
| DECISION No 34 | FSAR: 7 FSAR, Page 7-230 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 35 | FSAR: 7 FSAR, Page 7-231 |
| Recommendation : The device IMD is not in the list of abbreviation and devices components mentioned in this page UII-01, UII-02, PT-14 etc. cannot be found in the APCS CDDs. In this respect, it is advised to have the structural diagram of the subsystems and the list of hardware units in accordance with the latest design revision |  |
| Reply 33 | FSAR: 7 FSAR, Page 7-231 |
| Reply: The comment is accepted |  |
| DECISION No 35 | FSAR: 7 FSAR, Page 7-231 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The description of IMD and the structural diagram of the VMS and the list of hardware units in accordance with the latest design revision will be provided in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 36 | FSAR: 7 FSAR, Page 7-236 |
| Recommendation : The response time for SHC-HLMS to detect leakage has been mentioned "not more then 5 minutes", but please note that in doc "Materials on design revision" (letter No.7717-12/04-5270 dated 03.09.04), the time is not more then 3 minutes, please clarify |  |
| Reply 34 | FSAR: 7 FSAR, Page 7-236 |
| Reply: The information delay at leakage occurrence shall not exceed 3 min, leak spot detection and its magnitude estimate shall not exceed 10 min |  |
| DECISION No36 | FSAR: 7 FSAR, Page 7-236 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment was discussed and reply is accepted. The FSAR Rev. 1, will be corrected according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 37 | FSAR: 7 FSAR, 7.7.1.4.6 |
| Recommendation: In order to visualize the structure of LPMS, please include LPMS block diagram and the location of the sensors on the RCC. Please mention safety class of LPMS |  |
| Reply 35 | FSAR: 7 FSAR, 7.7.1.4.6 |
| Reply: Terminal box No.1 Sensor AR63 No.1 Preliminary amplifier No.1 SHC (IMD) • • • • • • Sensor AR63 No.5 Preliminary amplifier No.5 • • Terminal box No.4 • • Sensor AR63 No.16 Preliminary amplifier No.16 • • • • • • Sensor AR63 No.20 Preliminary amplifier No.20 Device of striking test blows Pulse hammer No.1 Power supply station Pulse hammer No.2 Control module Pulse hammer No.3 Pulse hammer No.4 Figure 1 – Structure diagram of LPMS Pulse hammers RCPS No.1 RCPS No.4 RCPS No.2 RCPS No.3 SG SG SG SG Sensors visible hidden Figure 1 – Arrangement of LPMS on the reactor plant equipment The LPMS is referred to the normal operation systems. The LPMS hardware is referred to safety class 4.. ПГ - SG ГЦНА - RCPS Датчики - sensors Импульсные молотки – pulse hammers Видимые - visible Скрываемые оборудованием – hidden |
| DECISION No 37 | FSAR: 7 FSAR, 7.7.1.4.6 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 38 | FSAR: 7 FSAR 7.7.1.4.7 |
| Recommendation: For the purpose of consistency with CDDs, please change "System of integrated analysis" to "Comprehensive Analysis Server"(CAS). Finally, please explain for not including "Secondary Leak Monitoring System"-SLMS2. |  |
| Reply 36 | FSAR: 7 FSAR 7.7.1.4.7 |
| Reply: We consider it inappropriate to change the terminology accepted in the MCDS design and corresponding to the regulatory documentation of Russian Federation (PNAE G-01-011-97) at this stage because such a procedure will result in revising the MCDS and APCS design. Description of secondary circuit leak detection system SOTT-2 is given in Chapter 3 FSAR |  |
| DECISION No 38 | FSAR: 7 FSAR 7.7.1.4.7 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: A description of SOTT-2 will be provided in Revision 1 of the FSAR-07 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 39 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: : Page 7-10: Term DDRH should be changed to DDLH. Furthermore, in this table LPM (Loose part monitoring system) and Refueling machine control system should be introduced |  |
| Reply 37 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Comments are accepted. Table 7.1.1-1 has been revised and attached |  |
| DECISION No 39 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1. Name of the system; Class as per OPB (safety class); Equipment design; Note. As per OPB; As per seismic categories. 1; 2; 3; 4; 5. 1. CPS-ESFIP. - transducers*; 2NC; 2; 1. - ISPE; 2 NC; 2; 1. - NFME; 2 NC; 2; 1. -PPPE; 2 NC; 2; 1. - SLPE; 2 NC; 2; 1. - DDLH; 3 NC; 3; 2b; Performs information and service functions only. 2. CPS EE. - ShAK; 2NC; 2; 1. - ShPUI; 2NC; 2; 1. - ShP6M; 2NC; 2; 1. -ShP6M1; 2NC. 3. ESFAS. - transducers *; 2 NC; 2; 1. - RCD; 2 NC; 2; 1. - PPPE; 2 NC; 2; 1. - SLPE; 2 NC; 2; 1. - TPTS52, TPTS53; 2 NC; 2; 1. - TPTS gateway; 3 NC; 3; 2b; Performs information and service functions only. 4 MCR, ECR consoles and boards with installed monitoring, control and alarm hardware; 2 NC; 2 3; 1 2b; For safety panels For normal operation panels. 3NC. 5. PP (PP1, PP2, APP3, power limitation controller); 3 NC; 2; 1; Equipment class is enhanced since it is implemented in the same cabinets and with the same transducers as the emergency protection system. - transducers *; 3 NC; 2; 1. - ISPE; 3 NC; 2; 1. - NFME; 3 NC; 2; 1. - PPPE; 3 NC; 2; 1. - SLPE; 3 NC; 2; 1. 6. MCDS***. - SHW-P; 2C; 2; 1; Сlass is enhanced, since ICND is arranged in ZK building and has an interface with SHW. - SHW - ICND; 4N; 2; 1. - SHW- IC, SHW - UL; 3N; 3; 2b. - SHW - LMS; 3N; 3; 2b. - SHW - LPM; 4N; 4; 3. - SHW-VMS; 4N; 4; 2b. |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 40 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-21: The term "generation of 36 days record of the safety system conditions" which had been mentioned in the PSAR is in contradiction with the features that has been implemented after manufacturing of IORPS. In this respect AEP is requested to revise the storage volume of IORPS and reduce it to 18 days (based on the results of IORPS storage time) |  |
| Reply 38 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Comments are accepted. The wording of the item 7.1.1.6.1 (Page 7-21): " -generation of 36 days record of the safety system conditions" should be replaced by the following: "- registration of the information in the mode of the circular archives within 70 hours at flow not less than 660 changing signals per second" |  |
| DECISION No 40 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 including description during normal operation and accident situation especially with respect to the input signals of IOPRS. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No.41 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-26: Considering the fact till now, no agreement have been met regarding omitting of hardwired link between two FMs of actuation part of safety systems (ESFAS), it should be indicated in the page 7-26 that for the FMs related to ESFAS, both of digital link (like RS232/RS485) and hardwired link are available |  |
| Reply 39 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Comments are not accepted By CS.TAG.ASE.00.00.0653 technical decision, approved by the OCE, NPPD and NPPD, the VNIIIA proposal regarding omitting of hardwired communication was accepted. In line with this decision the 7.3.1.3.8 wording would be revised |  |
| DECISION No 41 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Conclusions from the Technical Report on the use of digital channels in the ESFAS software-hardware complexes will be added in revision 1 of the FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 42 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation : Page 7-26: AS you promised in the stage of РSAR reviewing, the procedure of allocating of time tagged data which are used for acquisition of signals and provision of I&C errors, should be explained for the TPTS functional modules |  |
| Reply 40 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Item 7.1.1.9.5 should be added by the following: The special server connected to astronomical clock, having the satellite aerial is the universal time source in the I&C. All sluice computers are connected to a synchronizing server through local common station network, cooperating on NTP protocol. Interaction is performed by an exchange of timing sendings and an estimation of a divergence of hours with use of a statistical filtration. Accuracy of time synchronization in sluice computers is ± 5 ms. Time correction in sluice computers is made with the specified periodicity. The server independently from each other synchronizes each sluice computer. Sluice computers intended for TPTS synchronization, periodically send synchronizing telegrams through the system trunk. Synchronizing telegrams are transmitted in a broadcasting mode simultaneously to all TPTS racks, connected with sluice computer through TPTS system trunk. Synchronizing telegrams are sent with the set periodicity (each 16 s). Thus, the accuracy of hour’s synchronization in control modules of TPTS 53.1332 interfaces is ± 5 ms. Cyclic character of collecting and processing of entering signals in functional modules of SHW I&C NOS (on TPTS base) results in an error of a time label assignment to events in TPTS 53.1332. This error is actually equal to a cycle time of the functional module and makes for the discrete signals the time from 10 ms up to 130 ms at acyclic signals transmitting. At registration of the sequence of events (discrete signals) the assignment of different time labels is guaranteed, allowing to establish the sequence of events, if time between them is not more than 130 ms |  |
| DECISION No 42 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be introduced in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 43 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-26: Considering the fact that functional modules related to electronic part of turbine governor system are a part of TPTS functional modules, three modules namely emergency automation module, power amplifier module and frequency conversion module should be described in the table 7.1.1-4 |  |
| Reply 41 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Comments are accepted. Table 7.1.1-4 should be added by the following information: Table 7.1.1-4 TPTS53 functional modules Designation; Name; Function, brief technical characteristics. TPTS52.1412; Emergency automation module; Designed for emergency control of TG turbine power in the automation systems based on TPTS53 The module is applied in a set with UM power amplifier. TPTS52.1941; Power amplifier module; TPTS52.1941 power amplifier module is designed for the control signal generated in the TPTS52.1412 emergency automation module and operates for the load (electromagnetic transducer). TPTS52.1724-01; Frequency conversion module; Designed for signals conversion from rotation frequency sensors into DC voltage values corresponding to rotation frequency, rotation frequency change rate, and for commands generation. |
| DECISION No 43 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 44 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-124: Because of the fact that actuation time response in PSAR was introduced based on the Balakovo reference plant, roots of difference between the actuation response times mentioned in item 7.3.1.3.8 of PSAR and FSAR should be clarified whether the reference plant have changed. Furthermore, as it is indicated for response time of ESFAS in case of using of wire communication and digital bus; it is obvious that a.m. time response in case of using hardwired communication is lower than digital bus. So, we draw your attention to the fact that omitting of hardwired communication in ESFAS TPTS modules will increase the availability of ESFAS and for this purpose availability of both of digital and hardwired bus for TPTS modules of ESFAS cabinet is necessary |  |
| Reply 42 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Comments are not accepted By CS.TAG.ASE.00.00.0653 technical decision, approved by the OCE, NPPD and NNSD, the VNIIIA proposal regarding omitting of hardwired communication was accepted. In line with this decision the 7.3.1.3.8 wording would be revised. |  |
| DECISION No 44 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Conclusions from the Technical Report on the use of digital channels in the ESFAS software-hardware complexes will be added in revision 1 of the FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 45 | FSAR: 7 FSAR Section 7.4.1.4 |
| Recommendation: Page 7-150: Lack of information regarding I&C-T and I&C-TG is obvious. So, contractor iskindly requested to provide general description of the a.m. systems in case of software and hardware after item 4.1.4 |  |
| Reply 43 | FSAR: 7 FSAR Section 7.4.1.4 |
| Reply : Comments are not accepted FSAR gives general description of the I&C-TС, I&C-TG functions and structure principles which have not changed since the РSAR stage. Guide 1-70 does not require more detailed information |  |
| DECISION No 45 | FSAR: 7 FSAR Section 7.4.1.4 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In Revision 1 of the FSAR it will be mentioned that I&C-TC and I&C-TG have a similar architecture with I&C-RC, and a reference to item 7.4.1.3 will be provided |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 47 | FSAR: 7 FSAR Section 7.4.1.4 |
| Recommendation : Page 7-152: Clarification should be given regarding the reasons for increasing of channel response time (from remote control device to low voltage switchgear inlets) from 0,3 seс tо 0,5 seс comparing with РSAR |  |
| Reply 45 | FSAR: 7 FSAR Section 7.4.1.4 |
| Reply: In contrast to РSAR, the information on the SHW testing results obtained at the manufacturing plant (VNIIIA) is presented in the FSAR |  |
| DECISION No 47 | FSAR: 7 FSAR Section 7.4.1.4 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: FSAR Rev. 1, item 7.4.1.6, last paragraph will be completed as follows: “Increase of time from 0.3 s to 0.5 s, which does not contradict with the TA for APCS is caused by the requirements of software-hardware complex protection against interference. According to the tests results the time of input signal processing is doubled in order to prevent false actuations in input circuits” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| АЕОI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 48 | FSAR: 7 FSAR Section 7.6.1 |
| Recommendation: Page 7-183: Concept of signaling between fire alarm controllers (JBE), special equipment of fire alarm (JBA), powder firefighting (JBW) and fire extinguishing controller (JBW) in the other main buildings (except ZK1, ZK2) should be shown (including protocol of communication between them and fire alarm servers installed in MCR) in a new diagram. Furthermore, if the serial links are considered for a.m. purpose, clarification should be given regarding availability of AFPS in case of loss of a.m. serial links |  |
| Reply 46 | FSAR: 7 FSAR Section 7.6.1 |
| Reply: Item 7.6.1.7.1 should be added by the following: “Exchange of information between fire alarm controllers (JBE) and fire extinguishing controllers (JBW) of one set is performed through duplicated digital communication channel RS485. Communication between the sets is executed for information presentation on AFPS operation at the MCR rear circuit and provided by fibre-optic cable through the special equipment sets (11, 12, 13, 14 JBA01)” |  |
| DECISION No 48 | FSAR: 7 FSAR Section 7.6.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and will be included in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments.. |  |

OCE comments on Appendix B2 (to MoM to FSAR-7 (Rev. 0) dated 03-13.03.07, Tehran, LIST OF REPLIES TO OCE LETTER No.LTR-13070-65287 DATED 18.02.06)

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 2 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: In accordance with reply 1.6 of the supplement No. 1 of the PSAR chapter 7, the following text should be added where it has not been given in FSAR. - "NPP Seismic Design Code" PNAE G-5-006-87 - "Nuclear Power Generator Facilities Code "PNAE G-5-008-87 |  |
| Reply 2 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: The text of section 7.1.2 in page 7-39 shall be added: - ""NPP Seismic Design Code" PNAE G-5-006-87 - "Nuclear Power Generator Facilities Code "PNAE G-5-008-87 |  |
| DECISION No 2 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 3 | FSAR: 7 FSAR Section 7.2, Table 7.2-2 |
| Recommendation: "Primary to secondary leak within SG Dnom < 100 mm" is mentioned as initiating event in supplement No.1 of PSAR, Chapter 7 causing actuation when "pressure in steam line (any) more than 7.84 MPa", whereas it is not included in table 7.2.2 of FSAR |  |
| Reply 3 | FSAR: 7 FSAR Section 7.2, Table 7.2-2 |
| Reply: The comment is accepted. In Table 7.2-2 for the condition “Pressure in steam line (in anyone) is more than 7,84 MPa” a respective mark will be made in column “Primary-to-secondary leak within SG (Dnom < 100 mm)” |  |
| DECISION No 3 | FSAR: 7 FSAR Section 7.2, Table 7.2-2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 4 | FSAR: 7 FSAR Section 7.2, Table 7.2-2 |
| Recommendation: "Spectrum of steam line breaks inside and outside the containment" is mentioned as initiating event in supplement No. 1 of PSAR, Chapter 7 causing actuation when "Excessive pressure in the containment is more than 0.29MPa", whereas it is not included in Table 7.2.2 of FSAR |  |
| Reply 4 | FSAR: 7 FSAR Section 7.2, Table 7.2-2 |
| Reply: “SB LOCAs (break of pipeline Dnom < 100)”, “LB LOCAs (break of pipeline Dnom>100)”, “Spectrum of steam line break inside and outside the containment” are the initiating events for EP initiation criterion “Excessive pressure in the containment is more than 0,29 MPa”. For EP initiation criterion “Excessive pressure in the containment is more than 0,29 MPa” the marks will be made in the respective columns of Table 7.2-2 FSAR |  |
| DECISION No 4 | FSAR: 7 FSAR Section 7.2, Table 7.2-2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 5 | FSAR: 7 FSAR Section 7.2, Table 7.2-7 |
| Recommendation: In table 7.2.7 of FSAR the column for "maximum error" is not mentioned, while it exists in supplement No. 1 of PSAR, Chapter 7 |  |
| Reply 5 | FSAR: 7 FSAR Section 7.2, Table 7.2-7 |
| Reply: In Table 7.2-7 there is no column for maximum errors in connection with the fact that technical measures are provided to assure the reliability of system of ventilation and air-conditioning of primary transducer rooms. The temperature in rooms is maintained within the range of ± 2º С. In Chapter 7.2 no changes will be made |  |
| DECISION No 5 | FSAR: 7 FSAR Section 7.2, Table 7.2-7 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Additional materials will be provided during the commissioning license stage.(See replies 62 to NNSD comments) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 6 | FSAR: 7 FSAR Section 7.2, Table 7.2-7 |
| Recommendation: In reply No. 2.9 of supplement No. 1 of PSAR, Chapter 7, it is mentioned that three couples of pulse tubes are provided for each steam generator: first couple is for RTS set 1, the second is for RTS set 2, and the third is for start-up of emergency feedwater pumps in respective channel of ESFAS. Whereas the figure 7.2-7 of FSAR is not compatible to this text. Please clarify |  |
| Reply 6 | FSAR: 7 FSAR Section 7.2, Table 7.2-7 |
| Reply: In figure 7.2-7 FSAR the connection layout of impulse lines from steam generators to primary transducer rooms is given in the scope of reactor trip system considered in Chapter 7.2. The impulse lines from steam generators, intended for start-up of emergency feedwater pumps in the respective ESFAS channel are considered in Chapter 7.3 FSAR. The connection layout of impulse lines for indicators of reactor trip system is according to the design. We suggest to leave figure 7.2-7 as it is |  |
| DECISION No 6 | FSAR: 7 FSAR Section 7.2, Table 7.2-7 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: See Appendix A. Sheet A17, A23, A29, A35 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 7 | FSAR: 7 FSAR Section 7.3.1.2.9, 7.3.2.11, 7.3.2.12 |
| Recommendation: In reply 3.10 of supplement No. 1 of the PSAR, Chapter 7, it has been mentioned that the following items will be added or deleted in FSAR, whereas they have not been modified. а) In item 7.3.2.11, the following is to be added after para. 1 "According to items 190-191 of safety series …". b) In item 7.3.2.12, para. 1 is to be deleted. c) In item 7.3.1.2.9, sentence appearing at the end of para. 2 will be deleted. "are introduced to the side opposite to safety till the moment of unit cool-down" |  |
| Reply 7 | FSAR: 7 FSAR Section 7.3.1.2.9, 7.3.2.11, 7.3.2.12 |
| Reply: In item 7.3.2.11 the following is to be added after para 1: - "According to Item 190-191 of the Safety Series No.75-INSAG and IAEA-TECDOC-801, the plant operating staff are provided with appropriate safety equipment, instrumentation and operating procedures for to and control of accidents within the design basis. Design is such that abnormal developments are first met automatically by the restoration of normal conditions by means of the feedback characteristics of neutronic and process control. These are backed up by the normal capability for shutdown, continued cooling and protection against the release of radioactive materials. Further protection is available through automatic actuation of engineered safety systems. By means of such measures, any onset of abnormal behavior would be dealt with automatically by appropriately designed systems for at least a predetermined period of time ("decision interval"), during which the operating staff could assess systems, review possibilities and decide on a subsequent course of action for conditions not adequately responded to by the automatic functioning of plant systems. The design makes provision for diagnostic aids and symptom based emergency procedures for use in these circumstances. Typical decision intervals for operator action for future plants are 30 minutes or longer, depending on the system or situation. - The ability of systems and operators to control or halt the progression of addressed severe accidents is considered explicitly in the plant design for future plants. Controls for such sequences need not be automatic. And equipment used for response need not be safety grade. - The role of operator in circumstances is to ensure that all systems have responded correctly to the abnormal situation, to diagnose the abnormal event in a manner, to intervene if required and restore critical safety functions. Instrumentation and information display systems support these roles, including safety Parameter Display Systems (SPDS) and other sophisticated computer aids to help the operating staff trend and diagnose the evolution of accidents within the design basis. - Extracts from IAEA publication Rev. 4/1996-11-27 "Report of TCM on the implementation of defense-in-depth for new generation of NPPS" state that "Various design enhancements, including increased design margins, improvements in instrumentation, control and protection systems, etc., lead to the possibility of prolonging the grace period for the necessary intervention of operators. For future reactors a grace period of 30 minutes is now considered feasible and appropriate, a significant improvement over many previous stages. The concept of 30 minutes (design bases for BNPP-1) grace period is itself an application of defense-in depth philosophy, because it relies on the designer to take into account potential shortcomings operations and procedures, while at the same time relying on the operator, in a more relaxed mode with more time to evaluate actions, to take into account potential malfunctions in the design (e. g., in automatic responses) should they occur. This positive outcome is ensured by applying grace periods to the design of automatic control systems such that no human action should be necessary for that period, as opposed to no human action being allowed for that period. Design are implemented such that plant personnel can initiate safety functions and initiate necessary actions to deal with circumstances that could prejudice safety, but shall not be able to negate correct safety system action." - Para 2:in item 7.3.2.11 is to be revised in the following manner - According to the Russian standards in operation of protections starting SS a prohibition against operators intervention is introduced for 30 min. Considering the abovementioned explanations and by the request of the Iranian Party, the given time prohibition is not fulfilled. Due to this a possibility is provided in the design to remove the prohibition by an operator. Operators action on SS mechanisms under accident conditions shall be stipulated in special instructions. All protections, acting upon SS actuation, are made non-disconnectable. - In item 7.3.2.12 para 1 is to be deleted - In item 7.3.1.2.9, sentence appearing at the end of para 2, will be deleted "are introduced to the side opposite to safety till the moment of unit cooldown" |  |
| DECISION No 7 | FSAR: 7 FSAR Section 7.3.1.2.9, 7.3.2.11, 7.3.2.12 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 8 | FSAR: 7 FSAR Section 7.3.1.3 Тable 7.3.1.3-2 |
| Recommendation: According to the supplement No. 1, Chapter 7 of the PSAR, the following corrections shall be applied in table 7.3.1.3.2 of FSAR: - In item 3 of table 7.3.1.3.2 "Secondary leak (prior or after MSIV)" should be changed to "Secondary leak after MSIV" "emergency cool-down system: RS, RA" should be changed to "normal operation system: RR, RA (standby RS, RA)" "emergency cool-down system RS, RA" should be changed to "normal operation system RR, RA (standby, RS, RA)" - In item Nos. 4 & 5 of the table 7.3.1.3.2, please add the following underlined items |  |
| Reply 8 | FSAR: 7 FSAR Section 7.3.1.3 Тable 7.3.1.3-2 |
| Reply: Comments are accepted Table 7.3.1.3.2 is corrected and given below. Initial events; Safety functions provided; Actuated systems; Automatic actuation; Remarks. 3 Secondary leak (in isolable part of the system); RP cooldown through the primary system; LP ECCS and TH10-40 smooth cooldown line; Operator control. RP cooldown through the secondary system; Normal operation system RR RA (standby RS, RA); Operator control. Residual heat removal through the secondary system; Normal operation system RR RA (standby RS, RA); BRU-A opening P2>7.17 MPa; BRU-A closing P2<6. 3M Pa; - SG safety valve opening P2>8.23MPa - SG safety valve closing P2<6.86MPa Pump start-up and opening of emergency feedwater line valves LSG<-900mm. Steam generators isolation from the MSH; MSIV RA; - closing four MSVs Ts(1c-2c)>75 oC and P2<4.41 MPa +T1c>150oC. 4 secondary circuit leak prior to MSIV; MSH isolation from damaged SG;; - MSIV RA;; - damaged SG MSIV closing Ts(1c-2c)>75 oC and P2<4.9 MPa +T1c>150oC. - Prevention from primary coolant sub-cooling 1: 1) stop of forced coolant circulation in damaged SG loop; 2) stop of RL feedwater supply into damaged SG; 3) stop of RS feedwater supply into damaged SG; RP cooldown through the primary system Residual heat removal through the secondary system;; - RCP YD;; - damaged SG RCP trip Ts(1c-2c)>75 oC and P2<4.41 MPa +T1c>150oC. - RL system delivery line valves; - RS system delivery line valves;; - valves closing in feedwater supply line into damaged SG Ts(1c-2c)>75 oC and P2<4.41 MPa +T1c>150oC - valves closing in the emergency feedwater supply line into damaged SG Ts(1c-2c)>75 oC and P2<4.41 MPa +T1c>150oC. ECCS pumps TH10-40; Operator control. Normal operation cool-down system RR, RA (standby RS, RA);; BRU-A opening P2>7.17 MPa; BRU-A closing P<6. 3M Pa; - SG safety valve opening P2>8.23MPa - SG safety valve closing P2<6.86MPa Pump start-up and opening of emergency feedwater line valves LSG<-900mm. RP cooldown through the secondary system; Normal operation system RR, RA (standby RS RA);; Operator Control. 5 Primary-to-secondary leak; - damaged SG isolation from MSH; - stop of damaged SG pressure increase Damaged SG isolation from atmosphere - pressure rise and decrease limitation in the primary circuit Primary volume control system RP cool-down through the secondary system RP cool-down through the primary system; - MSIV RA; - BRU-A, SG safety valve, RA -BRU-K SF - BRU-A, RA; - volume control system TA (standby TW) HP ECCS - TH 15-45 - Unaffected SGs and systems RR and RA (standby RS and RA) ECCS pumps - TH10-40; Operator control BRU-A opening P2>7.15MPa; - SG opening P2>8.23MPa; -SG safety valve closing P2<6.86MPa; Operator control Operator control Operator control Operator control Operator control. |
| DECISION No 8 | FSAR: 7 FSAR Section 7.3.1.3 Тable 7.3.1.3-2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be corrected in the English text |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 9 | FSAR: 7 FSAR Section 7.5.2.3 |
| Recommendation: According to the supplement No.1 of PSAR, Chapter 7, the paragraph 7.5.2.3 should be completed as follows: "According to Guide 1.97, the types and categories of parameters used in Table 7.5.2.3-1 are as follows: Type A- Parameters that provide initial information that is required for the operator to take manual actions for which automatic control is not provided that are necessary to ensure that the safety system performs its functions during design-basis accidents; Type B- Parameters that provide information on safety functions fulfillment; Type C- Parameters that provide information on possible barrier failures or actual failures; Type D- Parameters that provide information on the functioning of personal protection means and other systems, important to safety. Type E- Parameters that identify the scope of activity releases and further assessment of such releases; Category 1- Key parameters, which are subject to the strictest instrumentation requirements (RP safety systems parameters); Category 2- Parameter, which are subject to less strict instrumentation requirements for support safety systems as well as other safety-related systems); Category 2- Parameters, the changers of which are not subject to any specific requirements; for their measurement serial industrial instruments may be used" |  |
| Reply 9 | FSAR: 7 FSAR Section 7.5.2.3 |
| Reply: Comment is accepted. Paragraph 7.5.2.3 shall be completed by the recommended above text "According to Guide 1.97, the types and categories of parameters used in Table 7.5.2.3-1 are as follows: Type A- Parameters that provide initial information that is required for the operator to take manual actions for which automatic control is not provided that are necessary to ensure that the safety system performs its functions during design-basis accidents; Type B- Parameters that provide information on safety functions fulfillment; Type C- Parameters that provide information on possible barrier failures or actual failures; Type D- Parameters that provide information on the functioning of personal protection means and other systems, important to safety. Type E- Parameters that identify the scope of activity releases and further assessment of such releases; Category 1- Key parameters, which are subject to the strictest instrumentation requirements (RP safety systems parameters); Category 2- Parameter, which are subject to less strict instrumentation requirements for support safety systems as well as other safety-related systems); Category 2- Parameters, the changers of which are not subject to any specific requirements; for their measurement serial industrial instruments may be used" |  |
| DECISION No 9 | FSAR: 7 FSAR Section 7.5.2.3 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 10 | FSAR: 7 FSAR Section 7.7 |
| Recommendation: Based on the PSAR supplement No.1, Chapter 7, the attached diagram shall be added to the FSAR, whereas it has not been given in FSAR, please add it |  |
| Reply 10 | FSAR: 7 FSAR Section 7.7 |
| Reply: Figure 7.7-3.1 given in Supplement No.1 to PSAR is replaced in FSAR with figure 7.7-5, which is more informative, in our opinion, because it contains the additional detailed information on interaction of APC with the adjacent systems. |  |
| DECISION No 10 | FSAR: 7 FSAR Section 7.7 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Figure will be corrected (shadows will be removed) in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 11 | FSAR: 7 FSAR Section 7.4 |
| Recommendation: In page No. 7-148 of the FSAR Chapter 7, Figure 7.4-6, please note the followings: a) The text "Formation of logic for the introduction of protection" which is directed to "R", shall be changed to "formation of logic for getting out of protection". b) Please specify the reference point of "signal automatic introduction of protection" |  |
| Reply 11 | FSAR: 7 FSAR Section 7.4 |
| Reply: Figure 7.4-6 shall be changed. Figure 7.4-6 Protection introduction/withdrawal unit |  |
| DECISION No 11 | FSAR: 7 FSAR Section 7.4 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and figure shall be corrected in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 12 | FSAR: 7 FSAR Section 7.4 |
| Recommendation: Concerning the Figure No. 7.7-4 of the FSAR (sheet No. 7-202), please consider our comments as follows: a) Please add the figure's title as: "Structure of sets of preventive protection equipment corresponds to the structure of reactor shutdown". b) Connection between PPPE (KTSK-01R) and PG has been omitted, please add it. c) Comparing figure No. 7.7-2 of the supplement No. 1 of the PSAR, Chapter 7 with figure No. 7.7.4 of the FSAR, please use the same abbreviations such as PPPE, NFME, etc. in figure 7.7.4 |  |
| Reply 12 | FSAR: 7 FSAR Section 7.4 |
| Reply: Figure 7.7-4, considering the given comment to English version of FSAR, is enclosed. Note - The structure of the sets of preventive protection equipment correspond to the structure of reactor shutdown system Figure 7.7-4 Structure of the sets of preventive protection |  |
| DECISION No 12 | FSAR: 7 FSAR Section 7.4 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The diagram will be updated in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 13 | FSAR: 7 FSAR Appendix А |
| Recommendation: Comparing the RS system's documents in chapters 7 and 10 of the FSAR there are some mismatch cases, for example: - In sheet No. 10.4.13.14 of the FSAR (Chapter 10) the "Alarm set point" of the parameter Nos. RS12/22/32/42F001 (pump RS12/22/32/42D001 flowrate) are ">75 and <25", whereas they have been mentioned as: "HA25 and HW25" in book 2 of FSAR, chapter 7, sheet 7.A-306 to 7.A-326. In addition, the operation value of these items is 150, which is in conflict with "Alarming setpoint" that has been specified as "HA25 and HW25". Please clarify. In sheet Nos. 10.4.13 to 15, the "Alarm set point" of parameter Nos. RS12/22/32/42 T002 (Temperature of the motor hot air) is ">110", whereas in book 2 of FSAR, Chapter 7, (sheet No. 7.A.308), "alarm set point" has not been mentioned (for instance: for item No. 11RS12T002 the relevant set point has not been mentioned). Please clarify |  |
| Reply 13 | FSAR: 7 FSAR Appendix А |
| Reply: At present the procedure of process systems running on the unit mathematical model takes place at which the operation modes of pumping and ventilation units, etc. are being specified. Concurrently the signal settings for these units are being corrected. Similar work will be performed as per the results of the commissioning and trial running of the unit. At completion of these stages the final changes will be introduced in the FSAR |  |
| DECISION No 13 | FSAR: 7 FSAR Appendix А |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 14 | FSAR: 7 FSAR Appendix А |
| Recommendation: Comparing P&ID diagrams of the RS system in the FSAR book 2 of chapter 7 and chapter 10 (sheet Nos. 7.A.305 and 10.4.13-5 respectively), the emergency filling branch of the tank Nos. RS10B001, 2, 3 & 4 has not been given in FSAR, Chapter 10, please clarify |  |
| Reply 14 | FSAR: 7 FSAR Appendix А |
| Reply: At reconciliation of РSAR Chapter 10 the emergency filling of DM water tanks was excluded (See Figure 10.4.13.2.1-1 of FSAR Chapter 10) |  |
| DECISION No 14 | FSAR: 7 FSAR Appendix А |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 15 | FSAR: 7 FSAR Appendix А and D |
| Recommendation: Concerning book 2 of the FSAR Chapter 7, sheet Nos. 327 to 336 (VJ system), please find our comments as follows: - There are some mismatched cases concerning set points between FSAR and document No. 29.BU.1ZK2.0.AK.AL.RDR001 (such as: on page No. 8, item No. 11VJ10T002, alarming set point has been mentioned as "HW>45", whereas it has not been mentioned in FSAR, Chapter 7, sheet No. 7.A-333). Please clarify. - There are some mismatched cases in "Alarming set point" between FSAR and Doc. No. 29.BU.1ZK2.0.AK.AL.RDR001 (such as: in item No. 1188, entitled as 11VJF00A, the "Alarming set point" is "HA 510, HW 510 & HT400" in the FSAR, whereas it has been mentioned as "LW<50 & LA<400" in Doc. No. 29.BU.1ZK2.0.AK.AL.RDR001, page 8). - The algorithm entitled as VJS11EH001, has not been identified in sheet 7.D.239 to 7.D.258 of book 5 of FSAR, Chapter 7, "algorithms of protections and interlocks secured closed cooling water system VJ ZK1, ZK2 BUILDING", whereas it has been specified for some VJ system parameters such as 11VJ11F001B, sheet No. 7.A-333 (book 2 of FSAR, Chapter 7). Please add the a.m. algorithm to VJ algorithm section 7.D.10 (sheet 7.D.239 to 7.D.258) |  |
| Reply 15 | FSAR: 7 FSAR Appendix А and D |
| Reply: At present the procedure of process systems running on the unit mathematical model takes place at which the operation modes of pumping and ventilation units, etc. are being specified. Concurrently the signal settings for these units are being corrected. Similar work will be performed as per the results of the commissioning and trial running of the unit. At completion of these stages the final changes will be introduced in the FSAR |  |
| DECISION No 15 | FSAR: 7 FSAR Appendix А and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 16 | FSAR: 7 FSAR Appendix А and D |
| Recommendation: The functional diagrams and algorithms for a number of systems have been mentioned in book 2, 4 and 5 of FSAR, Chapter 7, please specify how the systems have been selected to be included in FSAR and why algorithms for a number of the important systems (such as: YB, YC, YA, …) have not been taken in to consideration |  |
| Reply 16 | FSAR: 7 FSAR Appendix А and D |
| Reply: In Books 2, 4 and 5 of FSAR Chapter 7 the functional diagrams and algorithms for the main process systems mentioned in Book 1, are given. They relate to safety systems and unit shut down systems |  |
| DECISION No 16 | FSAR: 7 FSAR Appendix А and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 20 | FSAR: 7 FSAR Appendix А |
| Recommendation: The "RL" process diagram represented in the Figure A.18 (page No. 276 of book 2 of FSAR-7) is not completely compatible with the figure No. 10.4.6.2.2.1.2-1 (page No. 10.4.6-17 of chapter 10) there are considerable differences between the a.m. figures, please clarify these inconsistency and correct them accordingly |  |
| Reply 20 | FSAR: 7 FSAR Appendix А |
| Reply: The purpose of functional diagrams is to indicate the number and location of I&C transducers. Therefore some auxiliary process lines at functional diagrams are missed |  |
| DECISION No 20 | FSAR: 7 FSAR Appendix А |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 of FSAR, it will be corrected.(See reply 82) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 21 | FSAR: 7 FSAR Appendix A |
| Recommendation: On page No. 7.A-296 of the FSAR, book 2 of Chapter 7, the transducer "11XQ01P001A" (item No. 1228) has been referred to algorithm No. YCS05ER101, whereas this transducer has not been used as input to the a.m. algorithm (page No. 14 of Doc. No. 28.BU.1ZA.YC.AT.TB.RDR009, letter No. 02.1/02-4734 dated 12.03.03). The same problem exists for the following items: 1228, 1229, 1230, 2636, 2638, 2639, 2656, 2657, 2658, 2600, 2607, 2608 |  |
| Reply 21 | FSAR: 7 FSAR Appendix A |
| Reply: At present the procedure of process systems running on the unit mathematical model takes place at which the operation modes of pumping and ventilation units, etc. are being specified. Concurrently the signal settings for these units are being corrected. Similar work will be performed as per the results of the commissioning and trial running of the unit. At completion of these stages the final changes will be introduced in the FSAR |  |
| DECISION No 21 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 22 | FSAR: 7 FSAR Appendix A |
| Recommendation: On page No. 7.A-296 of book 2 of the FSAR, Chapter 7, the transducer "11XQ01P001A" (item No. 1228) has not been referred to algorithm No. YCS05EY105 whereas this transducer has been used as input to the algorithm YCS05EY105 (page No. 14 of the Doc. No. 28.BU.1ZA.YC.AT.TB.RDR009). The same problem exists for the following items: 1228, 1229, 1230, 2636, 2638, 2639, 2656, 2657, 2658, 2600, 2607, 2608 |  |
| Reply 22 | FSAR: 7 FSAR Appendix A |
| Reply: At present the procedure of process systems running on the unit mathematical model takes place at which the operation modes of pumping and ventilation units, etc. are being specified. Concurrently the signal settings for these units are being corrected. Similar work will be performed as per the results of the commissioning and trial running of the unit. At completion of these stages the final changes will be introduced in the FSAR |  |
| DECISION No 22 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 23 | FSAR: 7 FSAR Appendix А |
| Recommendation: On page number 7. A-296 FSAR, Book 2, Chapter 7, transducer "11XQ01P001A" (element No. 1228) was mentioned with regard to algorithm No. YCS05ER101, but this sensor was not used as input to the above-mentioned algorithm (page No. 14 Document No. 28. BU1ZA.YC.AT.TB.RDR009, letter No. 02.1/02-4734 dated 12.03.03). The same problem exists for the following items: 1228, 1229, 1230, 2636, 2638, 2639, 2656, 2657, 2658, 2600, 2607,2608 |  |
| Reply 23 | FSAR: 7 FSAR Appendix А |
| Reply: At present the procedure of process systems running on the unit mathematical model takes place at which the operation modes of pumping and ventilation units, etc. are being specified. Concurrently the signal settings for these units are being corrected. Similar work will be performed as per the results of the commissioning and trial running of the unit. At completion of these stages the final changes will be introduced in the FSAR |  |
| DECISION No 23 | FSAR: 7 FSAR Appendix А |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 24 | FSAR: 7 FSAR Appendix A |
| Recommendation: Measuring range of the following transducers (on page Nos. 7.A-296-304 of book 2 of FSAR, Chapter 7 is not compatible with maximum parameters values. 11XQ01P001A,B,C, 11XQ01P007A,B,C, 12XQ01P002A, B, C, 12XQ01P006A,B,C, 12XQ01P008A, B,C, 13XQ01P003A, B,C, 13XQ01P009A, B, C, 14XQ01P004A, B,C, 14XQ01P010A, B, C |  |
| Reply 24 | FSAR: 7 FSAR Appendix A |
| Reply: The given transducers are intended for control of underpressure in containment at NO modes and signal generation for ventilation isolation valves closing at pressure rise up to 3 kPa. At LOCA type accident these transducers do not operate |  |
| DECISION No 24 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: the FSAR Rev. 1, the value of 0.5 KPa should be changed to 0.5 MPa |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 25 | FSAR: 7 FSAR Appendix A |
| Recommendation: The following transducers have been specified in page No. 7.A-276 of book 2 of the FSAR, Chapter 7, (RL-functional diagram) whereas they have not been mentioned in page Nos. 7.A-277-279. RL61P002, RL61P001, RL61P001D, RL61T001, RL61F001A,B,D RL71P001, RL71P001D, RL71F001 A,B,D |  |
| Reply 25 | FSAR: 7 FSAR Appendix A |
| Reply: Issue requires explanations. The mentioned transducers are given both in page А-276, and also in pages А-277…279 |  |
| DECISION No 25 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In FSAR Rev. 1, the comment will be considered |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 26 | FSAR: 7 FSAR Appendix D |
| Recommendation: While there is leak in SG1, the "BRU-A" valve of SG1 shall not be opened, therefore the output of algorithm No. 1YZS60EY005 (page No. 7.D-80 of book 4, chapter 7 of FSAR) specified as B01 shall be changed as follows: New B01 into algorithm No. RAS10EE001 B01 & A01 The same approach should be applied to algorithm No.2YZS60EY005, 3YZS60EY005 and 4YZS60EY005 |  |
| Reply 26 | FSAR: 7 FSAR Appendix D |
| Reply: From output В01 of algorithm No. 1YZS60EY005 the signal is transmitted for switching on the cooling down through "BRU-A" valve of SG1, if there is leak in any other SG. Changes are not required |  |
| DECISION No 26 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 30 | FSAR: 7 FSAR Appendix D |
| Recommendation: A trigger function shall be added to algorithm No. TWS10EE007 or TWS10EE014 (page Nos. 7.D-44 and 7.D-61 of book 5, chapter 7 of FSAR).Operation of the algorithm Nos. TW10EE007 and TWS10EE008 shows that the valve No. TW10S009 will be closed when pump No. TW10D001 is on (100%) and level in tank Nos. TW10B003 and TW10B004 is less than 0.25m, moreover the algorithm No. TWS10EE014 leads the a.m. valve to be opened in two different situations; firstly, the pump No. TW10D001 is off (0%) and the a.m. tanks' level is more or equal to 0.25m. Secondly, the pump No. TW10D001 is on because of the existence of leak in SG and again the a.m. tanks' level is more or equal to 0.25m. Consequently, it seems that the common set-point (0.25) for valve opening and closing conditions (when there is leak) will cause the valve be opened and closed frequently. To avoid it, we believe that a trigger function shall be added to the a.m. algorithms |  |
| Reply 30 | FSAR: 7 FSAR Appendix D |
| Reply: The given situation might have a place in case we are facing two failures: check valve is leaky and the valves are leaky. Their tightness level can be checked at setting activities stage. In the worst case the command from interlock of TWS10-40EE008 might be performed with ban on opening |  |
| DECISION No 30 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 31 | FSAR: 7 FSAR Appendix D |
| Recommendation: In algorithm No. TWSN0EE011 (page No. 7.D-58 of book 5 of FSAR, Chapter 7), it has been referred to gate valve No. TWN0S023 whereas the a.m. gate valve has not been specified in the functional diagram of TW(page No. 7.A-249 of book 2 of FSAR, Chapter 7) and ancillary system for borating pump TWN0D001 (page 45 of Doc. No. 29.BU.1ZAB.0.AK.OK.RDR001, letter No. 04/02-13307 dated 29.08.04) |  |
| Reply 31 | FSAR: 7 FSAR Appendix D |
| Reply: The given valve is given in TWS10-40D001 pumps piping diagram |  |
| DECISION No 31 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 33 | FSAR: 7 FSAR Appendix В |
| Recommendation: The MCR layouts of panels and desks given in book 2&3, should be in accordance with the related last version |  |
| Reply 33 | FSAR: 7 FSAR Appendix В |
| Reply: In FSAR Chapter 7 (Book 3) the last version of the MCR layouts of panels and desks, submitted to the manufacturing plant, is presented |  |
| DECISION No 33 | FSAR: 7 FSAR Appendix В |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 34 | FSAR: 7 FSAR Appendix В |
| Recommendation: The given MCR layouts are not complete. Some layouts of desks have not been given |  |
| Reply 34 | FSAR: 7 FSAR Appendix В |
| Reply: In FSAR Chapter 7 (Book 3) the front panels of the desks described in section 7.5 of Book 1 ("Safety systems reactor control visual devices") |  |
| DECISION No 34 | FSAR: 7 FSAR Appendix В |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 36 | FSAR: 7 FSAR Appendix A |
| Recommendation: Referring to the FSAR, Chapter 7, sheet Nos. 7.A-8 to 16, in YC system, English notes to be added beside Russian notes. For example, in sheet No. 7.A-10, "WS" of "Analog" column for items namely 10YC00P020, 10YC00P021, 10YC00P022, MCR-SP & ECR-SP to be added |  |
| Reply 36 | FSAR: 7 FSAR Appendix A |
| Reply: Comment is accepted. The given changes will be considered at documentation revision |  |
| DECISION No 36 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 37 | FSAR: 7 FSAR Appendix A and D |
| Recommendation: Comparing FSAR, chapter 7, Book2 and FSAR, chapter 7, Book 5 there are many parameters which have been specified by A,B and C in the former document, but in the letter document sensors are not divided as three independent sensors as inputs of algorithms. For example algorithm namely TAR80EZ001 has been specified as "Designation" of parameters namely 10YC00P007A,B&C (The first document sheet No. 7.A-8). However in the second document (sheet no. 7.D-97) just YC00P007 has been mentioned as input of algorithm TAR80EZ001. It seems that the relation of each sensor as input of each algorithm shall be shown clearly. This is the case for many other algorithms of YD system. Please clarify |  |
| Reply 37 | FSAR: 7 FSAR Appendix A and D |
| Reply: In general case in inputs of process algorithms the control points are indicated, but not sensors (i.е. without А, В, С), as usually in the process algorithm the parameter measuring process method is not considered |  |
| DECISION No 37 | FSAR: 7 FSAR Appendix A and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: A clarification will be attached to the process algorithms how to use them, in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 41 | FSAR: 7 FSAR Appendix A and D |
| Recommendation: On page No. 7.A-22 of book 2, Chapter 7, FSAR, the transducers 11YB10L003A, B, C are referenced as input to the algorithms RLS61EE003, 4, whereas the a.m. algorithms have not been included in page Nos. 7.D-164-191 of book 5, Chapter 7, FSAR ("Algorithm of protections & interlocks main feed water system-RL"). The same problem exists for transducer Nos. YB20/30/40L003A, B, C |  |
| Reply 41 | FSAR: 7 FSAR Appendix A and D |
| Reply: At present the procedure of process systems running on the unit mathematical model takes place at which the operation modes of pumping and ventilation units, etc. are being specified. Concurrently the signal settings for these units are being corrected. Similar work will be performed as per the results of the commissioning and trial running of the unit. At completion of these stages the final changes will be introduced in the FSAR |  |
| DECISION No 41 | FSAR: 7 FSAR Appendix A and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 42 | FSAR: 7 FSAR Appendix A |
| Recommendation: The transducer Nos. 10YB51T001 and 10YB51T002 have been mentioned on page No. 7.A-21 of book 2, Chapter 7, FSAR, whereas on page No. 7.A-17 of the a.m. book (figure A.2, building ZA/B, functional diagram for P.M. steam generator YB10) they have not been specified. The same problem exists for transducer Nos. "10YB52T001, 2", "10YB53T001, 2",and "10YB54T001, 2" |  |
| Reply 42 | FSAR: 7 FSAR Appendix A |
| Reply: Comment is accepted. The given changes will be considered at documentation revision |  |
| DECISION No 42 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 43 | FSAR: 7 FSAR Appendix A |
| Recommendation: According to the page No. 7.A-20 of book 2, Chapter 7, FSAR, the transducer Nos. 10YB10P006 and 10YB10P007 have been used for monitoring of tightness of SG flange connection in the secondary circuit and transducer Nos. 10YB10P004 and 10YB10P005 have been used for monitoring of tightness of SG flange connection in the primary circuit, whereas on the page No. 7.A-17 of the a.m. book the transducers 10YB10P006 and 10YB10P007 have been specified in SG flange connection in the primary circuit and the location of transducer Nos. 10YB10P004 and 10YB10P005 is not clearly specified. The same problem exists for transducer Nos. YB20/30/40P004-7 |  |
| Reply 43 | FSAR: 7 FSAR Appendix A |
| Reply: Comment is accepted. The given changes will be considered at documentation revision |  |
| DECISION No 43 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 44 | FSAR: 7 FSAR Appendix A |
| Recommendation: On page Nos. 7.A-27 and 28 of book 2, Chapter 7, FSAR, the transducers 11YB20L001A, B, C and 12YB20L002A, B, C are referred as input to the algorithm Nos. YCS01EY123 and 10YCS01EY223 respectively, whereas the a.m. transducers have not been used as input in the a.m. algorithms (page Nos. 15 and 37 of Doc. No. 28.BU.1ZA.YC.AT.TB.RDR003, letter No.02.1/02-8440). The same problem exists for transducer Nos. 11YB30L001A, B, C, 12YB30L002, A, B, C, 11YB40L001A, B, C and 12YB40L002A, B, C |  |
| Reply 44 | FSAR: 7 FSAR Appendix A |
| Reply: Comments are accepted. Supplement А will be revised. Expected date is August 2006 |  |
| DECISION No 44 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 47 | FSAR: 7 FSAR Appendix A |
| Recommendation: The valve Nos. YP21, 22, 23S006, 7 shall be shown as normally closed valves. Please use the correct symbol |  |
| Reply 47 | FSAR: 7 FSAR Appendix A |
| Reply: The purpose of functional diagrams is to indicate the number and location of I&C transducers. Therefore some auxiliary process lines at functional diagrams are missed |  |
| DECISION No 47 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The P&ID shall be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 53 | FSAR: 7 FSAR Appendix A |
| Recommendation: In the a.m. sheet, only one sensor for measuring the pressure in the relief tank has been considered whereas in FSAR Chapter 5, two sensors have been considered |  |
| Reply 53 | FSAR: 7 FSAR Appendix A |
| Reply: FSAR Chapter 5 should be corrected |  |
| DECISION No 53 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. FSAR Chapter 5 should be corrected according to the comment by Contractor |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 55 | FSAR: 7 FSAR Appendix A |
| Recommendation: In the a.m. sheet measuring circuit Nos. 11YP10L00A, B, C has not been given in P&ID diagram (sheet No. 7.A-41) |  |
| Reply 55 | FSAR: 7 FSAR Appendix A |
| Reply: The purpose of functional diagrams is to indicate the number and location of I&C transducers. Therefore some auxiliary process lines at functional diagrams are missed |  |
| DECISION No 55 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The P&ID shall be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 58 | FSAR: 7 FSAR Appendix D |
| Recommendation: In the a.m. sheet, input No. A01 of all of the algorithms comes from algorithm No. YCR00EY001, whereas in this algorithm it has not been referred to the a.m. algorithms |  |
| Reply 58 | FSAR: 7 FSAR Appendix D |
| Reply: In the a.m. sheet the mentioned reference is missed. Apparently the cases in point are the sheets 318 and 319. In the absent in the FSAR algorithm YCR00EY001 there is a direct command for tripping of the PRZ Tubular Electric Heater instead of reference to algorithms YР10ЕE001-008 |  |
| DECISION No 58 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 59 | FSAR: 7 FSAR Appendix D |
| Recommendation: : The a.m. two comments are valid for algorithms given in sheet No. 7.D-313 |  |
| Reply 59 | FSAR: 7 FSAR Appendix D |
| Reply: In the a.m. sheet the mentioned reference is missed. Apparently the cases in point are the sheets 318 and 319. In the absent in the FSAR algorithm YCR00EY001 there is a direct command for tripping of the PRZ Tubular Electric Heater instead of reference to algorithms YР10ЕE001-008 |  |
| DECISION No 59 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 61 | FSAR: 7 FSAR Appendix D |
| Recommendation: In sheet No. 7.D-316, comment No. 9 is valid for all of the algorithms |  |
| Reply 61 | FSAR: 7 FSAR Appendix D |
| Reply: Apparently the case in point is sheet 330. In this case we inform that the reference to algorithm YPS21EZ003 relates only to algorithms YPS21EZ003 and YPS23EZ003 of additional control line of Pulse-Safety Device |  |
| DECISION No 61 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 63 | FSAR: 7 FSAR Appendix D |
| Recommendation: The given reactor pressure which cause the Injection valves YP11, 12, 13S002 be opened are not the same in algorithm Nos. YPR10EY005 and YPR10DP001 (which one is correct? 16.7 or 16.07 MPa) |  |
| Reply 63 | FSAR: 7 FSAR Appendix D |
| Reply: The pressure value of 16.7 MPa is determined by OKB "Gidropress" for opening of YP11, 12S001 |  |
| DECISION No 63 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed as follows: “Setpoint 16.07 MPa is for closed-loop operation, 16.7 MPA is a protection setpoint. It will be considered in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 68 | FSAR: 7 FSAR Appendix А |
| Recommendation: In sheet No. 7.A-42, it seems that the given HW (4.8) and HT(4.8) for measuring circuit Nos. 10YP10L004A, B, C are incorrect (operating values are 8.2m) |  |
| Reply 68 | FSAR: 7 FSAR Appendix А |
| Reply: It is incorrect in the FSAR. It should be: LW<4.8, LA<4.2, HA>4.2, HW>8.4. It will be corrected |  |
| DECISION No 68 | FSAR: 7 FSAR Appendix А |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. It will be corrected in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 69 | FSAR: 7 FSAR Appendix A |
| Recommendation: In sheet No. 7.A-45, it seems that the given HA and HW (1.5m) for measuring circuit Nos. 10YP20L001A, B are incorrect (operating values are 1.7m) |  |
| Reply 69 | FSAR: 7 FSAR Appendix A |
| Reply: It should be: LW<1.5 |  |
| DECISION No 69 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. It will be corrected in the FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 70 | FSAR: 7 FSAR Appendix A |
| Recommendation: : In sheet Nos. 7.A-46 and 7.A-47, signal from level meter Nos. 11, 12YP10L001A, B, C go to algorithm Nos. 1, 2, 3, 4YZ60EY001, 2, 3, 4, 5. In the a.m. algorithms respective logics have not been indicated and only one sensor has been mentioned |  |
| Reply 70 | FSAR: 7 FSAR Appendix A |
| Reply: In algorithms YZS60EY001-005 the following level measurements are used in PRZ: 1YP10L001 in algorithms 1YZS60EY001-005, 4YZS60EY001-005; 2YP10L002 in algorithms 2YZS60EY001-005, 3YZS60EY001-005 |  |
| DECISION No 70 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 72 | FSAR: 7 FSAR Appendix A |
| Recommendation: According to the table No. 5.1.2-1 of Chapter 5, FSAR, sheet No. 5-13, number of check points for temperature measurement in the cold leg of each loop is 12, whereas in page No. 7.A-48 of FSAR, book 2, Chapter 7, 11 check points have been specified for temperature measurement in the cold leg of loop 2&4. please verify |  |
| Reply 72 | FSAR: 7 FSAR Appendix A |
| Reply: Number of check points for temperature measurement in the cold leg of each loop is 12 |  |
| DECISION No 72 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 74 | FSAR: 7 FSAR Appendix A |
| Recommendation: According to the table No. 5.1.2-1 of Chapter 5, FSAR, sheet No. 5-13 ("list of check points of the main coolant pipeline"), in each loop it should be 2 sensors for measuring of pressure pulsation on the RCP set suction and head and one sensor for measuring of pressure pulsation at the reactor outlet that should be connected to the MCDS whereas on page No. 7.A-48 of book 2, chapter 7, FSAR, the a.m. sensors have not been specified |  |
| Reply 74 | FSAR: 7 FSAR Appendix A |
| Reply: For measurements on the primary circuit the following meterings are considered: Pressure difference at RCP YA10-40P01 – for EP Pressure difference at RCP YA10-40P02 – for EP Pressure difference at RCP YA10-40P03 – for RP MCDS Pressure difference at RCP YA10-40P04 – for RP MCDS Pressure difference at SG YA10-40P05 – for MCR monitor Pressure at RCP head - for MCR monitor |  |
| DECISION No 74 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 79 | FSAR: 7 FSAR Appendix A |
| Recommendation: On page Nos. 7.A-57, 60 & 63 of book 2, Chapter 7, FSAR for the following transducers, please specify the type of alarms (HA, LA, HW, LW, …) 11YA11T003A, B, C, 11YA21T003A, B, C, 11YA31T003A, B, C |  |
| Reply 79 | FSAR: 7 FSAR Appendix A |
| Reply: Temperature alarm LT<70 and LW<150 are used not for detection of emergency cases, but to inform the operator at cool down that the protections are not available |  |
| DECISION No 79 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted. The related page will be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 82 | FSAR: 7 FSAR Appendix A |
| Recommendation: On page No. 7.A-85 of book 2, chapter 7, FSAR (YT P&I diagram), all of the pipelines have been connected to the outlet chamber of the reactor whereas according to the page No. 7.A-7 of book 2, chapter 7, FSAR (YC P&I diagram) and 6th paragraph of chapter 6.3.1.3.2.4 of FSAR, two pipelines shall be connected to the outlet chamber of the reactor and two pipelines shall be connected to the inlet chamber of the reactor |  |
| Reply 82 | FSAR: 7 FSAR Appendix A |
| Reply: The purpose of functional diagrams is to indicate the number and location of I&C transducers. Therefore some auxiliary process lines at functional diagrams are missed |  |
| DECISION No 82 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: It will be corrected in the final version of the FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 83 | FSAR: 7 FSAR Appendix A |
| Recommendation: On page No. 7.A-85 of book 2, chapter 7, FSAR, the motorized valves YT11/12/13/14S005-8 have been identified as normally open valves, whereas according to the 2nd paragraph of page No. 6.3.1-101, Chapter 6, FSAR, the a.m. valves shall be identified as normally- close valves |  |
| Reply 83 | FSAR: 7 FSAR Appendix A |
| Reply: The purpose of functional diagrams is to indicate the number and location of I&C transducers. Therefore some auxiliary process lines at functional diagrams are missed |  |
| DECISION No 83 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: It will be corrected in the final version of the FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 93 | FSAR: 7 FSAR Appendix A |
| Recommendation: Alarming set points for some instruments such as 10YD10P001A, 1B, 1C do not seem to be correct (HA= 0.98, HW=0.98), please clarify. 93- In some cases "HW" for alarming set points have not been specified. As an example, please note for 10YD10T006, 10YD10T007A, 10YD10T007B, 10YD10T007, etc. Being this the case, all the alarming set points for RCPs should be checked again and reviewed throughout the document |  |
| Reply 93 | FSAR: 7 FSAR Appendix A |
| Reply: Given value of 0.98 MPa is specified by the RCP designer. It should testify on RCP glands failure. At NO the value is much higher. For points YD10T006 and YD10T007 HW>110, HА>120 are stipulated |  |
| DECISION No 93 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted. The text will be corrected in FSAR Rev. 1. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 99 | FSAR: 7 FSAR Appendix A and D |
| Recommendation: Whilst the algorithm, entitled "YDR30EY009", has been specified as designation of items 13YD30T002A, B&C (FSAR, Chapter 7, Book 2, sheet 7.A-144), these items are not mentioned as inputs of "YDR30EY009" (FSAR Chapter 7, Book 5, sheet 7.D-282). Please clarify |  |
| Reply 99 | FSAR: 7 FSAR Appendix A and D |
| Reply: Algorithms in the FSAR should be corrected due to the following: In algorithm YD10EY009 signal from YD10T001 is used; In algorithm YD20EY009 signal from YD10T002 is used; In algorithm YD30EY009 signal from YD10T002 is used; In algorithm YD40EY009 signal from YD10T001 is used; |  |
| DECISION No 99 | FSAR: 7 FSAR Appendix A and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and FSAR Rev 1 shall be corrected according to reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 100 | FSAR: 7 FSAR Appendix A and D |
| Recommendation: Same as above comment, whilst the algorithm "YDR40EY003", has been specified as designation of items namely 14YD40T001A,B&C(FSAR, chapter 7, Book 2, Sheet 7.A.147), these items are not mentioned as inputs of "YDR40EY003" algorithm (FSAR, chapter7, Book5, sheet 7.D-272). Please clarify |  |
| Reply 100 | FSAR: 7 FSAR Appendix A and D |
| Reply: Algorithms in the FSAR should be corrected due to the following: In algorithm YD10EY003 signal from YD10T001 is used; In algorithm YD20EY003 signal from YD10T002 is used; In algorithm YD30EY003 signal from YD10T002 is used; In algorithm YD40EY003 signal from YD10T001 is used; |  |
| DECISION No 100 | FSAR: 7 FSAR Appendix A and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and FSAR Rev 1 shall be corrected according to reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 103 | FSAR: 7 FSAR Appendix A |
| Recommendation: Comparing Doc. No. 29.BU.1ZAB.0.AK.OK.RDR001-12 with contents of FSAR, chapter 7, Book2 (page 7.A-3), "VF" should be changed in to "VE" as follows: "Building ZA/B. functional for PM. Service cooling water system VE for secured closed cooling water system TF-VJ". This comment should also be applied on the title of Fig.A.11 (FSAR chapter7, Book2 sheet No. 7.A-148) |  |
| Reply 103 | FSAR: 7 FSAR Appendix A |
| Reply: The comments are accepted. Supplement А will be revised. Revision tentative date is August 2006 |  |
| DECISION No 103 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted and FSAR Rev. 1 shall be corrected according to comment |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 104 | FSAR: 7 FSAR Appendix A |
| Recommendation: Comparing Figure A.11 (FSAR chapter 7, Book2, sheet No. 7.A-148) and Figure 6.3.2.2-1 (FSAR chapter 6, Book3 sheet No. 6.3.2-42) there are some non compliances with these two figures such as: A) VJ30F001 and VJ20F001 in Fig. No. 6.3.2.2-1 has not been specified in Figure A.11, please clarify. B) VE30F002 and VE20F002 in Fig. No. A11 has not been specified in Fig. 6.3.2.2-1. Please clarify. C) For the portion of VE system that has specified in ZK1 building: - VL82 and VL83 branches have not been shown in Figure 6.3.2.2-1. Please verify. 104-2 The icon of VJ30F001 ""in Fig. No.6.3.2.2-1 is in contrast to VE30F002" in Fig.A11. Please clarify |  |
| Reply 104 | FSAR: 7 FSAR Appendix A |
| Reply: A) Check points of the system VJ cannot be shown in this Figure, as they relate to system VE. B) Given сheck points VE are located in the part of the system which is in the ZK building. Therefore they are not required in the Figure А11, which relates to part of the system which is in the ZA/B building. C) Figure А11 shows in details only that relates to part of the system which is in the ZA/B building |  |
| DECISION No 104 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Chapter 6 should be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 105 | FSAR: 7 FSAR Appendix A |
| Recommendation: In FSAR, Chapter 7, Book2 sheet No. 7.A-148, please specify the location of VE23D001, VE22D001, VE31D001 and other pumps and equipment which are in ZM4 and ZM5 Building |  |
| Reply 105 | FSAR: 7 FSAR Appendix A |
| Reply: See Reply to comment 104 С), as Figure А-148 is Figure А-11 |  |
| DECISION No 105 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Chapter 6 should be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 106 | FSAR: 7 FSAR Appendix A |
| Recommendation: In the following table, the operating value for transducers is higher than high alarm setpoint value as example: the operating value for transducer No. 10TH71P002A is 0.75Mpa, whereas the high alarm setpoint is 0.4. Please verify. Transducer; Operating value; Alarm set point; Address of book 2, Chapter 7, FSAR. 10TH71P002A, B; 0.75 MPa; HA 0.4; 7.A-193. 10TH72P002A, B; 0.75 MPa; HA 0.4; 7.A-193. 10 TH 75L001; 0.05-0.4 m; HA 0.37 HW 0.5 HT 0.05; 7.A-194. 10 TH 60L001; 13.55 m; HA 13.45 HW 13.45 HT 12.55; 7.A-207. 11 TH 60L003; 13.55 m; HA 9.0; 7.A-208. 11 TH 60L004; 13.55 m; HA 6.0; 7.A-208. 12 TH 60L002; 13.55 m; HA 13.45 HW 13.45 HT 12.55; 7.A-221. 12 TH 60L005; 13.55 m; HA 9.0; 7.A-221. 12 TH 60L006; 13.55 m; HA 6.0; 7.A-221. |
| Reply 106 | FSAR: 7 FSAR Appendix A |
| Reply: For check point TH71P002 it should be LW < 0.4 MPa. For check point TH72P002 it should be LW < 0.4 MPa. For check point TH75L002 it should be LW < 0.05 m,. HW > 0.13 m, HA > 0.37m. For check point TH60L001 it should be LW < 13.45 m,. LA < 12.55 m, HW>13.65 m. For check point TH60L002 it should be LW < 13.45 m,. LA < 12.55 m, HW>13.65 m Check points TH60L003,004,005,006 are discrete signalizers of low level LA < 6.0 m. Analog value is not measured. For these points the values of rated, min and max levels are given as reference |  |
| DECISION No 106 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted and FSAR Rev.1 shall be corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 107 | FSAR: 7 FSAR Appendix D |
| Recommendation: In algorithm TAR13EE001 page 7.D.73 of book5 FSAR Chapter 7, the output signal "B06" refer to the algorithm TAR13EE02 whereas this algorithm does not exist in "algorithms of protections and interlocks volume control system TA" page 7.D-68 to 7.D-104, Book 5, FSAR |  |
| Reply 107 | FSAR: 7 FSAR Appendix D |
| Reply: В06 of the given algorithm should refer to algorithm TAR10FF902 |  |
| DECISION No 107 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 108 | FSAR: 7 FSAR Appendix D |
| Recommendation: In algorithm TAR10FF902, A01 signal is received from "B06" output of algorithm TAR13EE001 whereas "B06" output of algorithm TAR13EE001 is not sent to the TAR10FF902 |  |
| Reply 108 | FSAR: 7 FSAR Appendix D |
| Reply: Input А01 of the given algorithm should refer to algorithm TAR13ЕЕ001 |  |
| DECISION No 108 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 109 | FSAR: 7 FSAR Appendix D |
| Recommendation: For algorithms No. TAR10EZ002, two input signals have been named as "A03" (for interlock TAR00EY001 and operator command). Moreover, for algorithm Nos. TAR5NEZ001, two input signals have been named as "A02" (for temperatures YDN0T001 and YDN0T002) which are not correct. Please note that these comments were accepted in item No. 4 letter No. 04/02-25048 dated 04.12.05 but not implemented in FSAR |  |
| Reply 109 | FSAR: 7 FSAR Appendix D |
| Reply: Input from operator should have marking А04 |  |
| DECISION No 109 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 110 | FSAR: 7 FSAR Appendix D |
| Recommendation: In algorithm TAR00EY001, the output of flip-flap that is regulated by operator should be changed to mode "not" before entering to unit "&". Please note Item 1 letter No. 04/02-25048 dated 04.12.05 |  |
| Reply 110 | FSAR: 7 FSAR Appendix D |
| Reply: Algorithm is performed correct. Operator can stop the interlock operation for 5 min for blow down connecting after short-term make-up water closing at intermediate modes |  |
| DECISION No 110 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted. Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 111 | FSAR: 7 FSAR Appendix D |
| Recommendation: In the following algorithms, the type and title of the operator command in the respective input signals have not been specified. Please be informed that this comment was accepted in Item 3 of the letter No. 04/02-25048 dated 04.12.05 previously. Algorithm No.; Input No.. TAR10EZ001; A02. TAR10EZ002; A03. TAR20EZ001; A04, A05. TAR31EZ001; A09. TAR32EZ001; A09. TAR33EZ001; A09. TAS64EZ001; A03. TAS64EZ002; A03. TAS61EZ001; A03. TAS61EZ002; A03. TAS62EZ001; A03. TAS62EZ002; A03. TAS63EZ001; A03. TAS63EZ002; A03. |
| Reply 111 | FSAR: 7 FSAR Appendix D |
| Reply: In given interlocks the operator command is named "Remove ban" |  |
| DECISION No 111 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted. It will be added in the algorithms |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 112 | FSAR: 7 FSAR Appendix D |
| Recommendation: In some of the algorithms in page Nos. 7.D.259 up to 7.D.303 of Book5 of the FSAR some command signal refer to TA sensors, whereas these sensors do not exist in tables of instrument list (page 7-A-258 to 7.A.275) and in P & ID diagram(page No. 7.A.258). These sensors are listed in the following table: TA Sensors; YD Algorithms; Page No. of Algorithm. TA61P002C; YDR10EY002; 7. D-260. TA62P001C; YDR20EY002; 7. D-264. TA63P001C; YDR30EY002; 7. D-268. TA64P002C; YDR40EY002; 7. D-272. |
| Reply 112 | FSAR: 7 FSAR Appendix D |
| Reply: Check points and algorithms correspond to the design. Sensor "С" is not used |  |
| DECISION No 112 | FSAR: 7 FSAR Appendix D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: P&ID and the list of instruments shall be corrected in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 116 | FSAR: 7 FSAR Appendix A |
| Recommendation: In page 7.A-281 to 7.A-294 some set points exist but the related Algorithms do not exist. For example, in page 7.A-282, for set points "<5.1, <5.29, <5.59, >6.66" there is not any algorithm |  |
| Reply 116 | FSAR: 7 FSAR Appendix A |
| Reply: The comment is not clear, as in given pages the functional diagrams are presented |  |
| DECISION No 116 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 117 | FSAR: 7 FSAR Appendix A and D |
| Recommendation: The following Algorithms which are mentioned in pages 7.A.282- to 7.A-294 Book2, FSAR chapter7, do not exist in "Algorithms of protections and interlocks main steam pipe line system RA" page 7.D-104 to page 7.D-164 from FSAR Book5 Algorithm No.; Algorithm No.. RAS10EE001; RAS40EE001. RAS10EE002; RAS40EE002. RAS10EE003; RAS40EE003. RAS10EE004; RAS40EE004. RAS10EE005; RAS40EE005. RAS10EE006; RAS40EE006. RAS20EE001; RAS30EE003. RAS20EE002; RAS30EE004. RAS20EE003; RAS30EE005. RAS20EE004; RAS30EE006. RAS20EE005; RAS20EE006. |
| Reply 117 | FSAR: 7 FSAR Appendix A and D |
| Reply: See algorithms of protections and interlocks. Main steam pipe line system RA. Building ZA/B. 28.BU. 1 ZB.RA.AT.RDR001. Revision 1. Draw your attention, that algorithms may be corrected due to the change of the manufacturing plant of the “steam unit” valves |  |
| DECISION No 117 | FSAR: 7 FSAR Appendix A and D |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 118 | FSAR: 7 FSAR Appendix A |
| Recommendation: In page 10-3-5 of FSAR, chapter 10 the following sensors exist, whereas these are not mentioned in page 7-A-280, to 7.A-294 Book 2 of FSAR. Algorithm No.; Algorithm No.. 11RA10R005; 12RA20R001. 10RA10R003; 10RA20R003. 10RA10R004; 10RA20R004. 12RA10R006; 12RA20R002. 11RA10R001; 11RA20R005. 11RA10R002; 12RA20R006. 10RA30R003; 10RA40R003. 13RA30R006; 13RA40R006. 14RA30R005; 14RA40R005. 10RA30R004; 10RA40R004. 13RA30R001; 14RA40R001. 13RA30R002; 14RA40R002. |
| Reply 118 | FSAR: 7 FSAR Appendix A |
| Reply: See section 10.3.3 of FSAR Chapter10 |  |
| DECISION No 118 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 119 | FSAR: 7 FSAR Appendix A |
| Recommendation: P&I Diagram for "RA system in ZB.9 Building" in sheet 7.A.280, Book 2 FSAR is different from the P & I diagram of sheet 10-3-5 chapter 10 of FSAR |  |
| Reply 119 | FSAR: 7 FSAR Appendix A |
| Reply: Due to change of the manufacturing plant of the “steam unit” valves, the RA system diagram in the ZB.9 building will be corrected in the FSAR Chapter 10 |  |
| DECISION No 119 | FSAR: 7 FSAR Appendix A |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawings and algorithms will be submitted in Appendices A,B,C, and D to chapter 7 of the FSAR, Rev.1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

Comments on Appendix B3 (to MoM to FSAR-7 (Rev. 0) dated 03-13.03.07, Tehran, LIST OF REPLIES TO OCE LETTER No. LTR-13070-65287 DATED 18.02.06)

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 1 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: There are I&C system which are not presented in the FSAR. The important one is I&C of EDGs, especially EDGs sequencer. - There is no information about the control algorithm for refueling Machine and polar crane - There is no information about the control algorithm for containment personnel and emergency locks, etc. |  |
| Reply 1 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: EDG description is given in Chapter 9 of FSAR. Algorithms for its step loading (YZS40EY001, YZS41EY001) are given in Supplement D to Chapter 7 of FSAR. Control equipment for refueling Machine, polar crane and locks in the containment is supplied in a set with process equipment, is not included into APCS and shall not be described in Chapter 7 of FSAR, as specified in Guide 1-70 |  |
| DECISION No 1 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: All other instrumentation and control systems important to safety such as fire protection, emergency diesel generators, fuel handling, radiation monitoring, containment locks, and control of essential auxiliary supporting systems will be considered in the related chapters of FSAR The following will be added in FSAR Rev. 1: “Sequential startup of EDG loading is included in the ESFIP system” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 2 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Protection on local power is not acceptable. It shall be reconsidered. Even it looks that this is not considered in design e.g. for accident analysis in chapter 15 that there is no case with trip on local power. And also since protection on DNB is considered it do not seem necessary. Generally justification is required with respect to the precision and sensitivity and reliability of measurement with in core neutron detectors… being applied for Protection on local power. In addition it shall be assessed, if it could cause scram when it is not required. e.g. what will be the condition in transients such as condition with change of xenon concentration and distribution? Table 7.2-2 should be corrected accordingly |  |
| Reply 2 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: No Reply |  |
| DECISION No 2 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Substantiation of this protection necessity shall be discussed with Gidropress during FSAR-15 consideration |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 FSAR Section 7.1.1 does not demonstrate that the results of the above-mentioned discussion have been considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 3 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Clear information shall be provided on safety classification MCDS and its sub system and their boundaries. In this regard each safety function controlled or monitored by MCDS shall be justified. e.g. - protection on DNB - protection on local power - LBB monitoring - etc. |  |
| Reply 3 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Safety classification of MCDS and its subsystems according to PNAE G-01-011-97, given in FSAR text and MCDS structural diagram (Figure. 7.7-7), will be additionally presented in Table: Table 7.7-7 - Safety classification of MCDS and its subsystems Safety classification of MCDS and its subsystems; Classification designation as per PNAE G-01-011-97. SHC-P; 2C. SHC-IC; 3N. CC UL; 3N. ICND SHC; 4. LMS SHC (ALMS SHC, HLMS SHC); 3N. VMS SHC; 4. LPMS SHC; 4. SIA SHC; 3N. LL-CS SHC; 4. COC; 3N. Terminals cabinet; 3N. Safety classification of MCDS and its subsystems, given in Table 7.7-7, is justified in the text of section 7.7.1.4 FSAR. |
| DECISION No 3 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. The classification of ICND SHC (4) and SIA SHC (3N) shall be refined and English abbreviations shall be provided in Table 7.7-7. The SHC-P is for protection on DNB and local power |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 4 | FSAR: 7 FSAR Section 7.1.1.6 |
| Recommendation: Page 7-25; result of the test for TPTS stability to EM should be presented |  |
| Reply 4 | FSAR: 7 FSAR Section 7.1.1.6 |
| Reply: Page 7-25 reads that TPTS complies with GOST 50746-2000. Hence, TPTS was successfully tested for electromagnetic compatibility |  |
| DECISION No 4 | FSAR: 7 FSAR Section 7.1.1.6 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and the GOST number is corrected |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 6 | FSAR: 7 FSAR Section 7.7.1.4.5 |
| Recommendation: LBB monitoring system shall be in safety class 2 and in category 1 of seismic design, According to the guidance for application of LBB safety concept for NPP pipelines RD 95 10547-99 (R-TPR-01-99). |  |
| Reply 6 | FSAR: 7 FSAR Section 7.7.1.4.5 |
| Reply: LBB concept the RP main pipelines is provided with three leak monitoring systems: - acoustic leak monitoring system (ALMS) and humidity leak monitoring inspection system (HLMS) involved in RP MCDS - radiation monitoring system (RMS) involved in APCS of power Unit According to RD requirements of RF (PNAE G-01-011-97), the given systems are developed as systems important to safety, and hardware of the systems are referred to safety class 3. Thus, according to LBB requirements (RD 95 10547-99), one of the systems (RMS) is the system of category of seismic stability 1 and it withstands SSE. In RD 95 10547-99 (R-TPR-01-99) no requirements are stated for classification of LBB monitoring systems by safety class 2 |  |
| DECISION No 6 | FSAR: 7 FSAR Section 7.7.1.4.5 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and included in Chapter 5.2.5 of the FSAR, Revision 1. The power supply of LBB monitoring system is reliable power supply and it will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 7 | FSAR: 7 FSAR Section 7.7.1.4.3.3 |
| Recommendation: Core exit temperature measurement with higher range (up to 12000 C) is not mentioned in relevant section of FSAR. It shall be mentioned in all relevant sections |  |
| Reply 7 | FSAR: 7 FSAR Section 7.7.1.4.3.3 |
| Reply: Information on measurement of the reactor core outlet temperature un to 12000 C is given in reply No. 29 to OCE comment concerning section 7.7.1.4.3.3 (page 7-222, 2nd para) - "…In the NTMC of the third type (4 pieces) there are 5 thermocouples intended to signal that water-steam mixture is forming under the reactor top head and temperature is coming to 12000 C under accident conditions (the signals from these thermocouples arrive into the specialized devices which are not a part of the MCDS)" |  |
| DECISION No 7 | FSAR: 7 FSAR Section 7.7.1.4.3.3 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted. A description of the level and temperature monitoring equipment up to 1200 0C will be provided in section 7.5 of the FSAR, revision 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 8 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Table 7.1.1-1 shall be given in more detail for all I&C system and elements. And also for all sensors used in all system in different safety class |  |
| Reply 8 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Table 7.1.1-1 was presented in Chapter 7 of PSAR. Comments on a. m. Table were received from NPPD specialists and IAEA experts, allowed for in Supplement 1 to Chapter 7 and approved by the Principal. FSAR materials comply with Supplement 1 to Chapter 7 of PSAR and shall not be modified |  |
| DECISION No 8 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: This information is provided in Appendix A to the FSAR |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 9 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Fire monitoring system shall be in class 2. This issue was discussed and agreed during PSAR (chapter 9) review process. It should also be given in table 7.1.1-1 |  |
| Reply 9 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: According to Chapter 7 of FSAR, fire monitoring system equipment was referred to class 4N as per OPB 88/97. Equipment classified as above was manufactured at TENZOR plant, accepted by the Principal and supplied to BNPP. For this reason, it does not look possible to change equipment class in FSAR |  |
| DECISION No 9 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: According to Chapter 7 PSAR and design documents, fire detection equipment was referred to class 4N as per OPB 88/97. Additional discussion will be held in Moscow between VO "Safety" and ZAO ASE regarding seismic categories of AFPS and the results will be send to NPPD/NNSD by the end of April |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 10 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Seismic instrumentation shall be in class 2.it shall be included in table 7.1.1-1 |  |
| Reply 10 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: According to Table 7.1.1-1 Item 1, seismic instrumentation ISPE is referred to class 2NC as per OPB 88/97 |  |
| DECISION No 10 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In the English version of FSAR Rev.1, it will be corrected to C |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 13 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-17 instrumentation such as RPV level measurement , core exit temperature measurement with higher range, which are specifically considered for BDBA, shall be in class 2, to be assured on their higher availability in accident condition. They shall be given in Table 7.1.1-1. (The same for SPDS) |  |
| Reply 13 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: See Appendix A to Chapter 7 |  |
| DECISION No 13 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: see agreement No. 29 of Appendix B1. The classification of post-accident monitoring will be added to the table 7.5.1.3.-1 and 7.5.2.3.-1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 14 | FSAR: 7 FSAR Section 7.5.1.3 |
| Recommendation: RPV level measurement indication in MCR is an indication with only 5 divisions for all height of RPV which do not seems to be credible for level indication required for accident management. It shall be justified, unless It needs more precise level indication. The technique of level measurement shall be explained with the sensitivity and accuracy of parameter value and relevant indication |  |
| Reply 14 | FSAR: 7 FSAR Section 7.5.1.3 |
| Reply: See Table 7.5.1.3-1 |  |
| DECISION No 14 | FSAR: 7 FSAR Section 7.5.1.3 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: see reply 13 (Appendix B3) |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 15 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-21: in the list of parameter recording for RP control the core exit temperature shall be added. (The same for hydrogen concentration in containment). A list of important recording parameter may be added to the text |  |
| Reply 15 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: See Table 7.5.3-1 |  |
| DECISION No 15 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The table number is corrected, and on page 21 (English) it will be added: “etc.” |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 19 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: There is no clear information if the requirement of GOST 26843-86 item 1.2.7 is considered. And how this control is implemented to make sure that no important information is lost of being considered by operator in due time |  |
| Reply 19 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: All requirements of GOST 26843-86 (item 1.2.7) at the designing of rooms and panels of MCR/SCR |  |
| DECISION No 19 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Contractor stated that the English translation of item 1.2.7 of GOST 26843-86 is not correct. The reply is accepted |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 20 | FSAR: 7 Chapter 7 FSAR Section 7.2 |
| Recommendation: There is no clear information if the requirement of GOST 26843-86 item 1.2.9 is considered. Is the possibility to shut down the reactor considered only from ECR in addition to MCR or it is also possible from other control panel or directly from control cabinets. Please provide information in relevant section of the FSAR. The independency of information forming channel and line for transfer of control command should also be given to the FSAR |  |
| Reply 20 | FSAR: 7 Chapter 7 FSAR Section 7.2 |
| Reply: Commands from MCR and ECR arrive to cabinets 1PCC and 4PCC, included in sets of EP actuating part, that is shown in figure 7.2-16 FSAR. The commands arrive through physically independent lines. For input of the commands two EP buttons are provided in MCR, and two buttons - in ECR. Generation of a command from any of these buttons provides generation of a manual trip command, as described in item 7.2.1.6. Thus, in this case no correction of FSAR is required |  |
| DECISION No 20 | FSAR: 7 Chapter 7 FSAR Section 7.2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The Contractor stated that the English translation of item 1.2.9 of GOST 26843-86 is not correct. The reply is accepted |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 21 | FSAR: 7 FSAR FSAR Section 7.5.1 |
| Recommendation: In section of man machine interface (7.5 ) please provide information on how the information presented via TLS-U display in control room is managed and prioritized in order operator in each time be completely informed on important parameter changes and relevant alarm. For example for control rod position which LCO are 2 steps (chapter 16) and it cannot be monitored from main panel |  |
| Reply 21 | FSAR: 7 FSAR FSAR Section 7.5.1 |
| Reply: As item 7.5.1.2 reads, great display is envisaged on MCR to indicate the position of controllers, condition of actuators, information and control circuits |  |
| DECISION No 21 | FSAR: 7 FSAR FSAR Section 7.5.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be completed with the following information and will be included in FSAR Rev.1: - The most important information regarding reactor and turbine plant is provided in all video screens. Appearance of new messages is indicated by sound alarms. - A “rough” indication of the control rods position is provided on the MCR and ECR panels. The information on the exact position of control rods is provided on the TLS-U monitors in the appropriate formats. In case of TLS-U loss the operator may assess the changes of the position of the CPS control group by the reactor power value. If required, the information on the exact position of control rods may be always obtained on the SHKU cabinets in the rod control and instrumentation system room |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 22 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Table 7.1.1-7 page7-31; relevant information on references for each item concerning relevant experiences and results, should be given |  |
| Reply 22 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Comments are not accepted. The mentioned information could have been requested on stages of approval of TA, technical design and PSAR. After all the complexes have been manufactured, accepted by NPPD and NNSD representatives, supplied and installed at BNPP, a. m. comments look at least incorrect. Besides, Guide 1-70 contains clear-cut information on additional data to be included into FSAR as against PSAR. Please, be strictly adherent to requirements set forth in Guide 1-70 |  |
| DECISION No 22 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: A reference to the number of years (e.g. 2-3 years) and the name of the plant will be provided. It will be considered in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 24 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-24 item 7.1.1.6.3 no 1; information presented is not adequate to justify required safety level of soft- hardware complex items TPTS52 and 53. All information on assessment and verifying safety and reliability of items including their relevant software and applied test and results shall be given. Important characteristic of this element shall be explained; how they are programmed and how the program may be changed. What exact measures are considered to prevent changes to the program without required regulatory and safety analysis process for approval of changes. Considering Page 7-33 item 7.1.1.8 no information is presented on hardware specially intended for purpose of introducing application algorithm. And how its own reliability is assured? Considering statement “This can be done before inserting the module or after that, with the help of the hardware specially intended for this purpose”, how it is assured that the process of overwriting is reliable and safe and in no way there be possible that automatic overwriting be performed from failed module |  |
| Reply 24 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Comments are not accepted. The mentioned information could have been requested on stages of approval of TA, technical design and PSAR. After all the complexes have been manufactured, accepted by NPPD and NNSD representatives, supplied and installed at BNPP, a. m. comments look at least incorrect. Besides, Guide 1-70 contains clear-cut information on additional data to be included into FSAR as against PSAR. Please, be strictly adherent to requirements set forth in Guide 1-70 |  |
| DECISION No 24 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The conclusions from the VNIIA Technical Report on TPTS verification will be added in FSAR Rev. 1. (see reply 23 to NNSD comments in Appendix C) The following text will be included in FSAR Rev. 1: "In order to perform program loading a person should have special device and to know the proper password and only authorized person can load of the program" |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 25 | FSAR: 7 FSAR Chapter 7 |
| Recommendation: The issue of loading control algorithm to the module is a crucial one. It is not defined clearly how it should be introduced to the module? Who is authorized to do that how it is assured that there will not be any human error in loading, and what kind of design measure and procedural measure and requirement are in place to prevent any failure in loading and testing. How it is tested and verified to be accepted to put in operation. (What about possibility of by aim incorrect loading, how plant is protected against this kind of attack) |  |
| Reply 25 | FSAR: 7 FSAR Chapter 7 |
| Reply: Comments are not accepted. The mentioned information could have been requested on stages of approval of TA, technical design and PSAR. After all the complexes have been manufactured, accepted by NPPD and NNSD representatives, supplied and installed at BNPP, a. m. comments look at least incorrect. Besides, Guide 1-70 contains clear-cut information on additional data to be included into FSAR as against PSAR. Please, be strictly adherent to requirements set forth in Guide 1-70 |  |
| DECISION No 25 | FSAR: 7 FSAR Chapter 7 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The conclusions from the VNIIA Technical Report on TPTS verification will be added in FSAR Rev. 1. (see reply 23 to NNSD comments in Appendix C) The following text will be included in FSAR Rev. 1: "In order to perform program loading a person should have special device and to know the proper password and only authorized person can load of the program" |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 26 | FSAR: 7 FSAR Chapter 7 |
| Recommendation: Generally no information related to the reliability of safety related software is presented. Method applied for assessment of safety related software reliability and their verification and relevant results should be given. How the seismic qualification for the soft- hardware complex has been performed, and their functionality are assured |  |
| Reply 26 | FSAR: 7 FSAR Chapter 7 |
| Reply: Comments are not accepted. The mentioned information could have been requested on stages of approval of TA, technical design and PSAR. After all the complexes have been manufactured, accepted by NPPD and NNSD representatives, supplied and installed at BNPP, a. m. comments look at least incorrect. Besides, Guide 1-70 contains clear-cut information on additional data to be included into FSAR as against PSAR. Please, be strictly adherent to requirements set forth in Guide 1-70 |  |
| DECISION No 26 | FSAR: 7 FSAR Chapter 7 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The conclusions from the VNIIA Technical Report on TPTS verification will be added in FSAR Rev. 1. (see reply 23 to NNSD comments in Appendix C) The following text will be included in FSAR Rev. 1: "In order to perform program loading a person should have special device and to know the proper password and only authorized person can load of the program" |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 27 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-23 according to the text “extent of information on the GMS, have been provided in order to proceed with the technological sequence of operators action in case of loss of TLS-U displays, which yields to monitoring of stable state of the power unit within 2 hours and power unit shut down,..”. Please provide information to justify that extent of information on the GMS is enough for continue operation within 2 hours, while most of auxiliary system has no indication other than on TLS-U displays. The list of important information and control key on the GMS should be given. In addition it is required clearly specify if unit shall be shut down after 2 hours of loss of TLS-U displays |  |
| Reply 27 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: The abstract you’ve quoted is corroborated with the results of verification test held at APCS simulator (Electrogorsk), research at Kalinin NPP (reference power unit) and approved in Chapter 16 of PSAR/BNPP |  |
| DECISION No 27 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: Updated drawing will be provided in Appendices A,B, C, D to Chapter 7 of the FSAR, Revision 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1. FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 28 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Some paragraph in the text is not prepared carefully and need correction for example: - Page 7- 8, 9 that seems the plant I&C is designed for mitigation of BDBA that it is not correct and the plant I&C is not designed for mitigation of BDBA. Only some Instrumentation such as RPV level measurement, core exit temperature measurement with higher range, are specifically considered for BDBA (SPDS also is considered to be used in BDBA), which is not clearly mentioned what exact conditioned has been considered As design bases of them but obviously all the systems and elements are designed for DB condition listed for NPP (NO, AOO, DBA including seismic,..). Therefore the paragraph for level 4 is not correct. Even the design bases of habitability system are the list of DB considered for plant. Although every system which would be available At BDBA condition can be used but it does not mean they are designed for BDBA condition. And how it can be guaranteed that during beyond design accident condition that “the maximum design limit will not be exceeded”. - The safety classification groups shall be defined in a precise way in some parts the usage of definition for importance to safety is confusing because safety class two is defined as importance to safety (e.g. in page 7- 9) while it is clear that importance to safety contains both safety class 2 and 3 this shall be corrected in all part of the text. For example in the page 7-15 item 7.1.1.1 and 7.1.1.2. - Page 7-14 second paragraph shall be corrected because there is not such a division in among FSAR chapters. The text should be corrected. E.g. in chapter 9 there is safety grade chillers and ventilation system and also in chapter 8 emergency DGs, in chapter 9 auxiliaries of EDGs and in chapter 10, RS system are contained. - Page 7-14 in definition of safety class 2; the statement “their failures being normalized for the design basis accident” is not clear. - Page 7-15 item 7.1.1.2 “I&C important to safety” this is not fully in accordance to OPB .The title shall be changed. - Editorial correction is required for Page 7-19 in no. 2 the fuel channel is not correct. It may be safety system channel. Design bases of APCS shall clearly be given. Reference given to chapter 15(page 7-35) is not acceptable. For example the design bases of APCS that it shall automatically control the plant during first 30 min of accident shall be given among DB of APCS. (And all other relevant DB such as Number of control channels, their independency and separation of normal and safety control system,… ) |  |
| Reply 28 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Мany provisions are unclear and call for extra comments |  |
| DECISION No 28 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment is accepted and require correction will be included in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 29 | FSAR: 7 FSAR Section 7.2 |
| Recommendation: The first row in table7.2-2 related to FSAR sections shall be deleted. This method for referring is not correct. And the sections referred are not exact ones |  |
| Reply 29 | FSAR: 7 FSAR Section 7.2 |
| Reply: Upper line was added to Table 7.2-2 upon request of IAEA experts and NPPD specialists |  |
| DECISION No 29 | FSAR: 7 FSAR Section 7.2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The line will be deleted from the Table in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 30 | FSAR: 7 FSAR Section 7.2 |
| Recommendation: Table 7.2-3 no information on detectors are given. Generally there is no (or not enough) information related to the sensor for different measurement their type and principle of measurement their safety class and qualification… e.g. level measurement in SGs |  |
| Reply 30 | FSAR: 7 FSAR Section 7.2 |
| Reply: Table 7.2-3 addresses the arrangement of neutron flux detectors. It is absolutely irrelevant to level measurement in SGs |  |
| DECISION No 30 | FSAR: 7 FSAR Section 7.2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: A clarification will be provided in the text related with NFME in FSAR Rev.. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 32 | FSAR: 7 FSAR Section 7.1.1 |
| Recommendation: Page 7-32 Item 7.1.1.8 paragraph 4: engineered safety features activation or removal from services through TLS-U that is in class 3 is not acceptable. Justification is required |  |
| Reply 32 | FSAR: 7 FSAR Section 7.1.1 |
| Reply: Comments are not accepted. The mentioned information could have been requested on stages of approval of TA, technical design and PSAR. After all the complexes have been manufactured, accepted by NPPD and NNSD representatives, supplied and installed at BNPP, a. m. comments look at least incorrect. Besides, Guide 1-70 contains clear-cut information on additional data to be included into FSAR as against PSAR. Please, be strictly adherent to requirements set forth in Guide 1-70 |  |
| DECISION No 32 | FSAR: 7 FSAR Section 7.1.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: in FSAR Rev. 1 in item 7.1.1.8 (2nd para), the following will be corrected: "engineered safety feature" will be change to "process protection" |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 33 | FSAR: 7 FSAR Section 7.2.1 |
| Recommendation: Usage of abbreviation as it is applied is not appropriate. For example TTT (thermoelectric temperature transducer) and CDC TTT, E-CPS which are used in page 7-51 in fig 7.2-1 in table 7.2-4… are not in abbreviation list. It is better in the fig and in title of table and in the text for the first time its complete name be given. The same for all other cases |  |
| Reply 33 | FSAR: 7 FSAR Section 7.2.1 |
| Reply: We suggest supplementing the list of abbreviations with the following: CDC TTT - Compensation device of connection of TTT TTT - Thermoelectric temperature transducer E-CPS - Equipment of control and protection system SC - Shielded cable |  |
| DECISION No 33 | FSAR: 7 FSAR Section 7.2.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be introduced in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 34 | FSAR: 7 FSAR Section 7.2.1 |
| Recommendation: Reliability indices given in page 7-90 are based on calculation which do not seems to be predictive as actual Reliability indices. It is required actual Reliability indices related to any operational experience also be given |  |
| Reply 34 | FSAR: 7 FSAR Section 7.2.1 |
| Reply: The reply to the given comment is presented in Reply 2.11 of PSAR Supplement No.1. Item 7.2.1.6 FSAR shall be supplemented with the following text: "On the basis of calculations given in PSA (18.BU.1 0.0.00.VAB.PR) probability of failure of EP electric part to actuate by demand is 6,7х10-8. On the basis of calculations given in PSA (18.BU.1 0.0.00.VAB.PR) the maximum value of probability of failure within one safety channel is less than, than 1х10-4 per one demand". The calculations were performed on the basis of statistical data on reliability of accessories, obtained by the results of tests and operation experience |  |
| DECISION No 34 | FSAR: 7 FSAR Section 7.2.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be introduced in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 35 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-99 item 7.3.1.2.1. System shellfish removal VB is not safety system. The same for service water supply system (it is written VO which should be VC) |  |
| Reply 35 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Item 7.3.1.2.1, line 14 shall read: - service water supply VE; - VC will be deleted; - VB will be deleted if required; |  |
| DECISION No 35 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be introduced in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 36 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-99 it is not clear that detailed algorithms of the operation for each process system shall be developed or are developed |  |
| Reply 36 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Item 7.3.1.2.1, last paragraph shall read: "See Supplement D for detailed algorithms for each process system" |  |
| DECISION No 36 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be introduced in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 37 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-104 with respect to "voting" more clear information is required. - What exactly is meant by “the signals are not reliable” and how it is determined? Also the Timing required for checking should be specified. - Regarding that “in case three signals are non-reliable output signal is provided”. What kind of output signal is provided? it is required to justify that it will not cause spurious signal to actuate EP or starting safety system that could have adverse effect on plant safety |  |
| Reply 37 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Page 7-104, paragraph 1 shall be supplemented with the following: “Signal non-reliability is understood as failure of output component of equipment for logical processing of signals communication line fault” |  |
| DECISION No 37 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply will be introduced in FSAR Rev. 1. and the criteria for the failure also will be given |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 38 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-107 item 7.3.1.2.9 it shall explicitly mentioned in the FSAR, that the plant shall be automatically controlled during the first 30 min of accident then the possibility of operator actions should be written. In addition it shall be clearly mentioned this possibility is only related to switching off procedure or it is also possible for more control such as staring a system or other controls such as change in line up of system e.g. for TH. Also if it is only for safety system or other system e.g. TA pumps. - As it is in PSAR restrict regulation in operating procedure shall govern operator interfere. Regarding the safety importance of the issue it shall be addressed in the FSAR. - It is clear that table7.3.1.2-1 is not complete, other system/equipment shall be included, such as TJ valves, TW system. completeness of table7.3.1.2-1 should be discussed in the meeting |  |
| Reply 38 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: 1) The concept of control bans cancellation is set forth in detail in item 7.3.2.1.1. 2) Table 7.3.1.2-1 is in full compliance with WD and equipment manufactured according to a. m. WD |  |
| DECISION No 38 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The issue will be discussed in FSAR-06 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 40 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-114 the method for recognition non-reliable measurements is not mentioned |  |
| Reply 40 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: line 2 shall read: "- non-reliability of measurements (signal from sensor < 4 mА or >20 mА)" |  |
| DECISION No 40 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 42 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-117 item 7.3.1.3.1; table 7.3.1.3-3 is not given |  |
| Reply 42 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: The following shall substitute for paragraph 3, item 7.3.1.3.1: "Generation algorithms for safety system actuation are given in Supplement D" |  |
| DECISION No 42 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the reply |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 43 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-117 items 7.3.1.3.1and 7.3.1.3.2 - The statement "An initial event concurrency with loss of power, external effects (shock wave, aircraft crash, seismic effects) have been considered in Chapter 3 of the PSAR". Is not correct. - The same for statement "Calculated parameter operational limits under any operating conditions and the margins between each operating mode and the level considered typical for emergency conditions onset are presented in Chapter 16 of the PSAR" |  |
| Reply 43 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Item 7.3.1.3.2: substitute "Chapter 17" for "Chapter 16" |  |
| DECISION No 43 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The FSAR Rev. 1 shall be revised according to the following: - the first bullet will be deleted from the text; - the second bullet (item 7.3.1.3.2) shall be revised; |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 44 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-117 items 7.3.1.3.3; please provide information that regarding "ESFAS TPTS cabinets of each individual channel are supplied with power from 220 V d.c. boards of the two SS channels belonging to the same subsystem" will not cause dependent and common cause failure |  |
| Reply 44 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: The required explication is given in Chapter 8 of FSAR |  |
| DECISION No 44 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The issue shall be considered in FSAR-08 by the Contractor |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 45 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-123 In item 7.3.1.3.4; relevant information for sensors in the RPV, specially for the one considered to be used during BDBA should be given |  |
| Reply45 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Level sensors in RPV reactor are not related to PCSS and are described in Section 7.5 of FSAR |  |
| DECISION No 45 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: see agreement No. 29 of Appendix B1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 46 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-123 item 7.3.1.3.7; Calculation values of measurement error may be not predictive of real error. It is required actual measurement error be also given. For example: errors during tests, or any operational experience |  |
| Reply 46 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: Judging by reference unit (Kalinin NPP, Unit 3) operation pattern, measurement accuracy exceeds calculation values as the latter were obtained by conservative method |  |
| DECISION No 46 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The reply is accepted and the following will be included in FSAR Rev.1 item 7.3.1.3.7: "measurement accuracy exceeds calculation values as the latter were obtained by conservative method" |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 47 | FSAR: 7 FSAR Section 7.3.1 |
| Recommendation: Page 7-123 item 7.3.1.3.7; add to the table error of level measurement in RPV |  |
| Reply 47 | FSAR: 7 FSAR Section 7.3.1 |
| Reply: level sensors for reactor RPV are related to PCSS and described in Chapter 7.5 of FSAR |  |
| DECISION No 47 | FSAR: 7 FSAR Section 7.3.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: see agreement No. 29 of Appendix B1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 49 | FSAR: 7 FSAR Section 7.4.1 |
| Recommendation: Page 7-130; safe shut down state is defined only for cold shut down state not for hot shut down state |  |
| Reply 49 | FSAR: 7 FSAR Section 7.4.1 |
| Reply: Safe shutdown, unlike emergency shutdown, is executed mainly by normal operation systems and not by safety systems |  |
| DECISION No 49 | FSAR: 7 FSAR Section 7.4.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In Russian terminology, the term "safe shutdown" is used for both hot shutdown and cold shutdown |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 50 | FSAR: 7 FSAR Section 7.4.1 |
| Recommendation: Page 7-131in Table 7.4-1: Table shall be corrected. - Under de-energization condition the TA, RR, UD systems are not available. In case that connection to the common DG is considered in Table 7.4-1, it shall be taken into account that automatic loading to the common DG is not acceptable because it is not DB for a.m. system and possibility of loading these systems to common DG is considered for BDBA. Issue shall be discussed in the meeting. - In addition in this table it shall clearly be defined that for operability of each system what other system shall also be operable. For example for operability TA system TB, TN, TD, RQ, TC and TF are required. - Required Support system also shall be mentioned such as ventilation system. Table 7.4-2 in Page 7-132 is not prepared for all condition as are in Table 7.4-1. - UJ shall be changed to VJ - UE shall be changed to VE |  |
| Reply 50 | FSAR: 7 FSAR Section 7.4.1 |
| Reply: Table 7.4-1: substitute VJ and VE for UJ and UE. Other issues are to be discussed at the meeting |  |
| DECISION No 50 | FSAR: 7 FSAR Section 7.4.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: - 1st & 2nd bullet: The Table 7.4-1 will be checked by the Contractor according to the comment and FSAR Rev. 1 will be corrected, if required. - 3rd – 5th bullets: the comment is discussed and reply is accepted |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 51 | FSAR: 7 FSAR Section 7.4.1 |
| Recommendation: Information in Table 7.4-3 in Page 7-134 is not clear. In column five for all condition it is written that cooling is not required while cooling is the main function and always is required. If it is related to the cooling down of the plant it shall clearly be mentioned. In title column one for condition should be specified as table 7. 4-4. In column two and three, there are condition in chapter 15 that EP actuation and also actuation of PRZ PSD is actuating but they are not mentioned in table. In column 4 for all condition it is written compensating the coolant loss is not required. It is clear that cooling water in secondary shall be compensated. And it should be mentioned for how long compensating the coolant loss in primary is not required |  |
| Reply 51 | FSAR: 7 FSAR Section 7.4.1 |
| Reply: “Cooling” is understood as power unit transfer to cold state |  |
| DECISION No 51 | FSAR: 7 FSAR Section 7.4.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment was discussed and it will be corrected in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 53 | FSAR: 7 FSAR Section 7.5 |
| Recommendation: Page 7-156 statement "All instrumentation located on safety panels of MCR and ECR (MCR-SP, ECR-SP) are related to class 2 ;the rest instrumentation, described in the given section are of class 3" do not seems to be correct because there are other safety class 2 instrumentation that are on main panel and are safety class 2 |  |
| Reply 53 | FSAR: 7 FSAR Section 7.5 |
| Reply: In the last paragraph of item 7.5, substitute "indicating instrumentation" for "instrumentation" |  |
| DECISION No 53 | FSAR: 7 FSAR Section 7.5 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment was discussed and paragraph before item 7.5.1 will be expanded in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 54 | FSAR: 7 FSAR Section 7.5.1 |
| Recommendation: Table 7.5.1.1-1 List of safety systems, should be completed other system or element such as level monitors in RPV, containment sump. Containment isolation valves and locks, hydrogen concentration monitor should be mentioned. All instrumentation for radiation and pressure monitor are not mentioned. And also in the first row of table TH 15,25,35,45 pumps shall be deleted and fuel pool cooling system shall be added. TL10 shall be included to the table. Ventilation systems of the rooms MCR, ECR, DG rooms (ZX, ZK1 and ZK2) and pump house (ZM 4, 5) shall also be included to the table. Wide range core exit temperature up to 1200 C (if it is not on console), indications related to fuel pool temperature are not mentioned (important parameter and signalling may be given in a separate table). In addition indicators for Seismic intensity and pressurizer safety valves position are among class two and are not mentioned. In addition, related to the issue of applying LBB it is required relevant indication be added to safety panel |  |
| Reply 54 | FSAR: 7 FSAR Section 7.5.1 |
| Reply: Table 7.5.1.1-1 contains the list of safety systems located on MCR/SCR panels. System you offer cannot be included into a. m. Table. For instance, ventilation in ZM4,5 Building is arranged in LCPs located in the same buildings |  |
| DECISION No 54 | FSAR: 7 FSAR Section 7.5.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: In FSAR Rev. 1 the Table 7.5.1.1-1 will be revised for the following, if required: - TL-10; - Ventilation of ZX; - UF 40-70; |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 56 | FSAR: 7 FSAR Section 7.5.1 |
| Recommendation: Page 7-161: statement "Coincidence of such events as severe design-basis accident and aircraft crash is not considered in the design" is not related to the rest of the text. It needs more explanation |  |
| Reply 56 | FSAR: 7 FSAR Section 7.5.1 |
| Reply: Item 5.1.3, paragraph 2, reads that incomplete information on post-accident monitoring is displayed on SCR (which is not the case with MCR). For this reason, coincidence of accident and MCR destruction is not considered |  |
| DECISION No 56 | FSAR: 7 FSAR Section 7.5.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: 2nd para of Item 5.1.3, will be deleted |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is not considered. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 57 | FSAR: 7 FSAR Section 7.5.1 |
| Recommendation: Page 7-161: The safety class and seismic category of the post-accident instrumentation with extended scale shall be given. In Table 7.5.1.3-1 Wide range core exit temperature up to 1200 C is not mentioned |  |
| Reply 57 | FSAR: 7 FSAR Section 7.5.1 |
| Reply: As the indicators are located on MCR panels, they are referred to class 2 as per OPB88/97 and seismic stability category 1. Pos. 3? Table 7.5.1.3-1 gives coolant temperature scale |  |
| DECISION No 57 | FSAR: 7 FSAR Section 7.5.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The following information will be included in FSAR Rev. 1: - A column will be added to tables 7.5.1.3-1 and 7.5.2.3-1 to indicate safety class as per OPB; - The require explanation will be added according to Russian version; |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 58 | FSAR: 7 FSAR Section 7.5.1 |
| Recommendation: Page 7-163: Explanations Regarding PS function are not indication of loss of primary integrity for primary to secondary leak and inter system LOCA. Related to CC function containment locks also should be considered. For functions CS and HS, why SG PSD and YR system are not considered? |  |
| Reply 58 | FSAR: 7 FSAR Section 7.5.1 |
| Reply: The text of paragraph 2, page 7-163 shall be supplemented with the following: "Displays are located on safety panels to indicate leakage from primary to secondary circuit" |  |
| DECISION No 58 | FSAR: 7 FSAR Section 7.5.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment shall be checked for its correctness |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 59 | FSAR: 7 FSAR Section 7.5.2 |
| Recommendation: Page 7-164 justification is required with respect to adequacy of accuracy of 350 mm indication of position of all the control rods along the whole height of the core in MCR and ECR digital boards |  |
| Reply 59 | FSAR: 7 FSAR Section 7.5.2 |
| Reply: No justification is required. CPS equipment supplied to BNPP has accuracy of 350 mm |  |
| DECISION No 59 | FSAR: 7 FSAR Section 7.5.2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: see agreement 21 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 60 | FSAR: 7 FSAR Section 7.6.1 |
| Recommendation: Page 7-179 Item 7.6.1.2 the logic for reactor coolant overpressure protection system at low coolant temperature with respect to prohibition of YT system stop valves to operate should be explained clearly and it shall be justified that it will not impair functionality of TY when it is required (the same for low pressure TH pumps). Safety classification of the system shall be given (or in case that it is a part of other system it should be mentioned). - Page 7-179 Item 7.6.1.2 the logic for reactor coolant overpressure protection system at low coolant temperature with respect to prohibition of YT system stop valves to operate should be explained clearly and it shall be justified that it will not impair functionality of TY when it is required (the same for low pressure TH pumps) . Safety classification of the system shall be given (or in case that it is a part of other system it should be mentioned). - Item 7.6.1.1 Second dash it should be specified, what exact isolation system is this. Is it a part of containment isolation system? - Item 7.6.1.3 ТN is not primary circuit emergency and scheduled cool down system. It needs correction. In addition control logic “The gate valves are closed automatically in case the primary pressure is more than 1.8 MPa” is not in agree with overpressure protection system at low coolant temperature that it is for 3,5 MPa when coolant temperature is below 100 °С AKZ of a.m. gate valves shall be given in this case availability of safety valves on TH system assigned for cold over pressure protection, shall be assured, therefore it is required to check that a.m. safety valves will not be isolated by closing the gate valves. - In Item 7.6.1.5 description and safety class for polar crane control system and control system of refueling system shall be given. |  |
| Reply 60 | FSAR: 7 FSAR Section 7.6.1 |
| Reply: Comments are not accepted. Additional comment is required |  |
| DECISION No 60 | FSAR: 7 FSAR Section 7.6.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment was discussed and the comment will be considered in FSAR-06. In addition in item 7.6.1.3, the term "TN" shall be changed to "TH" in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 61 | FSAR: 7 FSAR Section 7.6.1 |
| Recommendation: Page 7-181 As it was in previous comment, The fire detection system shall be in safety class two, Regarding the control logic “generation of commands for ventilation systems switching off in the rooms and devices where fire has appeared, switching on the systems of smoke removal and air retention in the staircases” it is clear that it is not acceptable a signal from one safety class 4 fire detection system which may be a spurious signal could isolate the vital ventilation system. It is required in page 7-180 the Single failure in the fire detection means, be completed with consideration of spurious signal. What is the control logic for "these four announcers integrated into two trains"? |  |
| Reply 61 | FSAR: 7 FSAR Section 7.6.1 |
| Reply: According to Chapter 7 FSAR, fire detection equipment was referred to class 4N as per OPB 88/97. Equipment classified as above was manufactured at TENZOR plant, accepted by the Principal and supplied to BNPP. For this reason, it does not look possible to change equipment class in FSAR |  |
| DECISION No 61 | FSAR: 7 FSAR Section 7.6.1 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: According to Chapter 7 PSAR and design documents, fire detection equipment was referred to class 4N as per OPB 88/97. Additional discussion will be held in Moscow between VO "Safety" and ZAO.ASE regarding seismic categories of AFPS and the results will be sent to NPPD/NNSD by the end of April. |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 62 | FSAR: 7 FSAR Section 7.6.2 |
| Recommendation: Page 7-186 item 7.6.2.1 control logic "1 out of 1", is not mentioned in item 7.6.1.6.1 in Page 7-180 |  |
| Reply 62 | FSAR: 7 FSAR Section 7.6.2 |
| Reply: Item 7.6.1.6.1 gives system design operation, while Item 7.6.2.1 – system re-configuration in case of failure |  |
| DECISION No 62 | FSAR: 7 FSAR Section 7.6.2 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The comment was discussed and reply is accepted. In item 7.6.1.6.1 the term "ESFAS" shall be deleted and the section shall be reviewed and corrected by the Contractor. The required information and changes shall be introduced in FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

| AEOI | NUCLEAR POWER PLANT “BUSHEHR” POWER UNIT 1 FSAR ANALYSIS |
| --- | --- |
| ISSUE No. 63 | FSAR: 7 FSAR Section 7.5 |
| Recommendation: In appendix B, a list shall be provided for safety panels of MCR to define indications. Such as; ICSS, or FSDA pipelines. Drawing of other panel such as console reactor work station could be presented |  |
| Reply 63 | FSAR: 7 FSAR Section 7.5 |
| Reply: According to Section 7.5, Supplement В contains front sides of 8 safety panels (2 for each channel). What other list is required? |  |
| DECISION No 63 | FSAR: 7 FSAR Section 7.5 |
| DECISION ON UPDATE OF FSAR CHAPTER 7 ON RESULTS OF DISCUSSIONS OF NPPD COMMENTS AND CONTRACTOR’S REPLIES: Agreement: The abbreviation of ICSS, FSDA will be specified in general list of abbreviation of FSAR Rev. 1 |  |
| EXPERT CONCLUSION ON CORRECTNESS OF CONSIDERATION OF THIS COMMENT IN CHAPTER 7 FSAR REVISION 2 The comment is correctly and fully considered. No comments. |  |

# 3. Findings and recommendations

3.1. The information presented in Chapter 7 (revision 2) of the Final Safety Analysis Report in general corresponds to the structure of Guide 1.70.

3.2. The necessary scope of additional information, recommendations for correction of the considered document are reflected in the present expert review report.

This also refers, inter alia, to the issues of confirming the reliable functioning and operation of the Power Unit without violation of safe operation limits and conditions with account of influence on safety of external effecting factors, including operator’s erroneous actions.

3.3 In experts’ opinion, prior to obtaining the BNPP-1 Commercial Operation License, the presented Chapter 7 of the FSAR requires a serious update to confirm observance of safe operation limits and conditions (a more complete analysis of substantiation of design compliance with general design criteria and safety criteria), comprehensive analysis of potential interference of an operator till expiration of temporary ban after actuation of safety systems, full observance of the requirements of regulatory documents and other substantiating documents (including documentation of supplier-manufacturers), and also with account of the comments stated in the present report.

3.4 Additional materials and modifications reflected in Addendum 1 to the PSAR have not been included to Chapter 7 of the FSAR, which resulted in degradation of individual FSAR sections as compared to the PSAR.

3.5 Chapter 7 of the FSAR does not reflect modifications introduced to the APCS design after issuance of the FSAR, neither has it given the results of performed acceptance tests of the Power Unit APCS subsystems and of software-and-hardware complexes.

3.6 Chapter 7 of the FSAR does not contain information and analysis proper on radiation monitoring and “black box” subsystems.

3.7 The final conclusion on sufficiency of safety substantiation of APCS tools and systems can be made on the results of discussing the comments and recommendations with the document developers and analysis of updated materials.

The document developers are recommended to:

- special attention should be drawn to comments (2.1-10)(2.1-32) as they can have impact on safe operation of the unit. Control algorithms discussed in these comments should be thouroughly revised and verified. Other comments to Chapter 7 of the FSAR are not a matter of principle, decisions on them require supplemention and revision of the Chapter contents;

- consider recommendations of the present expert review report when updating Chapter 7 of the FSAR;

- notify regulatory authorities of the activity aimed at rectification of the above-listed comments.

# References

## i. List of documents considered during review

- Chapter 7 “Instrumentation and control systems (I&C)” of the document “Final Safety Analysis Report. Power Unit No.1. “Bushehr” NPP 49.BU.1 0.0.ОО.FSAR.RDR001 (revision 2, issue December 2014).

- Minutes of discussion results of the comments made during review of Chapter 7 "Instrumentation and control systems (I&C)” of the FSAR, revision 0, with the decisions made on every comment.

- Technical decisions taken on the results of the Power Unit commissioning.

## Ii. List of documents, which requirements have been selected as expert assessment criteria

- PNAE G-1-011-97 (OPB-88/97). General provisions of NPP safety assurance, section 5.2.6.

- PNAE G-1-024-90 (PBYa RU AS-89). Nuclear safety regulations for NPP plants.

- PBYa 04-74. Nuclear safety regulations for NPPs, section 4 with Amendment No. 1.

- NP-026-04. Requirements to control systems important for NPP safety.

- STO 1.1.1.01.0678-2007. Main regulations of NPP operation assurance (OPE-AS), 4th edition.

- RD 210.006-90. Regulations for NPP process design.

- 50-S-O. NPP safety - operation, commissioning and decommissioning of NPP. A Code of Practice. Vienna, 1979. Volume 3.

- 50-SG-D8. Instrumentation and control systems important to safety in nuclear power plants. 1984.

- 50-SG-O3. Operational limits and conditions for nuclear power plants. 1980.

- US NRC Regulatory Guide 1.70. Standard Format and Content of Safety Analysis Report of Nuclear Power Plants. 1978.

- NUREG-0800. Standard Review Plan for the Review of Safety Analysis Reports for Nuclear Power Plants LWR Edition. April 1996.