## Self-assessment report summary
Row | SOER Report | Report Title | Recommendation No. | Recommendation Title | Recommendation Status in WANO Peer Review 2019 | Actions Taken | NPP Self -Assessment
1 | 1999-1 | Loss Of Grid | 5d | Inaddition, incorporate the following into initial and continuing operator training: Incorporate aspects identified in recommendation 7 during periodic emergency plan drills or simulations. | FAR | BNPP telecommunication systems use two communication means (fiber and radio) for offsite communication. When voltage is disconnected or dropped (in emergencies) in case of fiber communication disconnection, the radio communication will still be operable and plant personnel can have offsite communication by dialing 5 before the phone number. 1- Instructions for eliminating the accident conditions were placed in the Reactor Shift Supervisor and the Unit Shift Supervisor workplaces. 2- The CAOU instruction was developed and is in the stage of removing the comments and obtaining final approval. 3- Once every four year, the comprehensive drill on the subject of release of radioactive materials into the surrounding environment is performed in which the provincial and national organizations take part and BNPP shift personnel are actively involved. 4- Once a month, every shift carries out the scenario exercise for responding to accidents in the simulator of the training center. 5- Once a month for every shift, the emergency preparedness exercise is carried out in the simulator of the training center. 6- Once a year for every shift, the emergency preparedness exercise for responding to the Beyond Design Basis Accidents is carried out in the simulator of the training center. 7- Once a month for every shift, the personnel continuing training program is carried out in the simulator. | SAT Satisfactorily implemented
2 | 1999-1 | Loss Of Grid | 7 | Review the plant’s ability to respond to loss of-off-site-power conditions to identify potential complications when nonessential power is lost for an extended period of time. Implement changes that are appropriate. The review should include the following, as a minimum: • The plant’s ability to maintain effective communications, both internally and externally, when normal and/or off-site power sources are lost and the station is being powered from emergency power sourcesThis includes the capability to contact off-duty plant personnel and outside organisations under regional blackout conditions when mobile (cellular) telephone and pager systems may be stressed; • The plant’s emergency response processes, including off-site notification capabilities and plant personnel contact information; • The plant’s ability to access important or critical plant information (e.g., design drawings, calculations, and tagging programs) normally contained in electronic files that would be needed during a loss of power; | AI | In accordance with the order No. LTR-1000-176866 dated 7 August 2017, the wireless MZ system of Unit-1 in the antenna covering area provided in the approved design of the BNPP became operational. This system is used as an internal communication reserve system. Furthermore, since all the BNPP telecommunication systems are fed by the busbar which is connected to the plant emergency diesel generator and in addition to this, all the telecommunication systems are equipped with local battery room, these batteries are able to feed these systems for 8 hours in case of voltage disconnection. | SAT Satisfactorily implemented
1 | 2001-1 | Unplanned Radiation Exposures | 8 | Review plant areas to ensure that all areas with existing or potential high radiation exposure rates are identified and such areas are properly posted and controlled. This should include those areas that have the potential for changing radiation conditions. | AI | 1-According to the radiation safety procedure during operation (51.BU.1 0.00.AB.WI. RSM13740) and industrial safety procedure which were put into effect in BNPP, these locations were determined. 2- In BNPP, all doors with category 1 and 2 have been specified by the radiation indications ‎i.e. dose rate, surface contamination and airborne contamination for which the limits have ‎been indicated for every parameter ( green : safe, yellow : alert and red : going and coming ‎prohibited ) . These signs have been attached on the doors.‎ 3- All the locations with high dose rate (hot-points) in the controlled area have been specified. ‎These points have been indicated by the radiation hazard sign on which the dose rate has ‎been written down and they have been enclosed. These points have been recorded in the ‎relevant logbook and are being monitored. In order to provide information about these points ‎and the radiation condition of the working locations, information panel equipped with touch ‎screen has been installed in the entrance of radiation controlled area. ‎ 4-According to the order of BNPP manager , lock of all exit emergency doors were replaced in control access area and the keys are kept with radiation safety shift staff in radiation safety management and it is not possible to open the doors without presence of dosimetrist even if it is necessary. ‎5-Rooms with high radiation exposure hazard whose one of radiation parameters (dose rate, ‎airborne contamination or surface contamination) is red, are locked and their key is with the ‎radiation safety shift staff and coming and going into these locations is possible by ‎coordination with the radiation safety shift staff to open them and by taking into account the ‎necessary arrangements for safety and protection of the staff. ‎ 6- Radiation checklist for visiting the radiation condition of the locations has been included in the instruction No. 52BU.10.AB.WI.RSM13740. 7-Necessary provisions for recording the dosimetry data in specified time has been arranged in the logbook of the radiation safety shift supervisor | SAT Satisfactorily implemented
1 | 2002-1 | Severe Weather | 4 | Ensure plant operating procedures are available to support the various actions to be taken on site depending on the probability and severity of the weather conditions predicted. These should include: • Actions, relevant to the type of severe weather predicted at the plant, to minimise potential wind-blown debris and to ensure that barriers, drainage and pumping systems to prevent flooding are available. • Actions to maximise safety and standby equipment availability • Verification of safety related equipment and communications system operability, consumable stock levels, and staffing arrangements for the period of the predicted severe weather. | AI | Monitoring of condition of emergency power supply systems to ensure prompt detection of deterioration of performance of these systems equipment is performed by the shift operating personnel in accordance with check-lists wherein the clear criteria of admissible and emergency parameters are stated, as well as personnel actions are described when admissible and emergency parameters change. In order to control the conditions of the Emergency Power Supply System aiming at timely detection of degradation of equipment performance (safety channel Emergency Diesel Generators(EDGs) ) and to take preventive measures before their failure, taking into account the monitoring of control parameters of the equipment, the following measures will be taken: 1. developing and implementing the program for periodical technical services of EDGs - Technical service No.1 which is carried out once a month. - Technical service No.2 which is carried out once a year during the annual Planned Preventive Maintenance)PPM) - Technical service No.3 which is carried out once every 6 years during an annual PPM. 2. developing and implementing the program for periodical tests of EDGs - No-load test of diesel generator, which is carried out once every month - Load test (100%) of diesel generator, which is carried out annually and before the PPM (ППР) for 2 hours. - Stage-by-stage startup test of diesel generator with virtual loss of power of the plant, which is carried out once every 672 hours and for at least half an hour. - Load test (110%) of the diesel generator, which is carried out once every 4 years before the PPM for 1 hour 3. Developing and implementing the checklist of visits (regular visits) for controlling the conditions of equipment and systems (EDGs and the related equipment) - Checklist for operator visit which is carried out at least twice every shift 4) Developing a protocol including all the above mentioned activities together with obtaining approval of the executer and controller of the intended activity 5) Analyzing all the parameters recorded in the protocols and the archive of protocols In addition, the following programs and actions are also carried out by the Senior Process Engineering Management. In addition, the following programs and actions are also carried out by the Senior Process Engineering Management 1. Developing the program for comprehensive periodical tests of the safety channels and the post-repairs tests 2. Developing the logbook of controlling the conditions of systems important to safety for recording the tests and defects of important systems such as emergency power supply channels of category 1 and 2 3. Analyzing the performance of algorithm for stage-by-stage actuation of safety mechanism such as time of connection of the diesel generator to the safety channel Busbar in each time of conducting periodical test 4. Developing an archive for data of Top Level System of the Unit (TLSU) for controlling the implementation of periodical stage-by-stage startup test and attaching it to the Act of implementation of the test and the analysis 5. Developing databank of the conducted safety channels comprehensive tests 6. Developing the Act of comprehensive tests of safety channels stating the non-existence of problem in putting the channel in standby state. 7. Developing the data of indicators of safety channels failure and safety channel operation/performance | SAT Satisfactorily implemented
1 | 2004-1 | Managing Core Design Changes | 2a | Perform risk evaluations when making significant changes to the core operating regime or fuel design. The evaluation should address the potential for anomalous core behaviour and identify appropriate contingency plans and monitoring requirements. Review risk evaluation results and monitoring plans with a senior nuclear executive before proceeding with a significant change. In addition, members should promptly notify the industry of adverse reactor core or fuel performance events. | AI | There is no plan for change in the reactor core operating regime as well as fuel design in the near future. No need for risk evaluation. Technical decision for control rod 31-023 was taken at BNPP and was sent to NPPD to be approval. | SAT Satisfactorily implemented
1 | 2007-1 | Reactivity Management | 1b | All core reactivity changes are made in a deliberate, carefully controlled manner. Plant procedures shall specify which backup and redundant nuclear instrumentation as well as other reactor and plant indications (pressures, flows and temperatures) operators shall monitor when making reactivity changes. Reactivity changes are normally made by only one method at a time | AI | The personnel performance in the simulator of the Plant’s Human Resources and Training Center includes instructions, One of the most important ones is the “CTO” which includes the following scenarios: 1- Controlling the temperature of hot and cold air in the main circulation pumps drives 2- Controlling the leak from primary to secondary circuit based on the ILA instruction 3- Actuation/Performance of BRU-SN 4- Related to the Containment localization 5- Transferring the water of intermediate cooling circuit to the primary circuit through the (Injection and suction) system in one hour 6- Increasing the temperature of the reactor upper unit | SAT Satisfactorily implemented
1 | 2010-1 | Shutdown Safety | 12a | Training on shutdown safety for operating crews, including field operators who may be directed to perform support activities. This training should cover associated abnormal and emergency operating procedures, and any contingency actions (recommendation 10) that are being implemented during the outage. This training should reinforce management expectations regarding shutdown safety. | FAR | 1- The recommendations written in the 2010-1 have been included in the theoretical and practical training program of the newly-recruited personnel and the personnel continuing training program. 2- The scenario of personnel performance during an accident, when the reactor is in the “shutdown for repairs” conditions, exists in the scenarios of the Human Resources & Training Center and has been carried out for all shifts. | SAT Satisfactorily implemented
1 | 2011-3 | Fukushima Daiichi Nuclear Station Spent Fuel Pool/Pond Loss of Cooling and Makeup | 3 | Verify the adequacy of station abnormal/emergency operating procedures for responding to the loss of SFP cooling and/or coolant inventory and damage to dry cask(s) used for storage of spent fuel. Ensure these procedures include actions and contingencies to monitor SFP coolant level, temperature and radiation level at a location that will be accessible during accident conditions. Also, include the capability to make up coolant inventory to the SFPs during a loss of all AC power and monitor the radiation level around the storage facility or its site boundary. Perform periodic inspections to ensure the confinement, shielding, heat removal and other safety functions are fulfilled. Verify that the guidance in abnormal/emergency operating procedures can be implemented during and following severe weather, seismic events, loss of control room and flood conditions. | AI | In the instruction for TH system operation “16.BU.1 0.TH.AB.WI.ATEX.001”,the performance of operators in case of level reduction in fuel pool were indicated. Also the guide for what to do in case of temperature increase, level reduction and acid boric concentration is in preparation. In the section 10-2 of the instruction for accident prevention at Bushehr NPP “52.BU.1 0.00.AB.WI.ATEX.003”, the performance of the staff in case of blackout and loss of the spent fuel pool cooling was included. Also, the instruction for modification of the spent fuel pool level is available at Bushehr NPP. In the safe operation instruction “52.BU.1 0.00.AB.WI.ATEX.001”, the items of controlling the level, temperature and acid boric concentration of spent fuel pool and the permissible level of fluid and permissible time span for reducing it and also permissible time of temperature maximum were included. In order to cool the spent fuel pool , four pumps called TH18,28,38,48D001 and also four pumps called TH10,20,30,40D001 can be used. Also, the pumps of the systems TH71,72D001 and TD can be used for supply of water level. In case of total blackout and loss of the power supplies, first the emergency diesel generators are used and if they are not operable, the mobile diesel generators GY60,70D001 are used. The process of using the mobile diesel generators is according to the instructions 99.BU.1.00.AB.WI.PSEM15995,15910,14940,14794. | SAT Satisfactorily implemented
1 | 2013-1 | Operator Fundamentals Weaknesses операторов | 1 | Conduct a self-assessment for operations training programmes Conduct a self-assessment of the operations training programmes using ‘Self-Assessment Guide: Assessing Training Effectiveness in Addressing Operator Fundamentals’, May 2011, to understand fully their effectiveness in training on the subject of operator fundamentals. Develop corrective actions based on the results of the self-assessment to improve the quality of operator fundamentals training. | AI | Self-assessment of operator fundamental skills was performed in three areas: a. assessment of programs of training and preparing the operators b. assessment of operator fundamental skills in FSS c. assessment of operator fundamental skills in MCR Based on the results of this assessment, the following corrective actions were taken: • Translating the document of the role of operators in operator fundamental skills and implementing the related training in the Continuous Training course of the staff • Constantly investigating the events in the events investigation committee , determining the violated operator fundamental skill and preparing the corrective actions for it • conducting training for promoting teamwork skills of MCR staff • Adding the chapter “operator fundamental skills” to the Continuous Training program of training instructors The specialized workgroup on self-assessment of operators’ basic skills has been formed in the Plant and will conduct its self-assessment in accordance with the indicators included in the WANO MC document MC19/031 by the end of Mordad 1400 (22 August 2021). | SAT Satisfactorily implemented
2 | 2013-1 | Operator Fundamentals Weaknesses операторов | 2 | Perform a self-assessment of operator fundamentals as practiced Perform a self-assessment of operator fundamentals using ‘Self-Assessment Guide to Operator Fundamentals’, June 2011, to identify gaps that could cause events or reduce crew effectiveness when responding to a transient. Use the results of the self-assessment to develop corrective action designed to better focus training and coaching of operators on identified weaknesses. | AI | The specialized workgroup on self-assessment of operators’ basic skills has been formed in the Plant and will conduct its self-assessment in accordance with the indicators included in the WANO MC document MC19/031 by the end of Mordad 1400 (22 August 2021). | SAT Satisfactorily implemented
3 | 2013-1 | Operator Fundamentals Weaknesses операторов | 4a | Training should include the importance of staying in your assigned role, of challenging other team members who do not meet the intent of their roles or who step out of their role and of working together to control and monitor the plant effectively. | AI | The following items have been included in the job instructions of the Unit Shift Supervisor: 1- Adding details about the order of performing the diagnosis operation in the event of water leak in primary circuit 2- Required actions during total power disconnection of the 10 kv bus bar | SAT Satisfactorily implemented
1 | 2013-2 | Post-Fukushima Daiichi Nuclear Accident Lessons Learned” implementation | 5g | Establish site and corporate emergency plans that provide clear command and control structures, with defined lines of responsibility and accountability, for implementing response actions as deemed necessary to maintain or restore key safety functions throughout the duration of an event. | AI | personnel protection activity plan in case of accident at bushehr-1 npp ,No. 52.BU.1 0.00.AB.WI.ATEX.015 and the following documents are used in case of site emergency in order to determine the way to organize activities , determine notification order, composition of participants and distribution of responsibilities in case of accident in the site. Regulation of BNPP crisis management committee” No. 99.BU.1 0.0.GO.PL.CMC12587 in order to lay down regulations, determine requirements , duties and members of committee and also appointing the committee members in the BNPP. Procedure for organizing specialized teams of BNPP emergency operation No. 99.BU.1 0.0.GO.PRO.MRM15654 in order to determine the duties, preparedness process and manner of training these teams and also how to use them in emergencies for taking urgent measures in the process of response operation - “Instruction for how to notify emergencies in case of accident at Bushehr NPP” No. “99.BU.1 0.0.GO.INS.CMC15162. - “Procedure of emergency evacuation at Bushehr NPP” No. 99.BU.1 0.0.AB.PRO.CMC12818 in case of accident. - “Instruction of organizing the responses of medical and radiological emergencies in case of radiation accidents at Bushehr” NPP No. 99.BU.1 0.0.ABP.INS.ISM15128" - “Instruction for training and making aware the public regarding the nuclear accident” NO. 99.BU.1 0.0.GO.INS.MDOPRIA15173 - “Instruction for organizing the technical; support services in case of accident” No. 99.BU.1 0.0.AB.INS.ETD15588 In the province level, plan of protecting the public and environment in case of accident at BNPP-1 No. 84.BU.1 0.0.GO.PLN.CMC13549 was developed in order to obtain appropriate coordination of administrative organizations and organs of Bushehr province , to notify the neighboring provinces and to request help in national level. Also the structure of the system of managing the accident, the sequence of the actions, determining the notification order, composition of participants and distribution of responsibilities in case of accident. - In order to organize mutual cooperation of BNPP with civil organizations for gaining necessary preparedness for the following memoranda of understanding were developed and implemented: - “Agreement between the university of medical sciences and health and therapeutic services with BNPP operating company in nuclear accidents” No. 84.BU.1 0.0.GO.PLN.CMC16186 “Agreement between firefighting safety services of Bushehr municipality with Bushehr NPP operating company in nuclear accidents” No. 84.BU.1 0.0.GO.PLN.CMC16183 - “Agreement between Bushehr general administration of education with Bushehr NPP operating company in nuclear accidents” No. 84.BU.1 0.0.GO.PLN.CMC16189 - “Agreement between Bushehr center IRIB (Islamic republic of Iran broadcasting of education with Bushehr NPP operating company in nuclear accidents” No. 84.BU.1 0.0.GO.PLN.CMC16185. - “Agreement between Bushehr telecommunication administration with Bushehr NPP operating company in nuclear accidents” No. 84.BU.1 0.0.GO.PLN.CMC16187 - In case of accident, technical support and cooperation of regional crisis center (RCC) will be utilized according to the document “REGULATION FOR WANO MOSCOW CENTER REGIONAL CRISIS CENTER FOR NPPS WITH VVER REACTOR”. In case of accident, it will be explained how to issue the order for implementation of emergency plan and also criteria for how to obtain this order – based on the radiation level at the plant. | SAT Satisfactorily implemented
2 | 2013-2 | Post-Fukushima Daiichi Nuclear Accident Lessons Learned” implementation | 11a | Establish communication protocols and infrastructure such that plant data and emergency response information can be provided to (and received from) support organisations. | AI | • The document “procedure of organizing the crisis management structure in the NPPD Company” No. PRO-4930-22 includes the duties and roles of the NPPD Company in the event of an accident. In this document, the duties have been categorized into the following levels: 1- Operational level 2- Technical support level 3- Technical Consultation level The technical support level is the main duty of the NPPD Company at the time of occurrence of an accident or event. This level includes the following items: 1)Acting based on the crisis management policy of the NPPD Company No. emp-4100-01 2) Forming the crisis management committee in the NPPD Company 3) Foreseeing the resources and equipment for Emergencies at the Plant 4) Organizing the activities and services needed at the BNPP according to the decisions of the crisis management of the NPPD 5) Providing resources and services needed at the Plant during an emergency | SAT Satisfactorily implemented
1 | 2015-1 | Safety Challenges from Open Phase Events | 2b | Determine compensatory actions needed to detect degraded offsite power sources due to open phase conditions. For example: • real-time monitoring of phase voltages • operator training and use of designated operator functions • use of thermography scans • changes to equipment rounds or inspection criteria | AI | Currently in all internal consumption bus bars, preventive measures are implemented in order to prevent long term disconnection of phase via using controller relays and also shift staff in main control room of the plant and 400 KV substation monitor the condition for power transmission lines. Checklist for performance of staff in the working location of 10-KV bus bar in case of accident has been prepared. | SAT Satisfactorily implemented
1 | 2015-2 | Risk Management Challenges | 2 | Verify that individuals understand the RM policy or expectation requirements and feel empowered to identify risks. | AI | A: - Training courses on the subject of risk management for managers and staff of the plant were conducted - Conducting meeting on the subject of “risk management” in the council of the deputies and managers of the plant - Training workshop on the subject of “ elaboration of the procedure of the risk management of activities and processes of integrated management system” - Conducting the course of risk management for staff of the M&R department of the plant on the subject of “ M&R risk management” - Conducting two training workshops on the subject of “ identification and assessment of safety related hazards and environmental aspects” B: Following measures were carried out for culture building, familiarization and disseminating the culture of risk management: - Establishing the working groups of identification of the safety related hazards and environmental aspects in all the managements of Operating Company - Distributing the form for recording the experiences and identification of safety related hazards - Safety culture self-assessment at BNPP whose one of its criteria is the safety culture regarding risk management. C: Questions in the fields of important aspect of risk management were included in the list of the examination questions of “controlling the assessment of the knowledge of the staff and managers”. | SAT Satisfactorily implemented
2 | 2015-2 | Risk Management Challenges | 3 | Ensure that the RM policy or expectations are embedded into the following key processes that maintain plant safety: online and outage work management, operational decision-making, equipment reliability, modification and project management. | AI | - Procedure “ identification and assessment of safety related hazards and environmental aspects and determination of measures for controlling them” - Procedure “ risk management of activities and processes of management system” - Procedure “ change management” - Based on the three above-mentioned procedures, risk topic was institutionalized in the BNPP Operating Company. In the main processes of the plant including the following: - Production and operation processes - M&R processes - Technical support processes - Nuclear safety assurance processes , risks were identifies and assessed at least in the following five areas: • Organizational risks • Stakeholders related risks • Processes risks • Technology risks • Legal requirements processes For which the management of activities during operation and M&R are covered in the following issues: • Decision making in operation • Equipment reliability • Modernization and management of projects | SAT Satisfactorily implemented
3 | 2015-2 | Risk Management Challenges | 4 | Ensure that first-of-a-kind or first-in-a-while projects, complex modifications, infrequently performed tests and evolutions and emergent conditions with significant reduction in operating and design margins, are appropriately assessed with the degree of risk. | AI | Recommendation 4 - Based on the procedures “change management” and modernization”, risks related to the rare plans, complicated modernizations, rare unusual developments and emergencies which are accompanied with drastic reduction of design and operation margins are identified , assessed and if needed, control measures are determined for them. | SAT Satisfactorily implemented
4 | 2015-2 | Risk Management Challenges | 5 | Verify that, as risks increase, key decisions require escalation to a higher RM forum or level in management and, if applicable, include independent review and corporate participation. | AI | In the procedure “risk management of activities and processes” and also the procedure “ organization processes risk management” which determine the decision making levels and the level of activities and processes of the Plant , it is made sure that key decisions are transferred to higher managerial group or level and are performed by them. | SAT Satisfactorily implemented
5 | 2015-2 | Risk Management Challenges | 6 | Verify that action plans for eliminating, minimising or mitigating risks are specific, measurable, achievable, realistic and timely (SMART). Verify that changes to actions or plans are communicated and approved by appropriate leadership levels and/or decision making forums. | AI | Based on the procedure “risk management of activities and processes” and the procedure “identification and assessment of safety related hazards and environmental aspects “and determination of the their control measures for unacceptable risks and risks which have legal requirements, program of control measures is conducted and established with the participation of the department in charge of risk for removing, minimizing or reducing the risk. Based on the procedure of identification and removal of the non-conformities and taking corrective actions, actions which are transparent, realistic, measurable, time- bound and achievable are controlled and their effectiveness is assessed. | SAT Satisfactorily implemented
6 | 2015-2 | Risk Management Challenges | 7 | Verify that a self-assessment of the RM implementation is conducted using internal operating experience, observations of behaviours and checking full implementation of risk-related criteria in the PO&Cs. Ensure that identified gaps are addressed through the station’s corrective action programme. | AI | The procedure “independent assessment and self-assessment at plant” was developed with a new approach and it was planned that based on this method, executive self-assessment of risk management by use of internal operating experiences would be carried out until the end of the Iranian year 1400(ending at 21 March 2022) by full implementation of the risk criteria in the document PO&C so that the criteria conditions be determined and actions for improving them be determined and implemented. | SAT Satisfactorily implemented
1999-1: Loss Of Grid
2001-1: Unplanned Radiation Exposures
2002-1: Severe Weather
2004-1: Managing Core Design Changes
2007-1: Reactivity Management
2010-1: Shutdown Safety
2011-3: Fukushima Daiichi Nuclear Station Spent Fuel Pool/Pond Loss of Cooling and Makeup
2013-1: Operator Fundamentals Weaknesses операторов
2013-2: Post-Fukushima Daiichi Nuclear Accident Lessons Learned” implementation
2015-1: Safety Challenges from Open Phase Events
2015-2: Risk Management Challenges