|  | Московский центр Всемирная Ассоциация Организаций, эксплуатирующих Атомные Электростанции ВАО АЭС – МЦ Россия, 109507, Москва, Ферганская ул., 25 Тел. +7 495 376 15 87 Факс: +7 495 376 08 97 info@wanomc.ru |
| --- | --- |

REQUEST

for technical or organizational information through WANO

- NPP/Organization: SE “Rivne NPP” / SE NNEGC “Energoatom”

- Information request topic: causes of failures of air-operated valves’ control units

- Information request purpose: operating experience exchange on air-operated valves’ control units

- Description of the problem: Rivne NPP operates several air-operated valves with control units manufactured by the Kiev Central Valves Designing Bureau (KTsKBA, Ukraine) of the following types: - UF96569-012.00.00-01; - UF96557-008.00.00; - UF96557М-008.00.00-01; - UF96558-006.00.00; - UF96559-008.00.00 Spontaneous AOV position change was observed several times when there were no control signals from the switches and/or automation and interlocks.

- Specific questions: - Do you operate AOV control units of the above types at your plants? - Have you experienced failures/malfunctions of AOV with the above types of control units? If yes, what were the causes of failures/malfunctions?

- Organizations to be requested: WANO MC

- Department initiating the request: Reliability, service life, and lifetime extension department