## Sheet1
[10 empty] | Current Date : | 2017-10-24
|  |  | R.1 | AFI LF.1-1 Corrective Measures - Corrective measures in the field of Management and Leadership | اقدامات اصلاحی AFI LF.1-1 | Responsible entity Manager of management system and supervision | Deadline | STATUS | R.1 | Change DATE : | 2017-10-24 09:52
1LF.1-1 | 1 | LF.1-1 | 1.1 | Categorizing the plant events according to the type of event and system of equipment which is defective | طبقه بندي رويدادهاي نيروگاه بر اساس نوع رويداد و سيستم يا تجهيزي که داراي ايراد مي باشد؛ | Manager of management system and supervision / Head of Operating experiences group | 2015-10-22 | SAT | 1.1
1LF.1-1 | 1 | LF.1-1 | 1.2 | Drawing up the order for re-evaluating all of the events in terms of effectiveness of corrective measures and their repetition and the measures which were taken | تنظيم ابلاغيه جهت ارزيابي مجدد کليه رويدادها از ديدگاه موثر بودن اقدامات اصلاحي و تکراري بودن آنها و تصميمات اتخاذ شده؛ | Manager of management system and supervision | 2015-10-31 | SAT | 1.2
1LF.1-1 | 1 | LF.1-1 | 1.3 | Analyzing the evaluation of events on the basis of notification issued and developing the report | انجام آناليز ارزيابي رويداد ها بر اساس ابلاغيه صادره و تهيه گزارش؛ | Manager of management system and supervision / Chairman of evaluation committees | April 31, 2016 | AI | 1.3
1LF.1-1 | 1 | LF.1-1 | 1.4 | Developing procedure for evaluation of effectiveness of corrective measures in the area of events | تهيه دستورالعمل ارزيابي موثر بودن اقدامات اصلاحي در حوزه رويدادها؛ | Manager of management system and supervision / Head of Operating experiences group | 2015-11-21 | SAT | 1.4
1LF.1-1 | 1 | LF.1-1 | 1.5 | Analysis of events annually and submitting report to high committee of safety | آناليز و تحليل رويدادها بصورت ساليانه و ارائه گزارش به کميته عالي ايمني؛ | Manager of management system and supervision / chairman of nuclear safety self-assessment committee | Permanent one-year periods | SAT | 1.5
1LF.1-1 | 1 | LF.1-1 | 1.6 | Sending letter to NPPD as for performing independent analysis of events related to BNPP and taking necessary measures for improvement | ارسال نامه به شرکت توليد و توسعه در رابطه با انجام آناليز مستقل رويدادهاي مربوط به نيروگاه اتمي بوشهر و اتخاذ تدابير لازم جهت بهبود؛ | Manager of management system and supervision | 2015-10-22 | SAT | 1.6
1LF.1-1 | 1 | LF.1-1 | 1.7 | Revising the procedure of orders and notifications and determining the strict and cautionary requirements in decision-taking | بازنگري دستورالعمل دستورات و ابلاغيه ها و تعيين الزامات سخت گيرانه و محتاطانه در اتخاذ تصميمات؛ | Manager of management system and supervision | 2015-03-10 | SAT | 1.7
1LF.1-1 | 1 | LF.1-1 | 1.8 | Pursuing the approval and ratifying the procedure of technical decisions by NNSD and NPPD | پي گيري تاييد و تصويب دستورالعمل تصميمات فني توسط نظام ايمني و شرکت توليد و توسعه؛ | Manager of management system and supervision / Planning and Technical Documents manager | 2015-07-20 | SAT | 1.8
1LF.1-1 | 1 | LF.1-1 | 1.9 | Revising or developing the new procedure (including technical, managerial decisions) in BNPP (procedure in the level of plant) and receiving the necessary approvals. | بازنگري يا تدوين دستورالعمل جديد براي اتخاذ تصميمات (شامل تصميمات فني، مديريتي) در نيروگاه (دستورالعمل در سطح نيروگاه) و دريافت تاييدات لازم؛ | Manager of management system and supervision / Planning and Technical Documents manager | 2016-03-19 | SAT | 1.9
1LF.1-1 | 1 | LF.1-1 | 1.1 | Sending letter to NPPD for establishing an independent and high supervision committee in order to analyze and evaluate event investigation reports and the adequacy of corrective measures taken and technical decisions which were taken. | ارسال نامه به شرکت توليد و توسعه مبني بر استقرار یک کمیته نظارتی عالی و مستقل به منظور ارزیابی وتحلیل گزارشات بررسي رويدادها وکفایت اقدامات اصلاحی اتخاذ شده و تصميمات فني؛ | Manager of management system and supervision | 2016-03-19 | AI | 1.1
1LF.1-1 | 1 | LF.1-1 | 1.11 | Establishing the methodology of ASSET and HPES in the investigation of events and incidents in plant by using the capacities of technical support contracts. | استقرار متدولو‌ژي ASSET و HPES در بررسي حوادث و رويدادها در نيروگاه با استفاده از ظرفيت هاي قرارداد پشتيباني فني؛ | Manager of management system and supervision | 2016-09-20 | FAR | 1.11
1LF.1-1 | 1 | LF.1-1 | 1.12 | Using the principle of similar equipment in drawing up the corrective measures and making necessary changes in the procedure of investigating events and receiving necessary approvals: (drawing up correcting measures based on the principle of corrective and preventive measures in similar equipment ). | استفاده از اصل تجهيزات مشابه در تنظيم اقدامات اصلاحي مربوط به بررسي حوادث و رويدادها و ايجاد تغييرات لازم در دستورالعمل بررسي حوادث و دريافت تاييدات لازم؛ (تنظيم اقدامات اصلاحي بر اساس اصول اقدامات اصلاحي و پيشگيرانه در تجهيزات مشابه) | Manager of management system and supervision / chairman of events and accidents investigation committee | 2016-03-19 | AI | 1.12
1LF.1-1 | 1 | LF.1-1 | 1.13 | Adding the requirement of comparison of technical decisions and notification orders with FSAR (NPP Final Safety Assessment Report) in the procedure of technical decisions | اضافه نمودن الزام مقايسه تصميمات فني اتخاذ شده و دستورات ابلاغي با FSAR در دستورالعمل تصميمات فني | Manager of management system and supervision / Planning and technical documents manager | 2016-03-19 | SAT | 1.13
1LF.1-1 | 1 | LF.1-1 | 1.14 | Adding the requirement of comparison of notification orders with FSAR in the procedure of notifications and orders | اضافه نمودن الزام مقايسه دستورات ابلاغي با FSAR در دستورالعمل ابلاغيه ها و دستورات | Manager of management system and supervision | 2016-03-19 | SAT | 1.14
1LF.1-1 | 1 | LF.1-1 | 1.15 | Pursuing the establishment of the risk analysis system and executing PSA level 1 and 2 in the plant | پي گيري استقرار سيستم ريسک آناليز در نيروگاه و اجرايي نمودن PSA سطح 1 و 2 در نيروگاه | Manager of management system and supervision / Deputy for Safety | 2016-03-19 | AI | 1.15
1LF.1-1 | 1 | LF.1-1 | 1.16 | Performing the analysis trend of reliability of safety channels and safety equipment in terms of safety based on a list approved by chief engineer , safety deputy. | انجام ترند آناليز قابليت اطمينان کانالها و تجهيزات ايمني و تجهيزات مهم از لحاظ ايمني بر اساس فهرستي که به تاييد سرمهندس نيروگاه و معاونت ايمني مي رسد. | Manager of management system and supervision | 10/22/2015 Permanently(every quarter) | SAT | 1.16
1LF.1-1 | 1 | LF.1-1 | 1.17 | сравнения показателей блока с наилучшей отраслевой практикой (бенчмаркинг) | ارسال نامه به وانو مرکز مسکو مبني بر درخواست انجام بنچ مارکينگ و بازديد علمي در حوزه هاي مختلف مخصوصا مديريتي از نيروگاه هاي غير روسي در سال 2016 |  |  | SAT | 1.17
1LF.1-1 | 1 | LF.1-1 | 1.18 | Developing procedure and executing the supervision on all of processes which are important in terms of safety | تهيه يا بروز رساني دستورالعمل كنترل ايمني هسته اي | Manager of management system and supervision / Fuel and nuclear safety manager | 2015-11-21 | SAT | 1.18
1LF.1-1 | 1 | LF.1-1 | 1.19 | Preparing order for performing corrective measures in due time and taking necessary measures for more control on corrective measures and necessary solutions for more accountability of managements as for corrective measures. | تهيه ابلاغيه در رابطه با انجام اقدامات اصلاحي در موعد مقرر و اتخاذ تدابير لازم بمنظور کنترل بيشتر بر انجام اقدامات اصلاحي و راه کارهاي لازم بمنظور جوابگويي بيشتر مديريت ها نسبت به اقدامات اصلاحي | Manager of management system and supervision | 2015-08-10 | SAT | 1.19
1LF.1-1 | 1 | LF.1-1 | 1.2 | Preparing software of event investigation and corrective measures bank. | تهيه نرم افزار بانک اقدامات اصلاحي و بررسي حوادث | Manager of management system and supervision / ICT manager | 2016-05-21 | AI | 1.2
1LF.1-1 | 1 | LF.1-1 | 1.21 | Making it possible to record significant events on this software 1.20 | ايجاد امکان درج رويدادهاي مهم | Manager of management system and supervision / ICT manager | 2017-06-20 | SAT | 1.21
1LF.1-1 | 1 | LF.1-1 | 1.22 | Preparing and executing the procedure of trending the analysis of defects on all the equipment and corrective measures for improvement. | تهيه و اجرايي نمودن دستورالعمل انجام ترند آناليز ديفکت ها و عيوب بر روي کليه تجهيزات و اقدامات اصلاحي به منظور بهبود | Manager of management system and supervision / M&R planning manager | 2016-03-20 | SAT | 1.22
1LF.1-1 | 1 | LF.1-1 | 1.23 | Improvement in the managers monitoring system ( in three managerial levels) from working locations (equipment and staff) and also continuous monitoring how to remove the comments obtained from the visits ( including the development of checklist , qualitative analysis of the managers and evaluation of the precision and speed in executing the corrective measures). | بهبود در سیستم پایش مدیران (در سه سطح مدیریتی )از محل های کاری(تجهیزات وکارکنان) و همچنین پایش مستمر نحوه بر طرف شدن نتایج گزارشات بازدیها (شامل تدوین چک لیست ،آنالیز کیفی عملکرد مدیران و ارزیابی سرعت و دقت در برطرف نمودن اقدامات اصلاحی ) | Manager of management system and supervision / Head of Operating experiences group | 2016-03-20 | SAT | 1.23
1LF.1-1 | 1 | LF.1-1 | 1.24 | Developing and preparing the comprehensive program for decreasing the human error in NPPs ( methods of training and using the consultants). | تهیه وتدوین برنامه جامع کاهش خطای انسانی در نیروگاه (متدها و روشهای آموزش و استفاده از مشاورین) | Manager of management system and supervision / Head of Human resources and Training center | 2016-02-20 | SAT | 1.24
1LF.1-1 | 1 | LF.1-1 | 1.25 | Improvement in the maintenance and repairs system ( including developing the strategies and maintenance and repairs policy related to all the equipment and systems, record sustem related to monitoring the scheduled activities of the maintenance and repairs, improbement and simplification of the methods for the repairing the equipment, supervision and control on the performance of the contractors). | بهبود در سیستم نگهداری وتعمیرات (شامل : تدوین راهبردها و خط مشی نت مرتبط با کلیه تجهیزات و سیستمها, سیستم سوابق مرتبط با پایش فعالیتهای برنامه ریزی شده نت، بهبود و ساده سازی روشهای تعمیرات تجهیزات،نظارت و کنترل عمکرد پیمانکاران ) | Manager of management system and supervision / Deputy for M&R | 2016-03-20 | SAT | 1.25
1LF.1-1 | 1 | LF.1-1 | 1.26 | Developing the exectuitve program of modernization for those equipment which udergo defect continuously in BNPP operation | تهیه برنامه اجرایی مدرنیزاسیون برای آن دسته از تجهیزاتی که بصورت مستمر دچار دفکت و نقص در کار نیروگاه می گردد | Manager of management system and supervision / Deputy for engineering and technical support | 2016-03-20 | SAT | 1.26
1LF.1-1 | 1 | LF.1-1 | 1.27 | Improvement in the program of controlling the documents (revising and editing the working document). | بهبود در فرآیند کنترل مدارک (بازنگری و ویرایش مدرک کاری) | Manager of management system and supervision / Deputy for engineering and technical support | 2016-01-20 | SAT | 1.27
1LF.1-1 | 1 | LF.1-1 | 1 | Participation especially NPP managerial positions on bench marking and scientific visit in this area to other plants regarding 2016-17 interaction plan with WANO-MC. | نشست فني با وانو در حوزه بهبودهاي مشخص شده و سازماندهي تهيه و اجراي اقدامات اصلاحي در حوزه مربوطه (متدهاي تصميم گيري، تصميم گيري محتاطانه) | Manager of management system and supervision / NPP Management | According to the program of interaction with WANO-MC for 2016-17 | SAT | 1
1LF.1-1 | 1 | LF.1-1 | 1.29 | Holding Tchnical Support Missions about AFIs and organizing for formulating the corrective measures in relevant areas: methods for decision making, conservative decision-making). | برگزاري نشست فني با وانو در حوزه بهبودهاي مشخص شده و سازماندهي تهيه و اجراي اقدامات اصلاحي در حوزه مربوطه (متدهاي تصميم گيري، تصميم گيري محتاطانه) | Manager of management system and supervision / NPP Management | According to the program of interaction with WANO-MC for 2016-17 | SAT | 1.29
|  |  | R.2 | AFI ОР.2-1 corrective measures - Corrective measures in the field of Operation area | اقدامات اصلاحی AFI ОP.2-1 | Responsible entity Deputy for production | Deadline |  | R.2
2ОР.2-1 | 2 | ОР.2-1 | 2.1 | Performing technical training of all of the operator s in the field of operators communication, controlling the working parameters of equipment, switching , controlling each other’s work during switchings. | انجام آموزش فني پرسنل اپراتور (کليه کارکنان اپراتوري) در زمينه نحوه انجام ارتباطات و مكالمات اپراتوري ، كنترل پارامترهاي كاري تجهيزات ، انجام كليد زني و نحوه كنترل انجام كار يكديگر در كليدزنيها. | Head of Human Resources and Training Center | 2016-09-20 | AI | 2.1
2ОР.2-1 | 2 | ОР.2-1 | 2.2 | Making changes in the job description of NPP shift supervisor , unit shift supervisor and shift supervisors of the managements in the issue of realizing a unitary management during technical working on the equipment including switchings in NPP MCR | اعمال تغييرا ت در شرح وظايف رئيس شيفت نيروگاه، رئيس شيفت واحد و روساي شيفت مديريتها در موضوع تحقق مديريت واحد در زمان انجام عمليات فني روي تجهيزات از جمله كليدزنيها در اتاق كنترل اصلي نيروگاه | Deputy for production, Turbine manager, Reactor manager, electricity manager, I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-03-19 | AI | 2.2
2ОР.2-1 | 2 | ОР.2-1 | 2.3 | Providing technical briefing of operators of Reactor managerment and ventilation for using switching cards , checklists and operation procedures, receiving permit , reporting and control request by a superior official ( operation, technical –administrative management). (OP-06-OD-06) | انجام توجيه فني پرسنل اپراتور مديريت راكتور و تهويه براي استفاده از كارتهاي كليد زني، چك ليستها و دستورالعملهاي بهره برداري، دريافت مجوز، گزارش دهي و درخواست كنترل از طرف مقام بالاتر ( مديريت اداري-فني يا اپراتوري) | Reactor manager, chiller and ventilation manager | 2016-03-19 | SAT | 2.3
2ОР.2-1 | 2 | ОР.2-1 | 2.4 | Technical training of emergency diesel operators (operation of diesel and related procedures). OP-06-OD-06 | اموزش فني اپراتورهاي ديزلهاي اضطراري ( نحوه بهره برداري از ديزل و دستورالعملهاي مرتبط) | Reactor manager / Head of Human resources and Training center | 2016-06-19 | SAT | 2.4
2ОР.2-1 | 2 | ОР.2-1 | 2.5 | Determining the working modes of ventilators UV61(62,63,64)D(002A, 002В,001А, 0015), UF61(62,63,64)S(002, 013, 007) (when putting them in a manual mode) and other ventilation equipment of buildings ZK1,2,3 and their valve ware. Developing technical order and making necessary changes in operating procedures. OP-06-OD-06 | تعيين رژيم كاري ونتيلاتورهاي UV61(62,63,64)D(002A, 002В,001А, 0015), UF61(62,63,64)S(002, 013, 007) ( زمان قرار دادن آنها در وضعيت دستي) وديگر تجهيزات تهويه ساختمانهاي ZK1,2,3 و شير الات انها, تهيه دستور فني و انجام تغييرات لازم در دستورالعملهاي بهره برداري | Ventilation manager | 2016-03-19 | SAT | 2.5
2ОР.2-1 | 2 | ОР.2-1 | 2.6 | Durung exercise and training in simulator, it should be analyzed how to do operator communication , control of working parameters of equipment and control of each other’s work by instructors and they should be included in the report and evaluation of exerices and results. (OP-06-OD-06) | در زمان انجام تمرين و آموزش در سيمولاتور, نحوه انجام مكالمات اپراتوري، كنترل پارامترهاي كاري تجهيزات و كنترل كار يكديگر, توسط مربيان آناليز و در گزارش و ارزيابي تمرينها و نتايج آنها آورده شود | Head of Human resources and Training center / simulator manager | 2016-03-10 | SAT | 2.6
2ОР.2-1 | 2 | ОР.2-1 | 2.7 | Checklist of controlling condition of equipment of channels of safety system of emergency diesels buildings for using during visits and during periodical tests and after repairs. OP-06-OD-06 | چك ليست كنترل وضعيت تجهيزات كانالهاي سيستم ايمني ساختمان ديزلهاي اضطراري براي استفاده درزمان بازديد و در زمان تست هاي دوره اي و بعد از تعميرات تهيه شود. | Reactor manager | 2016-03-19 | SAT | 2.7
2ОР.2-1 | 2 | ОР.2-1 | 2.8 | In themes of periodical briefings of reactor operators, it should be added how to work under supervisor. OP-04-VG-02 | در تمهاي توجيهات دوره اي پرسنل اپراتور راكتور نحوه انجام كار تحت نظارت فرد كنترل كننده اضافه شود | Reactor manager | 2016-03-19 | SAT | 2.8
2ОР.2-1 | 2 | ОР.2-1 | 2.9 | In the periodical briefing themes of Unit shift supervisor and NPP shift supervisor, it should be included how to work under supervisor. | در تمهاي توجيهات دوره اي رئيس شيفت واحد و رئيس شيفت نيروگاه نحوه انجام كار تحت نظارت فرد كنترل كننده اضافه شود | Deputy for production | 2016-02-19 | SAT | 2.9
2ОР.2-1 | 2 | ОР.2-1 | 2.1 | In the monthly and periodical briefing themes of operators, it should be included how to do switching and operator’s communication. OP-04-VG-02 | در تمهاي توجهيات دوره اي و ماهانه كليه پرسنل اپراتور موضوع نحوه انجام كليد زنيها و مكالمات اپراتوري وارد شود | Turbine manager, Reactor manager, Deputy for production, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-03-19 | AI | 2.1
2ОР.2-1 | 2 | ОР.2-1 | 2.11 | Providing technical training of operators of production division, Reactor managerment, Turbine , electrical power, I&C , common systems, radiation safety and waste treatment workshop in the field of working with schedule , switchings and manner of work supervision. OP-04-VG-02 | انجام آموزش فني پرسنل اپراتور معاونت توليد ، مديريت راكتور ، توربين ، برق ، كنترل و ابزاردقيق ، سيستمهاي مشترك ، ايمني پرتوي و كارگاه پسمانداري در زمينه كار با برنامه هاي انجام كار ، كليد زنيها و نحوه كنترل انجام كار | Head of Human resources and Training center | 2016-09-20 | AI | 2.11
2ОР.2-1 | 2 | ОР.2-1 | 2.12 | In the periodical briefing program of shift supervisors of plant and Unit , it should be included how to submit order for performing step-by-step operation during technological operation in accordance with working program. OP-04-VG-01 | در برنامه توجيه دوره اي روساي شيفت نيروگاه و واحد نحوه ارئه دستور انجام عمليات گام به گام در زمان عمليات تكنولوژيكي طبق برنامه هاي كاري وارد شود | Turbine manager, Reactor manager, production manager, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager | 2016-03-19 | AI | 2.12
2ОР.2-1 | 2 | ОР.2-1 | 2.13 | Reviewing the existence of necessary requirements in technical ocuments which were producedin the field of presence of technical-administrative staff of managements during important switchnings and if necessary, making changes in documents. OP-04-VG-01 | بررسي وجود الزامات لازم در مدارك فني توليدي در زمينه حضور پرسنل فني- اداري مديريتها در زمان انجام كليد زنيهاي مهم و در صورت لزوم اعمال تغييرات در مدارك | Deputy for production | 2016-02-19 | FAR | 2.13
2ОР.2-1 | 2 | ОР.2-1 | 2.14 | Developing the list of managements present in different switching. OP-04-VG-01 | تهيه فهرست مشاغل مديريتها كه در كليدزنيهاي مختلف بايد حاضر باشند | Deputy for production | 2016-03-19 | AI | 2.14
2ОР.2-1 | 2 | ОР.2-1 | 2.15 | In the periodical briefing program of operators of emergency diesels , it should be included how to do switching under supervision of a controller or by obtaining the permit of above-mentioed operator. OP-04-OD-07 | در برنامه توجيه دوره اي پرسنل اپراتور ديزلهاي اضطراري موضوع نحوه انجام كليد زني تحت نظارت فرد كنترل كننده يا با دريافت مجوز اپراتور مافوق گنجانده شود. | Reactor manager | 2016-03-10 | SAT | 2.15
2ОР.2-1 | 2 | ОР.2-1 | 2.16 | In the list of monthly briefing program of all the operators , it should be included how to do switching and how the communication of operators is done. OP-04-OD-07 | در فهرست برنامه توجيه ماهانه كليه پرسنل اپراتور نحوه انجام كليد زنيها و ارتباطات اپراتوري گنجانده شود | Deputy for production, Turbine manager, Reactor manager, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-03-09 | AI | 2.16
2ОР.2-1 | 2 | ОР.2-1 | 2.17 | Technical training for all of the operators bout switching and operator’s communication should be held. OP-01-OD-02 | آموزش فني براي كليه پرسنل اپراتور باموضوع نحوه انجام كليد زنيها و ارتباطات اپراتوري برگزارشود OP-01-OD-02 | Head of Human resources and Training center | 2016-03-10 | AI | 2.17
2ОР.2-1 | 2 | ОР.2-1 | 2.18 | Revising the list of necessary switching cards of all of managements ( an operation for which more than 3 switchnings should be done ). OP-01-OD-04 | بازنگري فهرست كارتهاي كليد زني لازم كليه مديريتها ( عملياتي كه بيش از 3 كليدزني براي انجام آن نياز مي باشد) OP-01-OD-04 | Deputy for production, Turbine manager, Reactor manager, electricity manager , chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-06-19 |  | 2.18
2ОР.2-1 | 2 | ОР.2-1 | 2.19 | Giving technical briefing to executor of when technical service is done and also observing the requirements of switching cards and working programs. OP-01-OD-04 | انجام توجيه فني براي مجري انجام كار در زمان انجام سرويسهاي فني با موضوع رعايت الزامات كارتهاي كليد زني و برنامه هاي انجام كار OP-01-OD-04 | Deputy for M&R | 2016-03-10 | SAT | 2.19
2ОР.2-1 | 2 | ОР.2-1 | 2.2 | Correcting the reulation of performing technical services of equipment about all of the articles of regulations of technical service and its checklist should be done step by step and also any step should be specified after being done. OP-04-OD-05 | تصحيح آيين نامه انجام سرويسهاي فني تجهيزات با اين موضوع كه كليه بندهاي رگلامنت سرويس فني و چك ليست آن بايد به صورت گام به گام انجام شود با مشخص كردن اجراي هر گام پس از انجام آن. OP-04-OD-05 | Deputy for M&R | 2016-03-10 | SAT | 2.2
2ОР.2-1 | 2 | ОР.2-1 | 2.21 | Analyzing the working program of effiency test of permanent power feeding supply of emergency channels 1 to 4 of safety systems and in case of non-complinace with requirements of procedure 69.BU.1 0.0.FB.PRO.BNPP1338 , developing again the program. OP-04-OD-05 | اجراي آناليز برنامه تست كارآيي منبع تغذيه برق دائمي ديزل هاي اضطراري كانال 1-4 سيستمهاي ايمني و در صورت مغايرت با الزامات دستورالعمل 69.BU.1 0.0.FB.PRO.BNPP1338 تهيه مجدد برنامه OP-04-OD-05 | I&C manager | 2016-02-09 | SAI | 2.21
2ОР.2-1 | 2 | ОР.2-1 | 2.22 | Performing unplanned briefings of all staff of I&C management about not using the unapproved and invalid programs during works. OP-03-OD-04 | اجراي توجيه خارج از برنامه كليه پرسنل مديريت كنترل و ابزار دقيق با موضوع عدم استفاده از برنامه هاي تاييد نشده و نامعتبر در انجام كارها OP-03-OD-04 | I&C manager | 2016-02-09 | SAT | 2.22
2ОР.2-1 | 2 | ОР.2-1 | 2.23 | Submitting letter to the designer AEP and posing the problem of lack of flow rate sensors in the outlet of pumps of middle cooling water system TF of safety channels 2 and 3 | ارسال نامه به طراح AEP و طرح مشكل عدم وجود سنسورهاي دبي در خروجي پمپهاي سيستم آب خنك كننده مياني TF كانالهاي 2و3 ايمني | Reactor managerment | 2016-03-10 | AI | 2.23
2ОР.2-1 | 2 | ОР.2-1 | 2.24 | Preparing the method of calculating the total flow rate of systems TF in order to submit it in СВБУ. OP-03-OD-04 | تهيه روش محاسبه دبي كلي سيستم TF جهت ارائه آن در СВБУ | I&C manager | 2016-03-10 | SAT | 2.24
2ОР.2-1 | 2 | ОР.2-1 |  |  |  | Reactor manager |  | SAT
2ОР.2-1 | 2 | ОР.2-1 | 2.25 | Making changes in operation procedure of system TF in issue: method of controlling flow rate in TF system , mentioning permissible flow rate in system and explanations about necessary measures when permissible values are deviated. OP-01-VG-06 | اعمال تغييرات در دستور العمل بهره برداري سيستم TF در موضوع زير : -روش كنترل دبي در سيستم TF , ذكر مقادير مجاز دبي در سيستم و توضيح اقدامات لازم در زمان انحراف از مقادير مجاز | Reactor manager | 2016-03-10 | SAT | 2.25
2ОР.2-1 | 2 | ОР.2-1 | 2.26 | Briefing (issuing technical order) of the reactor shift supervisor, Turbine control engineer, Turbine supervisor , uint shift supervisor, and NPP shift supervisor about necessity of performing operator communications in Russian language in MCR. OP-01-VG-03 | انجام توجيه (صدور دستور فني) رئيس شيفت راكتور، مهندس كنترل راكتور، رئيس شيفت توربين، مهندس كنترل توربين، رئيس شيفت واحد و رئيس شيفت نيروگاه در مورد لزوم انجام مكالمات اپراتوري به زبان روسي در اتاق كنترل | Deputy for production / Reactor manager / Turbine manager | 2016-03-10 | SAT | 2.26
2ОР.2-1 | 2 | ОР.2-1 | 2.27 | Performing technical training of operator СЭ-production division, РО-Reactor managerment, ТО-Turbine management, ОВиК-chiller and ventilation management, АСУ-ТП-I&C management, ЭТО-electricity management, ООО-common systems management, ХС-chemistry manager, РБ-radiation safety management and СДРАО-waste treatment management about how to do operator communications and switchings and incuding this issue in the list of monthly briefings of these staff. OP-01-VG-05 | اجراي آموزش فني پرسنل اپراتور СЭ.РО.ТО.ОВиК.АСУ-ТП.ЭТО.ООО. ХС.РБ.СДРАО در مورد نحوه انجام ارتباطات اپراتوري و كليد زنيها و گنجاندن اين موضوع در فهرست توجيهات ماهانه اين پرسنل | Deputy for production, Turbine manager, Reactor manager, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-05-09 | SAT | 2.27
2ОР.2-1 | 2 | ОР.2-1 | 2.28 | Briefing the operators of Reactor managerment (reactor shift supervisor and control engineer) during performing works simultaneously. OP-01-VG-05 | اجراي توجيه پرسنل اپراتور مديريت راكتور( رئيس شيفت ومهندس كنترل راكتور ) در مورد انجام همزمان كارها | Reactor manager | 2016-05-09 | SAT | 2.28
2ОР.2-1 | 2 | ОР.2-1 | 2.29 | Including the issue of how to switch during performing simultaneous works in the list of issues of monthly briefing and technical training of operators СЭ, РО, ТО, ОВиК, АСУ-ТП, ЭТО, ООО, ХС, РБ and СДРАО. OP-01-VG-05 | وارد كردن موضوع نحوه انجام كليدزني در زمان انجام كارهاي همزمان در فهرست موضوعات توجيهات ماهانه و اموزش فني پرسنل اپراتورСЭ.РО.ТО.ОВиК.АСУ-ТП.ЭТО.ООО. ХС.РБ.СДРАО | Turbine manager, Reactor manager, Deputy for production, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager, | 2016-05-09 | SAT | 2.29
2ОР.2-1 | 2 | ОР.2-1 |  |  |  | Head of Human resources and Training center
|  |  | R. | AFI OF.1-1 corrective measures - Corrective measures in the field of Operation area | اقدامات اصلاحی AFI ОF.1-1 | Responsible entity Deputy for production | Deadline |  | R.
2OF.1-1 | 2 | OF.1-1 | 2.33 | Preparing notebook and order for reviewing all videocadres of working locations, РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО,ОРБ, ОЭО, in main control room and recording all of the defects and non-compliances. | تهيه دفتر ثبت و ابلاغيه اي جهت بررسي تمام ويديوكادرهاي محل هاي كاري РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО,ОРБ ، ОЭОدر اتاق كنترل و ثبت تمام ايرادات و عدم تطابقها | I&C manager | 2016-02-08 | SAT | 2.33
2OF.1-1 | 2 | OF.1-1 | 2.34 | Reviewing all the videocadres of working locations РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО ,ОРБ, ОЭО in MCR and recording all the defects and non-complinaces including conditions of mechanisms, valves, violet color of parameters, lack of emergency and warning setpoints, inaccuracy of parameters shown, lack of compliance of warning signal and emergency signal with real value of parameter will be done in a separate notebook which will be prepared by I&C management. | بررسي تمام ويديوكادرهاي محل هاي كاري РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО,ОРБ , ОЭО,در اتاق كنترل و ثبت تمام ايرادات و عدم تطابقها شامل: وضعيت مكانيزمها ، شيرها ، رنگ بنفش پارامترها ، ست پوينتهاي اعلام هشدار و اضطراري ، عدم صحت پارامتر نشان داده شده ،عدم تطابق سيگنال هشداري و سيگنال اضطراري با مقدار واقعي پارامتر در دفتر ثبت جداگانه اي كه مديريت كنترل و ابزار دقيق براي ان تهيه خواهد كرد . | Turbine manager, Reactor manager, electricity manager , I&C manager, chiller and ventilation manager | 2016-05-09 | SAT | 2.34
2OF.1-1 | 2 | OF.1-1 | 2.35 |  | جمع آوري ايرادات از مديريت هاي مربوطه, آناليز ايرادات و تهيه اقدامات اصلاحي در حوزه مديريت کنترل و ابزار دقيق, مواردي که مربوط به مديريت کنترل و ابزار دقيق نمي باشد (موارد اختلافي) به معاونت توليد گزارش شود | I&C manager | 2016-06-09 |  | 2.35
2OF.1-1 | 2 | OF.1-1 | 2.36 | Holding a mutual meeting with I&C and equipment-owning manager in order to take decision about the remaining matters | برگزاري جلسه مشترك با كنترل و ابزار دقيق و مديريت صاحب تجهيز براي تصميم گيري موارد باقي مانده. | Deputy for production | 2016-07-09 | SAT | 2.36
2OF.1-1 | 2 | OF.1-1 | 2.37 | Revising the setpoint of changing the color of hexagon sof fuel assemblies during increase of temperature in their outlet (currently when the temperature of water coming out of assemblies is more than 327 degree, the color of assemblies changes inro red considering the fact that the maximum outlet temperature of fuel assemblies is 335 ˚C when four pumps of primary circuit are operating. | بازنگري ست پوينت تغيير رنگ شش ضلعيهاي كاست هاي سوخت در زمان افزايش دما در خروجي آن ( در حال حاضر در زمان افزايش دماي اب خروجي از كاست ها بيش از 327 درجه رنگ كاست به قرمز تغيير مي كند با توجه به اينكه در نظام نامه بهره برداري حد اكثر دماي خروجي از كاست سوخت در زمان كار 4 پمپ مدار اول 335 درجه است OP-04-VG-04 | I&C manager | 2016-03-10 | SAT | 2.37
2OF.1-1 | 2 | OF.1-1 | 2.38 | Revising the color change of setpoint color change of DNBR into red. Currently DNBR changes into less than 50 to red during reducing it. According to the operation regulation, reserve value of DNBR is at least 1.0 including its measurement error with reliability rate of 95% with the error of measurement parameters. | بازنگري تغييررنگ ست پوينت تغيير رنگ DNBR به قرمز . در حال حاضر DNBR در زمان كاهش مقدار آن به كمتر از 50 به رنگ قرمز تغيير مي كند مطابق با نظام نامه بهره برداري مقدار زاپاس DNBR با احتساب خطاي اندازه گيري ان با احتمال اطمينان 95% با خطاي پارامترهاي اندازه گيري، حداقل 1.0 مي باشد OP-04-VG-04 | I&C manager | 2016-03-10 | SAT | 2.38
2OF.1-1 | 2 | OF.1-1 | 2.39 | reviewing whether it is possible to provide signal in videocadres СВРК during increase of parameters Nакз, QL, Кq, КL from permissible values by specifying the increase rate of every parameters for which relevant signal will be provided. OP-04-VG-04 | بررسي امكان برقراري سيگنال در ويديوكادرهاي СВРКدر زمان افزايش پارامترهاي Nакз, QL, Кq, КL از مقادير مجاز با مشخص كردن مقدار افزايش ( اختلاف) به صورت درصد يا واحد اندازه گيري هر پارامتر كه براي آن سيگنال مربوطه برقرار خواهد شد OP-04-VG-04 | I&C manager | 2016-03-10 | SAT | 2.39
2OF.1-1 | 2 | OF.1-1 | 2.4 | It should be included in the program of briefing the personnel to monitor parameters ( in fragments of working locations) , record the defects and moving them. OP-03-VG-01 | در برنامه توجيه پرسنل موضوع كنترل پارامترها ( در فراگمنتهاي محل هاي كاري) ثبت ايرادات و رفع انها گنجانده شود OP-03-VG-01 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , | 2016-04-08 | SAT | 2.4
2OF.1-1 | 2 | OF.1-1 | 2.41 | Reviewing all of the videocadres of working locations РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО in MCR and recording all the defects and non-compliances including the condition of mechanisms, valves , violet color of parameters, setpoints of announcing warning and emergency, inaccuracy of parameters, non-compliance of warning signal and emergency signal with actual value of parameters in a separate logbook which will be prepared by I&C management for it. | بررسي تمام ويديوكادرهاي محل هاي كاري РО, ТО, АСУТП, СВРК, АКНП, ОВИК, СВО در اتاق كنترل و ثبت تمام ايرادات و عدم تطابقها شامل: وضعيت مكانيزمها ، شيرها ، رنگ بنفش پارامترها ، ست پوينتهاي اعلام هشدار و اضطراري ، عدم صحت پارامتر نشان داده شده ،عدم تطابق سيگنال هشداري و سيگنال اضطراري با مقدار واقعي پارامتر در دفتر ثبت جداگانه اي كه مديريت كنترل و ابزار دقيق براي ان تهيه خواهد كرد . OP-03-VG-01 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-09 | SAT | 2.41
2OF.1-1 | 2 | OF.1-1 | 2.42 | Holding a mutual meeting with I&C after gathering and analysis in order to divide the defects. OP-03-VG-01 | پس از جمع اوري و آناليز برگزاري جلسه مشترك با كنترل و ابزار دقيق براي تقسيم بندي ايرادات OP-03-VG-01 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT | 2.42
2OF.1-1 | 2 | OF.1-1 | 2.43 | Providing technical training and completing the issues of briefing the personnel about the performance of personnel when they receive signals and recording them and measures taken in operator logbook. OP-01-VG-08 | به موضوعات توجيهات پرسنل ،موضوع عملكرد پرسنل در زمان دريافت سيگنال و ثبت آنها و اقدامات انجام شده اضافه گردد و پس از توجيه در دفتر اپراتوري ثبت گردد | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-04-18 | SAT | 2.43
2OF.1-1 | 2 | OF.1-1 | 2.44 | Considering the procedure of staff reaction when they receive signal and checking the card for measures of personnel for all of the sign boards of MCR . OP-01-VG-08 | بررسي دستورالعمل واكنش كاركنان در زمان دريافت سيگنال و كنترل وجود كارت اقدامات پرسنل براي تمام تابلوهاي سيگنال اتاق كنترل OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-03-10 | SAT | 2.44
2OF.1-1 | 2 | OF.1-1 | 2.45 | Preparing logbook of signal boards which are constantly “on” and preparing technical order for addressing these signals in shift in order to remove the cause for the related boards which are “on” .OP-01-VG-08 | تهيه دفتر ثبت تابلوهاي سيگنال كه دائما روشن بوده و تهيه دستور فني جهت ارئه اين سيگنالها در شيفت براي رفع علت روشن بودن تابلوهاي مربوطه OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT | 2.45
2OF.1-1 | 2 | OF.1-1 | 2.46 | Preparing technical order for making it obligatory to record the signals which are “on” during shift change in the operator logbook. OP-01-VG-08 | تهيه دستور فني براي الزام ثبت سيگنالهاي روشن در زمان تعويض شيفت در دفاتر اپراتوري OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT | 2.46
2OF.1-1 | 2 | OF.1-1 | 2.47 | Revising the shift acceptance and deliverychecklist of operating logbook in the field of adding item of signal boards which are “on” | بازنگري چك ليست پذيرش و تحويل شيفت دفاتر اپراتوري در زمينه اضافه كردن آيتم تابلوهاي سيگنال روشن OP-01-VG-08 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-04-18 | SAT | 2.47
2OF.1-1 | 2 | OF.1-1 | 2.48 | The issue of checking the parameters ( in fragments of working locations) , and recording the defects and removing them should be included in the program of briefing the staff. | در برنامه توجيه پرسنل موضوع كنترل پارامترها ( در فراگمنتهاي محل هاي كاري) ثبت ايرادات و رفع انها گنجانده شود OP-03-VG-03 | Deputy for production, Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-02-09 | SAT | 2.48
2OF.1-1 | 2 | OF.1-1 | 2.49 |  | 2.41 برای OP-03-VG-03 |  |  |  | 2.49
2OF.1-1 | 2 | OF.1-1 | 2.5 |  | 2.42 برای OP-03-VG-03 |  |  |  | 2.5
2OF.1-1 | 2 | OF.1-1 | 2.51 | Considering whether it is possible or not to separate the tonality of warning sound signals from emergency ones and realizing it. OP-04-VG-03 | بررسي امكان جدا سازي تناليته سيگنالهاي صوتي هشداري با اضطراري و اجراي آن OP-04-VG-03 | I&C manager | 2016-03-10 | AI | 2.51
2OF.1-1 | 2 | OF.1-1 | 2.52 | Considering wheher it is possible to stabilize the blinking state of optical diods of pumps and valves in mimicking the MCR panel which comes into being when their power feeding circuit is in a separate condition . OP-03-OD-03 | بررسي امكان ثابت كردن حالت چشمك زن ديودهاي نوري پمپها و شيرها در مميك پنل اتاق كنترل كه در وضعيت جدا بودن مدار تغذيه برق آنها بوجود مي آيد OP-03-OD-03 | I&C manager | 2016-03-10 | AI | 2.52
2OF.1-1 | 2 | OF.1-1 | 2.53 | Considering whether it is possible to install placard ( with a text) on the button of valves and pumps in mimic panel . OP-03-OD-03 | بررسي امكان نصب پلاكارد ( داراي متن مورد نظر ) روي دكمه شيرها و پمپها در مميك پنل OP-03-OD-03 | I&C manager | 2016-05-19 |  | 2.53
2OF.1-1 | 2 | OF.1-1 | 2.54 | Checking all the boards and panels of MCR in terms of having Russian translation for all of the titles of signals (in case of existence of only English text, Russian translation should also be near the English text). OP-03-OD-05 | بررسي تمام تابلوها و پنلهاي اتاق كنترل از نظر وجود ترجمه روسي عناوين سيگنال ( در صورتيكه فقط متن انگليسي وجود دارد ترجمه آن به روسي و نصب در كنار متن انگليسي ) OP-03-OD-05 | I&C manager | 2016-03-10 | SAT | 2.54
2OF.1-1 | 2 | OF.1-1 | 2.55 | Providing technical training and completing the issues of briefing personnel anbout what personnel should do during receiving signal and recording the signals and measures taken in operaroe logbook. OP-01-VG -10،OP-04-OD-01،OP-01-VG-09 | انجام آموزش فني و تكميل موضوعات توجيهات پرسنل با موضوع عملكرد پرسنل در زمان دريافت سيگنال و ثبت آنها و اقدامات انجام شده در دفتر اپراتوري، | Reactor manager / Electricity manager / Turbine manager / Head of Human resources and Training center | 2016-03-10 | SAT | 2.55
2OF.1-1 | 2 | OF.1-1 | 2.56 | Reviewing the procedure of the staff reaction during receiving signal and checking the existence of card for measures taken by staff for all of the signal boards of MCR . OP-01-VG-10 ،OP-04-OD-01،OP-01-VG-09 | بررسي دستورالعمل واكنش كاركنان در زمان دريافت سيگنال و كنترل وجود كارت اقدامات پرسنل براي تمام تابلوهاي سيگنال اتاق كنترل، OP-01-VG-10 ،OP-04-OD-01،OP-01-VG-09 | Reactor manager / Electricity manager / Turbine manager | 2016-03-10 | AI | 2.56
2OF.1-1 | 2 | OF.1-1 | 2.57 | Preparing a logbook for signal boards which are constantly “on” and preparing technical order for addressing these signals in shift in order to remove the cause for related boards which are “on” . OP-01-VG-10،OP-04-OD-01، OP-01-VG-09 | تهيه دفتر ثبت تابلو هاي سيگنال كه دائما روشن بوده و تهيه دستور فني جهت ارئه اين سيگنالها در شيفت براي رفع علت روشن بودن تابلوهاي مربوطه OP-01-VG-10،OP-04-OD-01،OP-01-VG-09 | Deputy for production | 2016-05-19 | SAT | 2.57
2OF.1-1 | 2 | OF.1-1 | 2.58 | Revising checklist of shift supervisor and delivery of operator logbook in the field of adding item of signal boards which are on,. OP-01-VG-10،OP-04-OD-01،OP-01-VG-09 | بازنگري چك ليست پذيرش و تحويل شيفت دفاتر اپراتوري در زمينه اضافه كردن ايتم تابلوهاي سيگنال روشن OP-01-VG-10،OP-04-OD-01،OP-01-VG-09 | Deputy for production / Reactor manager / Electricity manager / Turbine manager | 2016-05-19 | SAT | 2.58
2OF.1-1 | 2 | OF.1-1 | 2.59 | Checking the manner of interaction among managements in order to remove the defects of equipment which are monitored from local panels. If the interactions are not cleartechnical order is developed to remove the defects of local panels , defects of equipment and necessary measures during receiving signal. OP-06-OD-07 | بررسي نحوه ارتباطات متقابل بين مديريتها جهت رفع ايرادات تجهيزاتي كه از پانلهاي كنترل محلي كنترل مي شوند .در صورت مشخص نبودن ارتباطات متقابل تهيه دستور فني با تعيين موارد لازم جهت رفع به موقع ايرادات در پانلهاي كنترل محلي ، ايرادات تجهيزات و اقدامات لازم در زمان دريافت سيگنال OP-06-OD-07 | Reactor manager / Electricity manager / I&C manager / Deputy for engineering and technical support | 2016-03-10 | SAT | 2.59
2OF.1-1 | 2 | OF.1-1 | 2.6 | Determimning the interactions among all managements which have equipment which are monitored by local panels. OP-06-OD-07 | تعيين ارتباطات متقابل بين تمام مديريتهايي كه داراي تجهيزات مورد كنترل از پانلهاي محلي هستندOP-06-OD-07 | Deputy for engineering and technical support | 2016-03-10 | SAT | 2.6
2OF.1-1 | 2 | OF.1-1 | 2.61 | Providing the technical training for staff of reactor , electricity and I&C managements about how to remove defects in safety channels of emergency power supply. OP-06-OD-07 | انجام آموزش فني براي پرسنل مديريت راكتور ، برق و كنترل و ابزار دقيق با موضوع نحوه رفع ايرادات در كانالهاي ايمني تامين برق اضطراري OP-06-OD-07 | Head of Human resources and Training center | 2016-03-20 | SAT | 2.61
2OF.1-1 | 2 | OF.1-1 | 2.62 | Preparing the procedure of measures of staff for the received signals in local panels of safety channels of emergency power. OP-06-OD-07 | تهيه دستور العمل اقدامات پرسنل براي سيگنالهاي دريافتي در پانلهاي محلي كانالهاي ايمني تامين برق اضطراري OP-06-OD-07 | Reactor manager, electricity manager , I&C manager, manager of process engineering | 2016-09-20 | SAT | 2.62
2OF.1-1 | 2 | OF.1-1 | 2.63 | Preparing the reaction card of staff for the received signals in local panels of safety channels of emergency power supply. OP-06-OD-07 | تهيه كارت واكنش پرسنل براي سيگنالهاي دريافتي در پانلهاي محلي كانالهاي ايمني تامين برق اضطراري OP-06-OD-07 | Reactor manager, electricity manager , I&C manager, manager of process engineering | 2016-10-21 | SAT | 2.63
2OF.1-1 | 2 | OF.1-1 | 2.64 | Preparing the defect logbook during scheduled repairs in different managements . | تهيه دفتر ثبت ايرادات جهت رفع در زمان تعميرات برنامه ريزي شده در مديريتها OP-01-OD-06 | Equipment-owning managers | 2015-11-11 | SAT | 2.64
2OF.1-1 | 2 | OF.1-1 | 2.65 | .Revising the defect logbook in working lications in order to identify defects which cannot be identified for different reasons and should be transferred to defect logbook in order to remove them during scheduled repairs. | بازنگري دفتر ثبت ايرادات در محلهاي كاري جهت مشخص كردن ايراداتي كه به دلايل مختلف قابل رفع نبوده و بايد به دفتر ثبت ايرادات جهت رفع در زمان تعميرات برنامه ريزي شده منتقل شوند OP-01-OD-06. | Equipment-owning managers | 2016-03-10 | SAT | 2.65
2OF.1-1 | 2 | OF.1-1 | 2.66 | Preparing the visit logbook with equal format in accordance with the requirements of management of planning and technical documents in all the equipment-owning with the following contents: ordinal No. of visit, date, time, shift, dfects observed, name and surname and signature, visitor and and initials of related manager. OP-02-OD-04 | تهيه دفتر ثبت بازديد با فرمت يكسان مطابق با الزامات مديريت برنامه ريزي و مدارك فني در تمام مديريتهاي صاحب تجهيز با محتواي زير : شماره ترتيبي بازديد ، تاريخ ، زمان ، شيفت ، ايرادات مشاهده شده ، نام و نام خانوادگي و امضاء فرد بازديد كننده و پاراف مديريت مربوطه OP-02-OD-04 | Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT | 2.66
2OF.1-1 | 2 | OF.1-1 | 2.67 | Providing the manual of completing visit logbook . OP-02-OD-04 | تهيه راهنماي نحوه تكميل دفتر بازديد OP-02-OD-04 | Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-05-19 | SAT | 2.67
2OF.1-1 | 2 | OF.1-1 | 2.68 | Making changes in the document 90.BU.10.0.QAPOP.BNPP021 OP-02-OD-04 | انجام تغييرات در مدرك90.BU.10.0.QAPOP.BNPP021 OP-02-OD-04 | manager of Process engineering | 2016-04-18 | SAT | 2.68
2OF.1-1 | 2 | OF.1-1 | 2.69 | Briefing all the operators with the issue of how to complete the visit logbooks and the logbooks for recording defect . | انجام توجيه كليه پرسنل اپراتور با موضوع نحوه تكميل دفاتر بازديد و دفاتر ثبت ايراد OP-02-OD-04 | Reactor manager, electricity manager , I&C manager, Turbine manager, chiller and ventilation manager , chemistry manager | 2016-04-18 | SAT | 2.69
2OF.1-1 | 2 | OF.1-1 | 2.7 | make visit to equipment and locations by operators such as exact visit to equipment of defect analysis , submitting and transferring defects to equipment-owning management and recording the defect in the subjects of periodic briefing of personnel which is repeated every three months. OP-03-OD-10 | نحوه انجام بازديد از تجهيزات و اماكن توسط پرسنل اپراتور از جمله بازديد دقيق از تجهيزات, آناليز ايرادات مشاهده شده، ارائه و انتقال ايردات به مديريت صاحب تجهيز و ثبت ايراد, در موضوعات توجيهات دوره اي پرسنل با تكرار سه ماهه وارد شودOP-03-OD-10 | Turbine manager, Reactor manager, Deputy for production, electricity manager , I&C manager, chiller and ventilation manager, common systems manager, waste treatment manager, chemistry manager, radiation safety manager | 2016-03-10 | SAT | 2.7
2OF.1-1 | 2 | OF.1-1 | 2.71 | In the program of preparing the local operators in training center , the issue of paying visit to equipment and locations should be included. OP-03-OD-10 | در برنامه آماده سازي پرسنل اپراتور محلي در مركز آموزش موضوع نحوه انجام بازديد از تجهيزات و اماكن وارد شود OP-03-OD-10 | Head of Human resources and Training center | 2016-03-10 | SAT | 2.71
2OF.1-1 | 2 | OF.1-1 | 2.72 | Revising the switching cards and preparing them in accordance with the procedure 69.BU.1 0.00.AB.WI.ATEX.002. OP-01-VG-12 | بازنگري كارتهاي كليد زني و تهيه انها مطابق با دستور العمل 69.BU.1 0.00.AB.WI.ATEX.002 OP-01-VG-12 | Reactor manager | 2016-06-19 | SAT | 2.72
2OF.1-1 | 2 | OF.1-1 | 2.73 | Performing unplanned technical briefings by the reactor control engineer and reactor shift supervisor for recording the parameters of safety pumps during test in the logbook of safety-related important systems LGB-1300-1017 . | انجام توجيه خارج از برنامه مهندس كنترل راكتور و رئيس شيفت راكتور براي ثبت پارامترهاي پمپهاي ايمني در زمان تست در دفتر ثبت سيستمهاي مهم براي ايمني LGB-1300-1017 OP-01-VG-12 | Reactor manager, electricity manager , I&C manager, Turbine manager, Chillness and ventilation manager , chemistry manager | 2016-03-10 | SAT | 2.73
2OF.1-1 | 2 | OF.1-1 | 2.74 | Making necessary changes in technical specifications related to controlling the level of oil of diesel generator bearings, making necessary changes in the visit checklist of emergency diesel by the local operator. OP-01-OD-13 | انجام تغييرات لازم در رگلامنت سرويس فني ديزلهاي اضطراري مرتبط با كنترل سطح روغن ياتاقانهاي ژنراتور ديزل، انجام تغييرات لازم در چك ليست بازديد از ديزل اضطراري توسط اپراتور محليOP-01-OD-13 | Reactor manager |  | SAT | 2.74
2OF.1-1 | 2 | OF.1-1 | 2.75 | Investigating the necessity and possibility of controlling working parameters of equipment of all safety systems in locations. OP-03-OD-13 | بررسي لزوم و امكان كنترل پارامترهاي كاري تجهيزات تمام سيستمهاي ايمني در محل OP-03-OD-13 | Reactor managerr, Turbine manager, chiller and ventilation manager , | 2016-03-10 | SAT | 2.75
2OF.1-1 | 2 | OF.1-1 | 2.76 | Investigating the necessity and possibility of controlling working parameters of safety systems pumps in their locations. OP-03-OD-13 | بررسي لزوم و امكان كنترل پارامترهاي كاري پمپهاي سيستمهاي ايمني در محل قرار گيري آنOP-03-OD-13 | Reactor manager | 2016-03-10 | SAT | 2.76
2OF.1-1 | 2 | OF.1-1 | 2.77 | Determining the controller who accompany diesel operator during performing the tests of emergency power channel . | تعيين فرد كنترل كننده همراه اپراتور ديزل در زمان انجام تستهاي كانالهاي برق اضطراريOP-04-OD-08 | Reactor manager | 2015-12-31 | SAT | 2.77
2OF.1-1 | 2 | OF.1-1 | 2.78 | Providing the technical training of reactor operator ( diesel operator ) with the subject of checking the working parameters of diesel in the monitors . OP-04-OD-08 | انجام آموزش فني پرسنل اپراتور راكتور ( اپراتور ديزل ) با موضوع كنترل پارامترهاي كاري ديزل در مونيتورهاي كنترلي OP-04-OD-08 | Reactor manager | 2015-12-31 | SAT | 2.78
2OF.1-1 | 2 | OF.1-1 | 2.79 | Oil level in the volume of technical service of emergency diesel is checked via glass openings. | در حجم سرويسهاي فني ديزلهاي اضطراري كنترل وجود سطح روغن از طريق دريچه هاي شيشه اي اندازه گيري وارد شود. | Reactor manager | 2015-12-31 | SAT | 2.79
2OF.1-1 | 2 | OF.1-1 |  | Marking the glass openings which measure oil in order to monitor the amount of oil in crankcases of bearing. | علامت گذاري دريچه هاي شيشه اي اندازه گيري روغن جهت كنترل ميزان روغن در كارترهاي ياتاقان.
2OF.1-1 | 2 | OF.1-1 |  | Recording the defect of openings which measure the oil of diesel of safety chaneel No. 3 . OP-01-OD-12 | ثبت ايراد دريچه هاي شيشه اي اندازه گيري روغن ديزل كانال سه ايمني OP-01-OD-12
|  |  | R. | AFI OP.1-1 corrective measures - Corrective measures in the field of Operation area | اقدامات اصلاحی AFI ОР.1-1 | Responsible entity Deputy for production | Deadline |  | R.
2OP.1-1 | 2 | OP.1-1 | 2.8 | It is necessary for superior technical administrative staff to be present during important switching and managers should check the basic skills of operators which were mentioned in SOER 2013. | در هنگام كليدزني هاي مهم حضور كاركنان اداري فني مافوق ضروري ميباشد و مديريت ها ميبايست مهارت هاي پايه اپراتورها كه در2013 SOER ذكر شده است را چك نمايند | Equipment-owning managers | Permanently | SAT | 2.8
2OP.1-1 | 2 | OP.1-1 | 2.81 | Preparing the list of important switchings in which the presence of superior technical administrative staff is necessary and submitting it to the senior process engineering management. | تهیه فهرست كليدزني هاي مهم كه حضور كاركنان اداري فني مافوق ضروري ميباشد و ارسال به مديريت مهندسي ارشد فرايند. | Reactor manager, Turbine manager, chemistry manager, ventilation manager, I&C manager | 2016-02-19 | SAT | 2.81
2OP.1-1 | 2 | OP.1-1 | 2.82 | Summing up and preparing the general switchings of BNPP and ordering it by the chief engineer to the sections of NPP. | جمع بندي و تهيه فهرست کلي كليدزني هاي مهم كه حضور كاركنان اداري فني مافوق ضروري ميباشد و ابلاغ از طرف سرمهندس نيروگاه به واحدها | Management of senior engineering of process | 2016-03-19 | SAT | 2.82
2OP.1-1 | 2 | OP.1-1 | 2.83 | Pursuing the preparation and approval of second revision ИЛА РУ,ТО, ЭО.(ИЛА: Instructions for Emergency Response, РУ-Reactor, ТО-Turbine, ЭО-Electricity, Equipments). | پي گيري تهيه و تاييد ويرايش دوم ИЛА РУ,ТО, ЭО | Deputy for engineering and technical support | 2016-09-20 | AI | 2.83
2OP.1-1 | 2 | OP.1-1 | 2.84 | Updating ИЛА РУ,ТО, ЭО in accordance with the structure of documents which is used in Russian NPPs. ( provided in the technical support contract) | به روز آوري ИЛА РУ,ТО, ЭО, مطابق با ساختار مداركي كه در نيروگاههاي روسي مورد استفاده قرار میگیرد(از محل قرارداد پشتيباني فني) | Deputy for engineering and technical support | 2017-03-10 | AI | 2.84
2OP.1-1 | 2 | OP.1-1 | 2.85 | Determining the strategy of how to use the existing documents during accidents and disruptions . | تعيين استراتژي نحوه استفاده از مدارك نيروگاهي موجود در زمان بروز حوادث و اختلالات | Deputy for engineering and technical support | 2017-03-10 | AI | 2.85
2OP.1-1 | 2 | OP.1-1 | 2.86 | Training personnel for how to use documents, providing training for how to exchange information, switching, and operators conversation. | آموزش پرسنل در خصوص استفاده از مدارك | Simulator manager | 2016-03-10 | SAT | 2.86
2OP.1-1 | 2 | OP.1-1 |  |  | انجام آموزش در خصوص نحوه تبادل اطلاعات ، انجام كليدزني و مکالمات اپراتوری |  | permanently | SAT
2OP.1-1 | 2 | OP.1-1 | 2.87 | Developing the controlling procedure of control physics. | تهيه آيين نامه كنترل كننده فيزيك | Fuel and nuclear Safety manager | 2016-01-20 | SAT | 2.87
2OP.1-1 | 2 | OP.1-1 | 2.88 | Providing training for MCR personnel in tems of requirements mentioned in SOER 2013-2 “ cautionary decision making , reactivity management, permanent monitoring og parameters and regimes in MCR and work in the group”. | انجام آموزش به پرسنل اتاق کنترل در خصوص الزامات ذکر شده در SOER 2013 -2 | Head of Human resources and Training center | 2016-03-10 | SAT | 2.88
2OP.1-1 | 2 | OP.1-1 |  |  | " تصمیم گیری به روش محتاطانه، مدیریت راکتیویته ،پایش دایمی پارامترها و رژیمها در اتاق کنترل و کار در گروه" |  | Periodically in qualification maintenance programs | SAT
2OP.1-1 | 2 | OP.1-1 | 2.89 | Pursuing the establishment of SAM and procedures related to beyond-design and design-basis accidents . | پي گيري استقرار مديريت حوادث شديد و دستورالعمل هاي م بوط به حوادث مبناي طرح و فرا طراحي | Deputy for engineering and technical support | 2016-03-10 | AI | 2.89
2OP.1-1 | 2 | OP.1-1 | 2.9 | Preparing procedure for making personnel use the fragment related to the amount of reserve water until the saturation temperature during heating and cooling the circuit and also in the cases which there is leakage in primary circuit. СРО-02-VGWTSV-01-01 | تهيه دستور در خصوص الزام پرسنل به استفاده از فراگمنت مربوط به مقدار زاپاس آب تا دماي اشباع در زمان گرم كردن و سرد كردن مدار و همچنين در مواردي كه نشت مدار اول وجود دارد СРО-02-VGWTSV-01-01 | Reactor manager | 2016-02-20 | SAT | 2.9
2OP.1-1 | 2 | OP.1-1 | 2.91 | Providing training as for leakage from primary circuit to secondary circuit | انجام آموزش در خصوص نشت مدار اول به دوم. СРО-02-VGWTSV-01-02 | Simulator manager | 2016-03-10 | SAT | 2.91
2OP.1-1 | 2 | OP.1-1 | 2.92 | Providing training as for the performance of staff during radiation accidents in emergency drills related to organization of works should be evaluated. СРО-02-VGWTSV-01-03 | انجام آموزش در خصوص عملکرد پرسنل در زمان بروز حوادث پرتوی در مانورهاي شرايط اضطراري موارد مربوط به سازماندهي انجام كار ارزيابي گردد.– СРО-02-VGWTSV-01-03 | Head of Human resources and Training center / simulator manager | 2016-03-10 | SAT | 2.92
2OP.1-1 | 2 | OP.1-1 | 2.93 | Reviewing the possibility of making sound signals for disconnecting the equipment of primary and secondary circuits and electrical equipment. | بررسي امكان ايجاد سيگنال صوتي براي قطع تجهيزات اصلي مدار اول و دوم و تجهيزات برقي СРО-02-VGWTSV-01-04 | I&C manager | 2015-09-22 | SAT | 2.93
2OP.1-1 | 2 | OP.1-1 |  | СРО-02-VGWTSV-01-04 |  |  |  | SAT
2OP.1-1 | 2 | OP.1-1 | 2.94 | Providng the list of equipment of primary and secondary circuits and electrical equipment in order to make sound signals. | ارائه لسيت تجهيزات اصلي مدار اول و دوم و تجهيزات برقي جهت ايجاد سيگنال صوتي | Equipment-owning managers | 2015-10-23 | SAT | 2.94
2OP.1-1 | 2 | OP.1-1 | 2.95 | Providing training about the leakage from primary to secondary circuit ( deenergizingthe heaters КД. СРО-02-VGWTSV-05 | انجام آموزش در خصوص نشت مدار اول به دوم(بی برق کردن گرمکن های КД СРО-02-VGWTSV-05 | Simulator manager | 2016-03-10 | SAT | 2.95
2OP.1-1 | 2 | OP.1-1 | 2.96 | Providing training in the field of sfaff performance after emergency outage. СРО-02-VGWTSV-01-06 | انجام آموزش در حوزه عملكرد كاركنان بعد از توقف اضطراري СРО-02-VGWTSV-01-06 | Simulator manager | 2016-03-10 | SAT | 2.96
2OP.1-1 | 2 | OP.1-1 | 2.97 | Providing changes in the document instructions for emergency response ИЛА РУ и instructions for emergency response ИЛА ЭО as for the performance of staff in case of disconnection of 10-Kv busbars in normal operation. | ايجاد تغيير در مدا ك ИЛА РУ И ИЛА ЭО در ارتباط با عملكرد پرسنل در صورت قطع شينه هاي 10 كيلوولت بهره‌برداري نرمال | Reactor manager / Electricity manager | 2016-01-01 | AI | 2.97
2OP.1-1 | 2 | OP.1-1 | 2.98 | Preparing the scenario and tprviding training after making the changes . CPO-04-VGWTSV-11-06 | تهیه سناریو و انجام آموزش پس از اعمال تغييرات CPO-04-VGWTSV-11-06 | Simulator manager | 2016-03-10 | AI | 2.98
2OP.1-1 | 2 | OP.1-1 | 2.99 | Making changes in the documents instructions for emergency response ИЛА TО related to the performance of staff in case of leakage or breakage of internal consumption collectors of NPP. | ايجاد تغيير در مدا ك ИЛА TО مربوط به عملكرد كاركنان اپراتور در صورت نشت و يا شكستن كلكتور مصرف داخلي نيروگاه | Turbine manager | 2016-01-01 | SAT | 2.99
2OP.1-1 | 2 | OP.1-1 | 2.1 | Preparing the scenario and tprviding training after making the change .CPO-04-VGWTSV-11-09 | تهيه سناريو و انجام آموزش پس از اعمال تغييرات CPO-04-VGWTSV-11-09 | Simulator manager | 2016-03-10 | AI | 2.1
2OP.1-1 | 2 | OP.1-1 | 2.101 | -Providing the training for MCR staff for performing properly the requirements of procedure for donnecting and disconnecting . | انجام آموزش كاركنان اتاق كنترل براي انجام درست الزامات دستورالعمل قطع و وصل اپراتوري در هنگام اجراي سناريوها در سيمولاتور CPO-04-VGWTSV-11-10 | Head of Human resources and Training center | 2016-03-10 | AI | 2.101
2OP.1-1 | 2 | OP.1-1 | 2.102 | -Sending the connection and disconnection blanks to training center. | ارسال بلانكهاي قطع و وصل به مركز آموزش | Equipment-owning managers | permanently | SAT | 2.102
2OP.1-1 | 2 | OP.1-1 | 2.103 | -Using the connection and disconnection in the process of training with simulator. | بكارگيري بلانكهاي قطع و وصل در فرايند آموزش با سيمولاتور | Simulator manager | permanently | AI | 2.103
2OP.1-1 | 2 | OP.1-1 | 2.104 | Providing training to Turbine shift staff about the performance of operator when the power of the Unit is decreasing . CPO-04-VGWTSV-11-11 | انجام آموزش به پرسنل شیفت توربین در خصوص عملکرد اپراتور در زمان کاهش بار واحدCPO-04-VGWTSV-11-11 | Simulator manager | 2016-03-10 | AI | 2.104
2OP.1-1 | 2 | OP.1-1 | 2.105 | Providing the training for MCR staff for performing properly the requirements of procedure for donnecting and disconnecting during performing scenarios in simulator. | انجام آموزش كاركنان اتاق كنترل براي انجام درست الزامات دستورالعمل قطع و وصل اپراتوري در هنگام اجراي سناريوها در سيمولاتورر | Simulator manager | 2016-03-10 | SAT | 2.105
2OP.1-1 | 2 | OP.1-1 | 2.106 | sending the connection and disconnection to the training center. | ارسال بلانكهاي قطع و وصل به مركز آموزش | Equipment-owning managers | permanently | SAT | 2.106
2OP.1-1 | 2 | OP.1-1 | 2.107 | Using the connection and disconnection blanks in the process of training with simulator. СРО-02-VGWTSV-13 | بكارگيري بلانكهاي قطع و وصل در فرايند آموزش با سيمولاتور СРО-02-VGWTSV-13 | Simulator manager | permanently | SAT | 2.107
2OP.1-1 | 2 | OP.1-1 | 2.108 | Making changes in ИЛА РУ as for function of reactor operator after falling of control rod in the core, and also the performance of staff during bringing up the control rod from the core , | ايجاد تغيير در ИЛА РУ در خصوص عملكرد اپراتور راكتور بعد از افتادن ميله كنترل در قلب ، و همچنين عملكرد پرسنل زمان بالا آوردن ميله كنترل از قلب | Reactor manager | 2016-03-01 | SAT | 2.108
2OP.1-1 | 2 | OP.1-1 | 2.109 | Preparing the scenario and providing training after making changes СРО-02-VGWTSV-07-1 | تهیه سناریو و انجام آموزش پس از اعمال تغييرات СРО-02-VGWTSV-07-1 | Simulator manager | 2016-07-01 | AI | 2.109
2OP.1-1 | 2 | OP.1-1 | 2.11 | Providing training for evaluations of ОР СУЗ . СРО-02-VGWTSV-07-03 | انجام آموزش در خصوص رفع рассогласование ОР СУЗ СРО-02-VGWTSV-07-03 | Simulator manager | 2016-03-10 | SAT | 2.11
2OP.1-1 | 2 | OP.1-1 | 2.111 | Briefing the MCR staff aas for using the proceures during changing reactivity , | انجام توجيه پرسنل اتاق كنترل در خصوص استفاده از دستورالعمل‌ها در زمان تغيير راكتيويته | Deputy for production | 2015-10-23 | SAT | 2.111
2OP.1-1 | 2 | OP.1-1 | 2.112 | Providing training for how to use АНФХ (album neutron physical characteristics). СРО-02-VGWTSV-07-04 | انجام آموزش نحوه استفاده از АНФХ СРО-02-VGWTSV-07-04 | Fuel and nuclear safety manager / simulator manager | 2016-03-10 | SAT | 2.112
2OP.1-1 | 2 | OP.1-1 | 2.113 | Making changes ТРБЭ as for the prohibition of increasing the reactor power if the working position of reactor control rods is not in the position specified in Technical Specifications and in case of inefieciency of РОМ, ПЗ-1. СРО-02-VGWTSV-04-01 | انجام تغيير در ТРБЭ در خصوص ممنوعيت افزايش قدرت راكتور در صورتي كه موقعيت كاري ميله‌هاي كنترل راكتور در وضعيت مشخص شده در رگلامنت نبوده و در صورت عدم كارايي РОМ, ПЗ-1. СРО-02-VGWTSV-04-01 | Management of senior engineering of process | 2016-04-01 | SAT | 2.113
2OP.1-1 | 2 | OP.1-1 | 2.114 | Making change in ИЛА РУ as for performance of reactor operator after falling of control rod in the core and also the performance of staff during bringing up the control rod from the core CPO-04-VGWTSV-11-08 | ايجاد تغيير در ИЛА РУ در خصوص عملكرد اپراتور راكتور بعد از افتادن ميله كنترل در قلب ، و همچنين عملكرد پرسنل زمان بالا آوردن ميله كنترل بعد از افتادن ان CPO-04-VGWTSV-11-08 | Reactor manager | 2016-03-01 | SAT | 2.114
2OP.1-1 | 2 | OP.1-1 | 2.115 | making change in the procedure ТРБЭ for how should POM of the power of Y=Unit be limited in case of inefieciency. СРО-02-VGWTSV-03 | انجام تغيير در دستورالعملТРБЭ در خصوص اينكه در صورت عدم كارايي РОМ, محدوديت قدرت واحد به چه صورت بايستي باشد СРО-02-VGWTSV-03 | Management of senior engineering of process / Reactor manager | 2016-04-01 | SAT | 2.115
2OP.1-1 | 2 | OP.1-1 | 2.116 | Making change in the procedure ИЭ РУ as for how to decrease power on the siede of reactor ( injection of noron to primary circuit and shutting down APM and launching the Turbine monitoring system in РД mode.) СРО-02-VGWTSV-11 | انجام تغيير در دستورالعمل ИЭ РУ در خصوص نحوه كاهش توان از سمت راكتور (تزريق بور به مدار اول و خاموش كردن АРМ و قرار دادن سيستم كنترل توربين در رژيم РД) СРО-02-VGWTSV-11 | Reactor manager | 2016-03-30 | AI | 2.116
2OP.1-1 | 2 | OP.1-1 | 2.117 | Making changes in the procedure ИЛА РУ as for the description of small leakage grom primary circuit and impossibility of normally injecting water into primary circuit and performance of the staff in this condition | انجام تغيير در دستورالعمل ИЛА РУ در خصوص شرح رژيم نشت كم از مدار اول و عدم امکان تزريق آب به صورت نرمال به مدار اول و عملكرد پرسنل در اين وضعیت CPO-04-VGWTSV-11-02 | Reactor manager | 2016-03-30 | AI | 2.117
2OP.1-1 | 2 | OP.1-1 | 2.118 | Making changes in the procedure ИЭ РУ about how to decrease the power from the reactor . | انجام تغيير در دستورالعمل ИЛА РУ در خصوص شروع رژيم نشت مدار اول و عدم تزريق آب به صورت نرمال به مدار اول و عملكرد پرسنل در اين وضعيت CPO-04-VGWTSV-11-03، CPO-04-VGWTSV-11-05 | Management of senior engineering of process / Reactor manager | 2016-03-30 | SAT | 2.118
2OP.1-1 | 2 | OP.1-1 | 2.119 | Making change in the procedure ИЭ РУ as for decreasing the power on the side of reactor ( injecting boron to primary circuit and launching the Turbine monitoring system in the РД mode. CPO-04-VGWTSV-11-04 | انجام تغيير در دستورالعمل ИЭ РУ در خصوص نحوه كاهش توان از سمت راكتور (تزريق بور به مدار اول و خاموش كردن АРМ و قرار دادن سيستم كنترل توربين در رژيم РД CPO-04-VGWTSV-11-04 | Reactor manager | 2016-03-30 | AI | 2.119
2OP.1-1 | 2 | OP.1-1 | 2.12 | Making change in the procedure ИЛА ЭО as for the performance of staff during disconnection of transformers and lack of performance of ABP busbars 10Kv and therefore losing the main equipment CPO-04-VGWTSV-11-07 | انجام تغيير در دستورالعمل ИЛА ЭО در خصوص عملکرد پرسنل در زمان قطع ترانسفورماتورها و عدم عملکرد АВР شینهای 10 کیلوولت و در نتیجه از دست دادن تجهیزات اصلی CPO-04-VGWTSV-11-07 | Reactor manager / electricity manager | 2016-06-01 | AI | 2.12
2OP.1-1 | 2 | OP.1-1 | 2.121 | Making change in the procedure ТРБЭ, ИЭ РУ, ИЛА РУ as for explaining how to bring up the group УПЗ, CPO-04-VGWTSV-11-08. | انجام تغيير در دستورالعمل ИЛА РУ ،ТРБЭ, ИЭ РУ در خصوص توضیح نحوه بالا آوردن گروه УПЗ . CPO-04-VGWTSV-11-08 | Reactor manager / fuel and nuclear safety manager / Management of senior engineering of process | 2016-03-30 | SAT | 2.121
2OP.1-1 | 2 | OP.1-1 | 2.122 | Making changes ТРБЭ as for the prohibition of increasing the reactor power if the working position of reactor control rods is not in the position specified in Technical Specifications and in case of inefieciency of РОМ, ПЗ-1. | انجام تغيير در ТРБЭ در خصوص ممنوعيت افزايش قدرت راكتور در صورتي كه موقعيت كاري ميله‌هاي كنترل راكتور در وضعيت مشخص شده در رگلامنت نبوده و در صورت عدم كارايي РОМ, ПЗ-1 | Management of senior engineering of process | 2016-04-01 | AI | 2.122
2OP.1-1 | 2 | OP.1-1 |  | Training in simulator СРО-02-VGWTSV-04-03 | انجام آموزش در سیمولاتور СРО-02-VGWTSV-04-03 | Simulator manager |  | SAT
2OP.1-1 | 2 | OP.1-1 | 2.123 | Providing training about taking the cautionary decisions СРО-02-VGWTSV-04-04 | انجام آموزش در مورد اتخاذ تصمیمات به روش محتاطانه СРО-02-VGWTSV-04-04 | Head of Human resources and Training center | 2016-03-10 | SAT | 2.123
2OP.1-1 | 2 | OP.1-1 | 2.124 | Providing training for Unit shift supervisor,Providing training about how to control the feeding condition of internal consumption CPO-04-VGWTSV-05 | انجام آموزش به رییس شیفت واحد در خصوص نحوه کنترل وضعیت تغذیه مصرف داخلی CPO-04-VGWTSV-05 | Head of Human resources and Training center | 2016-03-10 | SAT | 2.124
2OP.1-1 | 2 | OP.1-1 | 2.125 | Providing traing for the staff about the necessaity of requirements of the operation conversation CPO-04-VGWTSV-01 | آموزش كاركنان در خصوص نحوه انجام الزامات دستورالعمل مكالمات اپراتوري CPO-04-VGWTSV-01 | Head of Human resources and Training center | 2016-03-10 | SAT | 2.125
2OP.1-1 | 2 | OP.1-1 | 2.126 | Briefing the Unit shift supervisor as for how to perform operators conversation and submitting information to dispatcher of power grid in case of lack of presence of NPP shift supervisor. CPO-04-VGWTSV-01 | آموزش رئيس شيفت واحد در خصوص نحوه انجام مكالمات اپراتوري و ارائه اطلاعات به ديسپاچینگ شبكه برق در صورت عدم حضور رئيس شيفت نيروگاهСРО-02-VGWTSV-09-02 | Head of Human resources and Training center | 2016-03-10 | SAT | 2.126
2OP.1-1 | 2 | OP.1-1 |  | Preparing a note about performance of the Unit shift supervisor about the operation conversations and submitting information to dispatcher of power grid in case of lack of presence of NPP shift supervisor, | تهيه يادداشتي در خصوص عملكرد رئيس شيفت واحد در خصوص نحوه انجام مكالمات اپراتوري و ارائه اطلاعات به ديسپاچینگ شبكه برق در صورت عدم حضور رئيس شيفت نيروگاه ، | Head of Human resources and Training center / Deputy for production | 2016-05-21 | AI
2OP.1-1 | 2 | OP.1-1 |  | Applying changes in the procedure of the manner of the operators conversations | انجام تغییرات در دستورالعمل نحوه انجام مكالمات اپراتوري | Management of senior engineering of process | 2016-05-21 | AI
2OP.1-1 | 2 | OP.1-1 | 2.127 | Briefing the Unit shift supervisor as for how to perform operators conversation and submitting information to dispatcher of power grid in case of lack of presence of NPP shift supervisor. СРО-02-VGWTSV-09-03 | انجام توجيه رئيس شيفت واحد در خصوص نحوه انجام مكالمات اپراتوري و ارسال اطلاعات به ديسپاچر شبكه برق در صورت عدم حضور رئيس شيفت نيروگاه СРО-02-VGWTSV-09-03 | Deputy for production | 2016-03-10 | SAT | 2.127
2OP.1-1 | 2 | OP.1-1 | 2.128 | Briefing the MCR staff as for necessity of providing proper and accurate information to superior managers ( operation and administration managers) СРО-02-VGWTSV-09-05 | انجام توجيه كاركنان اتاق كنترل در خصوص لزوم ارائه اطلاعات دقيق و صحيح به مديران مافوق (اپراتوري و اداري)5 СРО-02-VGWTSV-09-0 | Deputy for production / Reactor manager / Turbine manager |  | SAT | 2.128
2OP.1-1 | 2 | OP.1-1 | 2.129 | Revising the requirements related to how to do purposeful briefings and also adding the requirement about the matter that Unit shift supervisor should brief all the staff in case of event of the Unit and especially in case of accident . CPO-04-VGWTSV-07 | بازنگري الزامات مربوط به نحوه انجام توجيهات هدفمند و همچنين اضافه نمودن الزام مربوط به اينكه در صورت بروز اتفاق در بلوك و مخصوصاً در صورت بروز حادثه، رئيس شيفت واحد تمامي پرسنل را توجيه نمايد CPO-04-VGWTSV-07 | Management of senior engineering of process | 2016-03-10 | AI | 2.129
2OP.1-1 | 2 | OP.1-1 | 2.13 | Briefing the staff of MCR about the matter that issuing the order for opening the electrical schema of equipment rests with the Unit shift supervisor and the shift supervisors of managements can do it with the permit of the unit shift supervisor. CPO-04-VGWTSV-09 | انجام توجیه کارکنان اتاق کنترل در خصوص آنكه صدور دستور براي باز كردن شماي الكتريكي تجهيزات بر عهده رئيس شيفت واحد بوده و رئيس شيفت مديريتها با اجازه رئيس شيفت واحد مي توانند آنرا انجام دهند CPO-04-VGWTSV-09 | Management of senior engineering of process | 2016-03-10 | AI | 2.13
2OP.1-1 | 2 | OP.1-1 | 2.131 | Take into account both internal and external operating experience in the development of plans for training of operator personnel of control room in the FSS. | Take into account both internal and external operating experience in the development of plans for training of operator personnel of control room in the FSS. | Deputy for production / Head of Human Resources and Training Center /Manager of management system and supervision (Head of Operating experiences group) | Done. 12/30/2015 | AI | 2.131
|  |  | R.3 | AFI MA.2-1 Corrective measure - Corrective measures in the field of Maintenance and Repairs | اقدامات اصلاحی AFI MA.2-1 | Responsible entity Deputy for M&R | Deadline |  | R.3
3MA.2-1 | 3 | MA.2-1 | 3.1 | Submitting monthly report about development and execution of mechanical repair documents from contractor to manager of plant and M&R division. | ارائه گزارش ماهانه از وضعيت تدوین و اجرایی نمودن مدارک تعمیراتی مکانیک از پيمانكار به رييس نيروگاه و معاونت نت | Deputy for M&R / Planning and technical documents manager | September 17, 2015Permanently in every month | SAT | 3.1
3MA.2-1 | 3 | MA.2-1 | 3.2 | Correspondence with NPPD about condition of M&R documents and pursuing unitl reaching the result. | مكاتبه با شركت توليد و توسعه در رابطه با وضعيت مدارك نت و پي گيري تا حصول نتيجه | Deputy for M&R / M&R manager | 2015-10-12 | SAT | 3.2
3MA.2-1 | 3 | MA.2-1 |  |  | مكاتبه با شركت توليد و توسعه در رابطه با وضعيت مدارك نت و پي گيري تا حصول نتيجه | Deputy for M&R / / Electricity manager / I&C manager |  | SAT
3MA.2-1 | 3 | MA.2-1 | 3.3 | Preparing sechdeule of revising repair documents and submitting the program to M&R division. | تهیه برنامه زمانبندی بازنگری مدارک تعمیرات و ارسال برنامه به معاونت نت | Deputy for M&R / Manager of planning and technical documentataions | 2015-09-11 | SAT | 3.3
3MA.2-1 | 3 | MA.2-1 | 3.4 | Preparing the procedure of categorizing the repairs workers. | تهیه دستورالعمل رده بندی کارگران تعمیرات | Deputy for M&R / Mechanical repairs manager | 2016-02-19 | SAT | 3.4
3MA.2-1 | 3 | MA.2-1 | 3.5 | Executimg the procedure of categorizing the repairs workers. | اجرايي نمودن دستورالعمل رده بندی کارگران تعمیرات | Deputy for M&R / | 2016-04-21 | AI | 3.5
3MA.2-1 | 3 | MA.2-1 | 3.6 | Preparing, approving and executing checklist of technical service of rotary equipment based on the type of equipment. | تهيه ، تاييد و اجرايي نمودن برنامه ها (چك ليست) سرويس هاي فني تجهيزات دوار بر اساس تيپ تجهيزات | Deputy for M&R / TAPNA rotary equipment repair manager | 2016-03-10 | SAT | 3.6
3MA.2-1 | 3 | MA.2-1 | 3.7 | Preparing, approving and executing checklist of technical service of static equipment based on the type of equipment. | تهيه ، تاييد و اجرايي نمودن برنامه ها (چك ليست) سرويس هاي فني تجهيزات استاتيك بر اساس تيپ تجهيزات | Deputy for M&R / TAPNA static equipment repair manager | 2016-03-10 | SAT | 3.7
3MA.2-1 | 3 | MA.2-1 | 3.8 | Preparing, approving and executing checklist of technical service of ventilation equipment based on the type of equipment. | تهيه ، تاييد و اجرايي نمودن برنامه ها (چك ليست) سرويس هاي فني تجهيزات تهويه بر اساس تيپ تجهيزات | Deputy for M&R / TAPNA ventilation equipment repair manager | 2016-03-10 | SAT | 3.8
3MA.2-1 | 3 | MA.2-1 | 3.9 | Preparing, approving, and executing the checkislts of repairs which have nuclear hazard. | تهيه ، تاييد و اجرايي نمودن برنامه هاي كار تعميرات با خطر هسته اي | Deputy for M&R / Head of primary circuit equipment displacement | 2016-01-10 | SAT | 3.9
3MA.2-1 | 3 | MA.2-1 | 3.1 | Preparing, approving, and executing the checklists of technical services of electrical equipment. | تهيه ، تاييد و اجرايي نمودن برنامه ها (چك ليست) سرويس هاي فني تجهيزات برقي | Electricity manager | 2016-03-10 | SAT | 3.1
3MA.2-1 | 3 | MA.2-1 | 3.11 | Preparing, approving, and executing checklist of technical services of I&C equipment. | تهيه ، تاييد و اجرايي نمودن برنامه ها (چك ليست) سرويس هاي فني تجهيزات كنترل و ابزار دقيق | I&C manager | 2016-03-10 | SAT | 3.11
3MA.2-1 | 3 | MA.2-1 | 3.12 | Revising the M&R repair document based on the experiences reached during 3-year repairs. | بازنگري مدارك تعميرات نت بر اساس تجربيات بدست آمده در زمان تعميرات 3 ساله | Deputy for M&R / M&R manager / electricity manager / I&C manager | 2016-03-10 | SAT | 3.12
3MA.2-1 | 3 | MA.2-1 | 3.13 | Adding the article related to unplanned emergency repairs in the daily chart. МА-01-GI-02 | اضافه نمودن بند مربوط به تعمیرات اضطراری خارج از برنامه در گراف روزانه МА-01-GI-02 | Deputy for M&R / M&R programming manager | 2015-09-11 | SAT | 3.13
3MA.2-1 | 3 | MA.2-1 | 3.14 | Cleaning the place of installing the equipment ZF.02.12-ZF.02.58, existence of metal covr of thermal insulation beside the repair people. | تمیزکاری محل نصب تجهیزات ZF.02.12-ZF.02.58 –وجود پوشش فلزی عایق حرارتی در کنار تعمیرکاران آماده سازی محل فعالیت تعمیرات UF11S067 - آموزش کارکنان МА-02-GI-01 | Turbine manager Ventilation manager | 2015-09-11 | SAT | 3.14
3MA.2-1 | 3 | MA.2-1 | 3.15 | Equipping the repair groups, preparing the containers particular for keeping alcohol, acetone, oil et cetra. (Facts: МА-02-GI-02 , MA-02-SP-04 , MA-01-SP-10) | تجهیز گروههای تعمیراتی -تهیه ظروف مخصوص نگهداری الکل، استن،روغن و ... МА-02-GI-0 / MA-02-SP-04 / MA-01-SP-10 | Deputy for M&R | 2015-11-06 | SAT | 3.15
3MA.2-1 | 3 | MA.2-1 | 3.16 | Training the staff of repairs and observing the technical requirements of repair documents – job was not done in accordance with checklist of repairs. Valve was not manually assembled and disassembled according to the repair documents because of working mode of the system. МА-02-GI-03 | آموزش کارکنان تعمیرات و رعایت الزامات فنی مدارک تعمیرات حین فعالیت-کارمطابق با چک لیست تعمیرات انجام نشد-بعد از تعمیرات والو مطابق با مدرک دستورالعمل تعمیرات به صورت دستی باز و بسته نشد.به دلیل رژیم کاری سیستم. МА-02-GI-03 | Deputy for M&R / TAPNA static equipments repairs manager | 2016-01-20 | SAT | 3.16
3MA.2-1 | 3 | MA.2-1 | 3.17 |  | بازنگری و اجرایی نمودن چک لیست ها و مدارک تعمیرات تجهيزات دوارМА-03-GI-01 | Deputy for M&R / TAPNA rotary equipments repairs manager |  | SAT | 3.17
3MA.2-1 | 3 | MA.2-1 | 3.18 |  | لزوم بازرسی و تصحیح ورودی های کانال ZW40 MA-01-SP-01 | Reactor manager |  | SAT | 3.18
3MA.2-1 | 3 | MA.2-1 | 3.19 | Revising and correcting the permits, briefing the staff . MA-01-SP-03 | بازنگری و اصلاح متن ناریادها- توجیه پرسنل MA-01-SP-03 | Ventilation manager | 2016-01-20 | SAT | 3.19
3MA.2-1 | 3 | MA.2-1 | 3.2 | Revising how the permits are prepared- recording the conditions of safew work and personal protection equipment , briefing the staff. MA-01-SP-04 | بازنگری نحوه تدوین ناریادها – درج شرایط ایمن انجام کار و لوازم حفاظت شخصی کارکنان- توجیه پرسنل MA-01-SP-04 | Ventilation manager | 2016-01-20 | SAT | 3.2
3MA.2-1 | 3 | MA.2-1 | 3.21 | Training about how to fill the permits properly , there was no signature of ventilation shift supervisor in the permit 195, not briefing the staff.MA-01-SP-05 | آموزش تکمیل صحیح ناریاد- در ناریاد 195 امضای رییس شیفت تهویه نبود توجیه پرسنل MA-01-SP-05 | Ventilation manager | 2016-01-20 | SAT | 3.21
3MA.2-1 | 3 | MA.2-1 | 3.22 | Providing technical training of ventilation repair group about how to use technical repair docuemnts. MA-01-SP-11 , MA-01-SP-07 | آموزش فنی کارکنان گروه تعميرات تهويه در ارتباط با نحوه استفاده از مدارك فني تعميراتي MA-01-SP-11MA-01-SP-07 | Head of ventilation repairs group | 2015-08-06 | SAT | 3.22
3MA.2-1 | 3 | MA.2-1 | 3.23 | Organizing and planning for performing simultaneously the current technical services of equipment ( electrical-mechanical). MA-01-SP-08 | سازماندهی و برنامه ریزی انجام همزمان سرویس های فنی جاری تجهیزات (برقی- مکانیکی) MA-01-SP-08 | M&R programming group | implemented | SAT | 3.23
3MA.2-1 | 3 | MA.2-1 | 3.24 | Revising and correcting the forms and checklists related to repais of ventilation equipment. | بازنگری و تصحیح فرم ها و چک لیست های کاری مربوط به تعميرات تجهيزات تهويه MA-01-SP-09 | Head of ventilation repairs group | 2015-10-07 | AI | 3.24
3MA.2-1 | 3 | MA.2-1 | 3.25 | Providing training og operation experiences to repairman in order to prevent the defect of GY50D001 again , records of equipment in a management should be given to the repairs group at the beginning og repairs of one equipment. MA-03-SP-01 | آموزش تجارب بهره برداری تجهیزات به تعمیرکار جهت جلوگیری ار بروز مجدد عیب GY50D001 سوابق تجهيزات در مديريت در زمان شروع تعميرات يك تجهيز به گروه تعميرات ارائه گردد MA-03-SP-01 | Reactor manager | 2016-01-20 | SAT | 3.25
3MA.2-1 | 3 | MA.2-1 | 3.26 | Briefing the head of diesel repair group about organizing the repair activities in proportion with the volume of activities. | توجيه رييس گروه تعميرات ديزل در ارتباط با سازماندهي فعاليت هاي تعميراتي متناسب با حجم فعاليت ها MA-03-SP-03 | Deputy for M&R | 2015-09-11 | SAT | 3.26
3MA.2-1 | 3 | MA.2-1 | 3.27 | Revising and correcting the program of job planning СМ-78 about technicians passing practical training after finishing theoretical training – datek program and at the moment the comment has been removed.Updating the repair documents is the attachment of the table. МА-04- SP -04 | بازنگری و تصحیح برنامه آماده سازی شغلی СМ-78 در خصوص گذراندن دوره آموزش های عملی کاردان ها بعد از اتمام دوره آموزش تئوری- برنامه داتک بوده و در حال حاضر کامنت رفع شده است.به روز رسانی مدارک تعمیرات مدرک ضمیمه جدول می باشد МА-04- SP -04 | Head of human resources and training center | implemented | SAT | 3.27
3MA.2-1 | 3 | MA.2-1 | 3.28 | Revising , root-finding and correcting the schedules of repair volumes – from 3331 activities scheduled , 1733 activity was performed and about %52 are nor yet done. Meanwhile, 576 unplanned activities have been done during repairs. On the basis of the grid request, the Unit was disconnected before the due time . The definite time of announcing the outage was not announced to TAPNA company until the last working operational day and this was because of lack of providing кд and lack of response of contractor in due time. The process of repair is a common process which includes spare parts for technical support and performing repairs and the implementation of program is depends on complete execution of all mentioned processes including preparation of conditions of equipment and systems for performing repairs, issuing repair permits, providing suitable spare parts, providing drawings and working documentset cetra. МА-04- SP -05 | بازنگری، ریشه یابی علل و تصحیح برنامه های زمانبندی احجام تعمیراتی –از 3331 فعالیت برنامه ریزی شده 1733 فعالیت اجرا شده و حدود 52 در صد احجام اجرا نشده اند در صورتیکه 576 فعالیت برنامه ریزی نشده در طول تعمیرات 2015 صورت گرفته است .براساس درخواست شبکه ، واحد پیش از موعد مقرر متوقف شد زمان قطعی اعلام توقف تا آخرین روز کارکرد نیروگاه به صورت رسمی به تپنا اعلام نشد و این امر به دلیل عدم تامین هیتر های кд و عدم پاسخ پیمانکار در موعد مقرر بروز نمود.فرایند تعمیرات فرایندی مشترک شامل تولید قطعات یدکی پشتیبانی فنی و اجرا تعمیرات می باشد که تحقق برنامه منوط به انجام کامل تمامی فرایند های مذکور من جمله آماده ساری شرایط تجهیزات و سیستم ها برای انجام تعمیرات ، صدور مجوز های تعمیراتی ، تامین قطعات یدکی مناسب ، تامین نقشه ها و مدارک کاری و ... می باشد. МА-04- SP -05 | Deputy for M&R | implemented | SAT | 3.28
3MA.2-1 | 3 | MA.2-1 | 3.29 | Reviewing repair documents – results of analyzing the documents Руководстве при ремонте (68.BU.1.0.0.ABR.RTO.ETS033, 68.BU.1.0.0.ABR.RTO.ETS265, 68.BU.1.0.0.ABR. RTO.ETS079) shows that mentioned documents do not meet the requirements of procedure PRO-3150-04. MA-05-SP-01 | بازبینی مدارک تعمیرات -نتایج آنالیز مدارک Руководстве при ремонте» (68.BU.1.0.0.ABR.RTO.ETS033, 68.BU.1.0.0.ABR.RTO.ETS265, 68.BU.1.0.0.ABR. RTO.ETS079 نشان میدهد که مدارک مذکور الزامات دستوالعمل PRO-3150-04 را برآورده نمی کند MA-05-SP-01 | TAPNA engineering and technical manager | 2015-09-11 | SAT | 3.29
3MA.2-1 | 3 | MA.2-1 | 3.3 | periodically revise the M&R documents, the validity period was envisaged three years for M&R documentsand the first document should be revised periodically in Iranian year 1395. | رعایت برنامه بندی تهیه و تدوین مدارک(نامه ) تهیه برنامه زمان بندی به روز رسانی مدارک همانند مدارک بهره برداری، مدت زمان اعتبار مدارک نت 3 سال در نظر گرفته شده است و اولین مدرک در سال 95 بایستی مورد بازنگری دوره‌ای قرار گیرد MA-05-SP-02 | TAPNA engineering and technical manager | Implemented under control | SAT | 3.3
3MA.2-1 | 3 | MA.2-1 | 3.31 |  | به روز رسانی و سازماندهی ژورنال عیوب- بیش از 11 عیب از سال 2012 در ژورنال Журнала дефектов и неполадок оборудования электротехнического оборудования» مشاهده می شود که به دلیل عدم وجود قطعات یدکی برطرف نشده اند. MA-02-SP-01 | Electricity manager / Commercial and equipment manager |  | AI | 3.31
3MA.2-1 | 3 | MA.2-1 | 3.32 | Developing, revising, and registering the working documents , list of activities at the hand of execting personnel of repairs шкафа0,4кВ 10NN01H lack registration Number , are not approvedand their activity description is not relevant to mentioned equipment. Two different activites were recorded in the article 12. MA-02-SP-02 | تدوین ، بازنگری و ثبت مدارک کاری –فهرست فعالیت های در دست مجریان تعمیرات шкафа 0,4кВ 10NN01H فاقد شماره ثبت ، تایید نشده و دارای شرح فعالیت غیر مرتبط با تجهیز مذکور بودند. در بند 12 در یک بند دو فعالیت متفاوت درج شده است MA-02-SP-02 | Electricity manager | 2015-10-12 | SAT | 3.32
3MA.2-1 | 3 | MA.2-1 | 3.33 | Updating the working documents. In the attached drawing and inside the tableau шкафа, 0,4кВ 10NN01H and drawing of repair-executing people do not agree with each other. There are some crossed out items and corrections with pencil and pen and the documents have not been approved yet. MA-02-SP-03 | به روز رسانی مدارک کاری –نقشه الصاقی در داخل تابلو шкафа 0,4кВ 10NN01H و نقشه در دست مجریان مغایرت داشته، خط خوردگی و تصحیحات با مداد و خودکار مشاهده شده و مدارک تایید شده نیستند. در نقشه کلید 10UL43D01 وجود ندارد. MA-02-SP-03 | Electricity manager | 2015-10-12 | SAT | 3.33
3MA.2-1 | 3 | MA.2-1 | 3.34 | Revising and updating rhe defect logbook of shift staff АСУ ТП. The review of logbook shows that there are 9 defects remaining from 2013. 34 defects remaining from 2014 have not been removed yet. ( All of the defects of 2013 were removed and considering the statement of contractor regarding the provision of spare parts for removing the mentioned defects until the end of overhaul 2015, the deadline for removing the remaining defects from 2014 is announced as 6 Dec. 2015 and 26 defects of the year 2014 (out of 34 defects ) has not been removed yet. | بازنگری و به روز رسانی ژورنال عیوب محل کاری کارکنان شیفت АСУ ТП –در بررسی ژورنال عیوب 9 عیب از سال های 2013 به دلیل عدم وجود قطعات یدکی وجود دارد.34 عیب از سال 2014 برطرف نشده است( کل عیوب سال2013 با توجه به اظهارات پیمانکار در خصوص تامین قطعات یدکی جهت رفع ایرادات ذکر شده تا پایان تعمیرات اساسی 2015، مهلت رفع ایرادات باقیمانده از سال 2014، 15/09/94 اعلام می‌گردد از 34 مورد عیوب سال 2014 تعداد 26 مورد باقیمانده است) МА-04-GI-01 | I&C manager | 2015-12-06 | SAT | 3.34
|  |  | R.4 | AFI EN.1-1 Corrective measure - Corrective measures in the Technical Support and Engineering area | اقدامات اصلاحی AFI EN.1-1 | Responsible entity Deputy for technical and engineering | Deadline |  | R.4
4EN.1-1 | 4 | EN.1-1 | 4.1 | Preparing the procedure of visit and tend of analysis of system engineers from the related equipment and systems along with requirements ( including aim of the visit, period of visits, visit of deputies of management, and manager ; it is a requirement to consider the human resources, logbooks, requirement of preparing the checklist , information form, process of the defect report and pursuing them, checklist format, general checklist for visits, process of recording the results of visits, et cetera. ) | تهيه دستورالعمل بازديد و ترند آناليز مهندسين سيستم از تجهيزات و سيستم هاي مربوطه همراه با الزامات (شامل: هدف از بازديد، دوره بازديد ها، بازديد معاونين مديريت و مديريت با الزام توجه به موارد منابع انساني، دفاتر ثبت، الزام تهيه چک ليست، فرم ثبت اطلاعات، روند گزارش ايرادات و پي گيري آنها، فرمت چک ليست و الزامات چک ليست، چک ليست کلي براي بازديد ها، روند درج نتايج بازديد ها، و ساير موارد) | Deputy for technical and engineering / Manager of management system and supervision | 2016-04-22 | SAT | 4.1
4EN.1-1 | 4 | EN.1-1 | 4.2 4.3 4.4 4.5 4.6 | Preparing the exclusive procedure of visit and tend of analysis of system engineers from the equipment and system in the area of reactor equipments, Turbine equipments, chemistry equipments, common facilities equipments, ventilation equipments and | تهيه چک ليست اختصاصي بازديد مهندسين سيستم از سيستم ها و تجهيزات در حوزه تجهيزات مدیریت ذیربط | Reactor manager / Turbine manager / Chemistry manager / Manager of common facilities / Ventilation manager | 2016-02-29 | SAT | 4.2 4.3 4.4 4.5 4.6
4EN.1-1 | 4 | EN.1-1 | 4.7 | Preparing the procedure of visit and tend of analysis of system engineers from the equipment and system of I&C. | تهيه چک ليست اختصاصي بازديد مهندسين سيستم از سيستم ها و تجهيزات در حوزه تجهيزات کنترل و ابزار دقيق | I&C manager | 2016-02-29 | SAT | 4.7
4EN.1-1 | 4 | EN.1-1 | 4.8 | Preparing the procedure of visit and tend of analysis of system engineers from the electrical equipment and systems. 4.8 | تهيه چک ليست اختصاصي بازديد مهندسين سيستم از سيستم ها و تجهيزات برقي | Electricity manager | 2016-02-29 | SAT | 4.8
4EN.1-1 | 4 | EN.1-1 | 4.9 | Preparing the format of data bank of monitoring equipment , systems and parameters , providing the conditions in order to record them in the internal network of NPP. 4.9 | تهيه فرمت پايگاه بانک اطلاعاتي پايش تجهيزات و سيستم ها و پارامترها، ايجاد شرايط جهت ثبت در شبکه داخلي نيروگاه، | Deputy for technical and engineering / ITC manager | 2016-03-19 | SAT | 4.9
4EN.1-1 | 4 | EN.1-1 | 4.10 4.11 4.12 4.13 4.14 | Preparing the list of parameters from reactor, Turbine, chemistry, common facilities, system which are needed to be monitored constantly and recording them in data bank and analyzing trend of changes and time period of trend analysis. | تهيه فهرست پارامترهايي از سيستم هاي راکتور ، توربين، شیمی، تهویه و سیستمهای مشترک که نياز است بصورت مداوم پايش شوند و درج در بانک اطلاعاتي و آناليز ترند تغييرات و دوره زماني انجام ترند آناليز | Turbine manager / Chemistry manager / Reactor manager / Ventilation manager / Common facilities manager | 2016-02-20 | SAT | 4.10 4.11 4.12 4.13 4.14
4EN.1-1 | 4 | EN.1-1 | 4.15 | Preparing the list of parameters from electrical system which are needed to be monitored constantly and recording them in data bank and analyzing trend of changes and time period of trend analysis. | تهيه فهرست پارامترهايي از سيستم هاي برقي که نياز است بصورت مداوم پايش شوندو و درج در بانک اطلاعاتي و آناليز ترند تغييرات و دوره زماني انجام ترند آناليز | Electricity manager | 2016-02-20 | SAT | 4.15
4EN.1-1 | 4 | EN.1-1 | 4.16 | Preparing the list of parameters from I&C system which are needed to be monitored constantly and recording them in data bank and analyzing trend of changes and time period of trend analysis. | تهيه فهرست پارامترهايي از سيستم هاي کنترل و ابزار دقيق که نياز است بصورت مداوم پايش شوندو و درج در بانک اطلاعاتي و آناليز ترند تغييرات و دوره زماني انجام ترند آناليز | I&C manager | 2016-02-20 | SAT | 4.16
4EN.1-1 | 4 | EN.1-1 | 4.17 | Preparing the procedure of evaluation of corrective measures and reviewing their effectiveness. | تدوين دستورالعمل ارزيابي اقدامات اصلاحي انجام شده و بررسي موثر بودن آنها | Head of operating experiences group | 2015-12-06 | SAT | 4.17
4EN.1-1 | 4 | EN.1-1 | 4.18 | Monitoring and analysis of effectiveness of corrective measures in order to evaluate corrective measures and avoiding the recurrence of accidents. | کنترل و آناليز موثر بودن اقدامات اصلاحي به منظور ارزيابي اقدامات اصلاحي و جلوگيري از تکرار رويدادها | Manager of management system and supervision / Relevant managers | 3/19/2016 For the accidents which have occurred and after that permanently | AI | 4.18
4EN.1-1 | 4 | EN.1-1 | 4.19 | In order to find root cause of accidents and determine exactly the root causes , also it is necessary to have specialist for methodology of investigate the accidents. | به منظور ريشه يابي حوادث و تعيين دقيق دلايل ريشه اي علاوه بر مهندسين سيستم نياز است تا متخصص متدولوژي بررسي حوادث نيز وجود داشته باشد. لذا سازماندهي آموزش متدولوژي ريشه يابي حوادث (ASSET) و (HPES) و اخذ گواهي نامه | Head of Human resources and training center / Manager of management system and supervision | 2016-08-21 | FAR | 4.11
4EN.1-1 | 4 | EN.1-1 | 4.12 | Organizing and executing the general training of methods of investigating the accidents for the staff who are involved in the analysis of defects and accidents. 4.20 | سازماندهي و اجراي آموزش عمومي متدهاي بررسي رويدادها براي کارکناني که در آناليز خرابي ها و حوادث مشارکت دارند | Head of Human resources and training center | 2016-12-21 | AI | 4.12
4EN.1-1 | 4 | EN.1-1 | 4.14 | When choosing the operational control key parameters, consider requirements of Technological regulations, equipment certificates, technical conditions for the operation of the equipment and also operational experience. |  | Deputy for engineering and technical support | 2016-01-30 | SAT | 4.14
4EN.1-1 | 4 | EN.1-1 | 4.15 | Develop a schedule for implementation of a unified database of equipment defects, defining milestones and specific timelines for each stage. |  | Deputy for engineering and technical support | Q3, 2016 | SAT | 4.15
4EN.1-1 | 4 | EN.1-1 |  | • Сделать запрос через ВАО АЭС-МЦ о применяемых на других АЭС методах анализа состояния оборудования, анализа тенденций изменения ключевых эксплуатационных параметров, а также анализа дефектов оборудования. |  | Deputy for engineering and technical support | During 2016 | SAT
4EN.1-1 | 4 | EN.1-1 |  | · При выборе контролируемых ключевых эксплуатационных параметров руководствоваться требованиями Технологического Регламента, паспортов оборудования, технических условий на работу оборудования, а также эксплуатационным опытом. |  | Deputy for engineering and technical support | During 2016
4EN.1-1 | 4 | EN.1-1 |  | • Разработать план-график внедрения единой базы данных дефектов оборудования, определяющий основные этапы и конкретные сроки реализации каждого этапа. |  | Deputy for engineering and technical support | During 2016
|  |  | 4.17 | AFI CM.3-1 Corrective measure - Corrective measures in the Technical Support and Engineering area | اقدامات اصلاحی AFI CM.3-1 | Responsible entity Deputy for technical and engineering | Deadline |  | R.
4CM.3-1 | 4 | CM.3-1 | 4.18 | Revising and making changes in the procedure of investigating the accidents in a way that the compliance of corrective measures before execution should be checked with requirements of FSAR and Technical Specification. It should not be written generally that the corrective measures do not agree with the requirement. The text and article of the given documents about the related system should be mentioned and then it should be concluded that the corrective measure has no non-compliance. 4.21 | بازنگري و اعمال تغييرات در دستورالعمل بررسي حوادث به اين ترتيب كه تطابق اقدامات اصلاحي قبل از اجرا مي بايست با الزامات مدارك FSAR و TECHICAL SPECIFICATION چك گردد. نبايد بصورت كلي نوشته شود كه با الزامات مدارك مذكور اين اقدام اصلاحي مغايرت ندارد، بلكه مي بايست متن و بند مدارك پيش گفته در خصوص سيستم مورد نظر ذكر شده و سپس نتيجه گيري گردد كه اقدام اصلاحي مغايرتي ندارد. | Manager of management system and supervision | 2015-10-23 | SAT | 4.17
4CM.3-1 | 4 | CM.3-1 | 4.19 | Revising and making changes in the procedure of correction and improvement in equipment and systems in a way that before temporary or permanent improvement, the requesting management should submit the report which shows that the safety of plant is not affected and safety margin is protected. The basis of report is FSAR and Technical Specifications. 4.22 | بازنگري و اعمال تغييرات در دستورالعمل اصلاح و بهبود در تجهيزات و سيستمها بطوريكه قبل از انجام بهبود موقت و يا دائم، مديريت متقاضي مي بايست گزارش عدم تاثير بر ايمني نيروگاه با ذكر حفظ حاشيه ايمني (Safety Margin) ارائه نمايد. مبناي تهيه گزارش مي تواند، مدارك FSAR و TECHICAL SPECIFICATION باشد. | Manager of the equipment and systems performance analysis | 2015-11-22 | SAT | 4.18
4CM.3-1 | 4 | CM.3-1 | 4.2 | Preparing the format of concentrated data bank of modernizations and obtaining the approval of deputies and chief engineer. 4.23 | تهيه فرمت بانك اطلاعاتي متمركز مدرنيزيشن ها و اخذ تائيديه از معاونت ايمني و سرمهندس نيروگاه | Manager of the equipment and systems performance analysis | 2015-10-27 | SAT | 4.19
4CM.3-1 | 4 | CM.3-1 | 4.21 | Preparing the order for the process of registering, accounting the temporary changes in data bank and access of staff to the data bank. 4.24 | تهيه دستور در رابطه با روند ثبت ، حسابرسي تغييرات موقت در بانک اطلاعاتي و دسترسي هاي کارکنان به بانک اطلاعاتي | Manager of the equipment and systems performance analysis | 2016-01-20 | SAT | 4.2
4CM.3-1 | 4 | CM.3-1 | 4.22 | Completing the concentrated data bank of permanent modernizations including the corrections on the equipment and technical orders in a way that it would be the reference for all plant units in terms of temporary modernizations. 4.25 | تكميل بانك اطلاعاتي متمركز بهبودها (مدرنيزاسيون ها) شامل انجام اصلاحات بر روي تجهيز و دستورات فني بطوريكه مرجع كليه واحدهاي نيروگاه در خصوص مدرنيزشن هاي موقت باشد. | Manager of the equipment and systems performance analysis / Manager of senior engineering of process / Equipment -owning managers | 2016-10-22 | SAT | 4.21
4CM.3-1 | 4 | CM.3-1 | 4.23 | Completing the concentrated data bank of improvements (modernizations) which are temporary including performing the corrections on the equipment and technical orders in a way that it would be a reference for all of the NPPs Units in terms of temporary modernizations . | تكميل بانك اطلاعاتي متمركز بهبودها (مدرنيزاسيون ها) موقت شامل انجام اصلاحات بر روي تجهيز و دستورات فني بطوريكه مرجع كليه واحدهاي نيروگاه در خصوص مدرنيزشن هاي موقت باشد. | Manager of the equipment and systems performance analysis | 2016-10-22 | SAT | 4.22
4CM.3-1 | 4 | CM.3-1 | 4.24 | TSM through the WANO-MC about applied at other plants about management practices and techniques for temporary modifications. |  | Deputy for engineering and technical support / Manager of the equipment and systems performance analysis | Done | SAT | 4.23
4CM.3-1 | 4 | CM.3-1 | 4.25 | Identify and document the requirement for the maximum duration of temporary modifications - not more than 1 year or a fuel company. |  | Deputy for engineering and technical support / Manager of the equipment and systems performance analysis | Q1, 2016 | SAT | 4.24
4CM.3-1 | 4 | CM.3-1 | 4.26 | Identify the persons responsible for the inclusion in the schedule of repairs, measures to eliminate temporary modifications. oblige responsibles to document the removal of temporary modifications after repairs. |  | Deputy for engineering and technical support / Manager of the equipment and systems performance analysis | 2016 | SAT | 4.25
R.5
|  |  | 5.1 | AFI CY.1-1 Corrective Measures - Corrective measures in the field of Chemistry | اقدامات اصلاحی AFI CY.1-1 | Responsible Entity Chemistry manager | deadline |  | R.5
5CY.1-1 | 5 | CY.1-1 | 5.2 | Unplanned training was performed for Chemistry laboratory technicians in the field of main regulations of BNPP operation and the logbook of training with registration number LGB-1442-1951 should be registered and signed in the room of chemistry shift supervisor. | برای کاردان هاي آزمایشگاه شیمی آموزش خارج از برنامه در زمینه قوانین اصلی بهره برداری نیروگاه اتمی برگزار شد و در دفتر ثبت تعلیمات مربوطه به شماره ثبتی LGB-1442-1951 در اتاق رئیس شیفت شیمی ثبت و امضاء شود. | Chemistry manager / Chemistry Lab. Manager | 2015-10-12 | SAT | 5.1
5CY.1-1 | 5 | CY.1-1 | 5.3 | Locating three tables in places where it was necessary to put oxygen gauge in building ZF. They were designed and the requisites for manufacturing were provided and were delivered to workshop section. They have been manufactured and are transferred to the related places. | سه عدد میز جهت استقرار در مکان هايی كه نیاز به قرار دادن دستگاه اکسیژن سنج در ساختمان ZF بود، طراحی و ملزومات مورد نیازجهت ساخت تامین شد و جهت ساخت به قسمت تاسیسات ساختمانی تحویل گردید که درحال حاضر ساخته شده و به مکان های مربوطه منتقل می شود. | Chemistry manager | 2015-10-12 | SAT | 5.2
5CY.1-1 | 5 | CY.1-1 | 5.4 | Comparing the results of automatic and manual analysis for two months and submitting the report along with suggestions given to BNPP chief engineer in order to taking necessary decision | تطابق نتايج آناليز دستي و اتوماتيک به مدت 2 ماه و ارسال گزارش به همراه پيشنهادات به سرمهندس نيروگاه جهت اتخاذ تصميم لازم | Chemistry manager | 2015-11-11 | AI | 5.3
5CY.1-1 | 5 | CY.1-1 | 5.5 | Pursuing the removal of defects of automatic monitoring system of chemistry regimes of BNPP main circuits water. | پي گيري رفع ايرادات سيستم کنترل اتوماتيک رژيم شيميايي آب مدار هاي اصلي نيروگاه | I&C manager / Chemistry manager | 2016-09-10 | SAT | 5.4
5CY.1-1 | 5 | CY.1-1 | 5.6 | On the basis of analysis measurement procedure before sampling of secondary circuit for analyzing iron and copper , the route should be blown and drain completely. Manual and automatic sampling was performed for providing the blowing and draining the route in 6 separation points of line. | بر اساس دستور العمل اندازه گیری آنالیز ها قبل از نمونه برداری از آب مدار دوم جهت آنالیز آهن و مس نیاز به پرادووکا و درین کامل مسیر می باشد که برای تامین پرادووکا و درین مسیر در 6 نقطه جداسازی خط نمونه برداری دستی و اتومات انجام گردید. | Chemistry manager | 2015-11-11 | SAT | 5.5
5CY.1-1 | 5 | CY.1-1 | 5.7 | The suitable table should be provided for correctly reading the graduated burette by operator of ZG.01. | جهت قرائت صحیح بورت مدرج توسط اپراتور ZG.01 ، میز مناسب تامین گردد. | Chemistry manager | 2015-09-21 | SAT | 5.6
5CY.1-1 | 5 | CY.1-1 | 5.8 | In order to provide clock in the location of sampling, purchase request should be given to logistic support management and the issue should be pursued. | جهت تامین ساعت در محل نمونه برداری به قسمت مدیریت پشتیبانی درخواست خرید داده شود و پي گيري تامين صورت پذيرد | Chemistry manager | 2015-09-21 | SAT | 5.7
5CY.1-1 | 5 | CY.1-1 | 5.9 | Additional cooler was requested for providing the temperature 250 C Celsius in laboratory environment and the issue should be pursued. | جهت تامین دمایc ˚25 در محیط آزمایشگاه درخواست کولراضافی داده شد و پي گيري نصب صورت پذيرد. | Chemistry manager | implemented | SAT | 5.8
5CY.1-1 | 5 | CY.1-1 | 5.1 | In the program of the staff competence maintenance in the Iranian year ( beginning March 21, 2015), a training session about the defects raised in WANO peer review should be taken into account for day workers and shift workers and all of the staff should be briefed in this regard. | در برنامه حفظ صلاحيت کارکنان در سال 94 يک جلسه آموزشي در رابطه با ايرادات مطرح شده در ارزيابي وانو براي کارکنان روزکار و کارکنان نوبت کار در نظر گرفته شود و کليه کارکنان در اين رابطه توجيه شوند. | Chemistry manager | 2016-03-10 | SAT | 5.9
5CY.1-1 | 5 | CY.1-1 | 5.11 | Submission of request for complementary training in the area of chemistry and also determining the training subjects. | ارسال درخواست آموزش تکميلي در حوزه شيمي با تعيين موضوعات مورد آموزش | Chemistry manager | 2015-12-11 | SAT | 5.1
5CY.1-1 | 5 | CY.1-1 | 5.12 | Performing complementary training based on the requirements for chemistry staff with cooperation of chemistry management. | اجراي آموزش تکميلي بر اساس موارد درخواست شده براي کارکنان مديريت شيمي با همکاري مديريت شيمي | Head of Human resources and training center | 2016-09-10 | SAT | 5.11
5CY.1-1 | 5 | CY.1-1 | 5.13 | Preparing the briefing plan as for updating laboratory equipment and approving and enacting it in BNPP. | تهيه طرح توجيهي در رابطه با بروز رساني تجهيزات آزمايشگاه و تاييد و تصويب در نيروگاه | Chemistry manager | 2015-11-11 | AI | 5.12
5CY.1-1 | 5 | CY.1-1 | 5.14 | Submission of list of necessary equipment to logistic support management based on the plan which has already been briefed and approved. | ارسال فهرست تجهيزات مورد نياز به معاونت پشتيباني بر اساس طرح توجيهي مصوب | Chemistry manager | 2015-11-16 | AI | 5.13
5CY.1-1 | 5 | CY.1-1 | 5.15 | Provision of equipment necessary for chemistry laboratory based on the required. | تامين تجهيزات مورد نياز آزمايشگاه شيمي طبق درخواست | Commercial and equipment manager | 2016-09-10 | AI | 5.14
5CY.1-1 | 5 | CY.1-1 | 5.16 | Developing explanatory note and approval of chemistry manager and installation in the related locations (laboratories). | تهيه يادداشت هاي توضيحي (Памятка) و تاييد مديريت شيمي و نصب در محل هاي مورد نظر (آزمايشگاه ها) | Chemistry manager | 2016-03-10 | SAT | 5.15
5CY.1-1 | 5 | CY.1-1 | 5.17 | Provision of power switch and plug of laboratory hood in building ZC, room CO-844 with coordination with (power section) and was included in execution list. CY-01-SA-01 | تامین کلید و پریز برق هود آزمایشگاهی در ساختمان ZC اتاق 844 - C0 با آقای مهندس حیدری بخش برق جهت انجام, هماهنگی گردید و در لیست اقدام قرار گرفت. CY-01-SA-01 | Chemistry manager / Electricity manager | 2015-09-21 | SAT | 5.16
5CY.1-1 | 5 | CY.1-1 | 5.18 | Safety label should be installed on all of the laboratory dishes. CY-01-SA-02 | بر روي کليه ظروف آزمايشگاه بر چسب ايمني مناسب نصب گردد CY-01-SA-02 | Chemistry manager | implemeted | SAT | 5.17
5CY.1-1 | 5 | CY.1-1 | 5.19 | The container of distilled water in ZC analysis laboratory was labeled.. CY-01-SA-03 | عدم نصب برچسب نام محتوی ظرف آب مقطر در آزمایشگاه تجزیه zc ، با تامین برچسب انجام شد. CY-01-SA-03 | Chemistry manager | Implemented | SAT | 5.18
5CY.1-1 | 5 | CY.1-1 | 5.2 | Registering the expiry date of chemical materials on chemical packages . CY-01-SA-04 | درج تاريخ اعتبار (تاريخ مصرف) مواد شيميايي بر روي بسته هاي مواد شيميايي CY-01-SA-04 | Chemistry manager | Permanently | SAT | 5.19
5CY.1-1 | 5 | CY.1-1 | 5.21 | Procedure of determining the validity date of chemical materials was developed and approval of procedure. CY-01-SA-05. CY-01-SA-06 | دستورالعمل تعیین تاریخ اعتبار مصرف مواد شیمیایی تدوین شد و پي گيري تاييد و تصوب دستورالعمل. CY-01-SA-05 | Chemistry manager | 2015-12-21 | SAT | 5.2
R.6
|  |  | 6.1 | AFI EP.2-1 Corrective Measures - Corrective Measures in the Field of Emergency Planning | اقدامات اصلاحی AFI EР.2-1 | Responsible Entity Manager of emergency planning | Deadline |  | R.6
6EP.2-1 | 6 | EP.2-1 | 6.2 | Issuing notification by the managing director for the responsible entity for severe accident management SAM in BNPP. | صدور ابلاغيه از طرف مدير عامل در رابطه با متولي حوزه مديريت حوادث شديد در نيروگاه | managing director/ Manager of management system and supervision | 2016-02-04 | SAT | 6.1
6EP.2-1 | 6 | EP.2-1 | 6.3 | Preparing a plan for establishing SAM system with cooperation of the contractor and in accordance with technical support contract with contractor. | تهيه پلان استقرار سيستم مديريت حوادث شديد با همکاري پيمانکار و بر اساس قرارداد پشتيباني فني با پيمانکار | Manager of management system and supervision / Deputy for engineering and technical support | 2016-05-19 | AI | 6.2
6EP.2-1 | 6 | EP.2-1 | 6.4 | Pursuing the provision of equipment related to SAM and emergency planning according to the plan which has already been approved by NPPD. | پي گيري تامين تجهيزات مربوط به مديريت حوادث شديد و برنامه ريزي اضطراري طبق پلان مصوب توسط شرکت توليد و توسعه | Deputy for engineering and technical support | 2016-05-19 | AI | 6.3
6EP.2-1 | 6 | EP.2-1 | 6.5 | Pursuing the design and modernization necessary for using the provided equipment. | پي گيري طراحي و مدرنيزاسيون لازم جهت استفاده از تجهيزات تامين شده | Deputy for engineering and technical support | 2016-06-19 | AI | 6.4
6EP.2-1 | 6 | EP.2-1 | 6.6 | Pursuing the preparation of operation procedures, repairs and technical services for the equipment provided by NPPD. | پي گيري تهيه دستورالعمل هاي بهره برداري، تعميرات و سرويس هاي فني از تجهيزات تامين شده توسط توليد و توسعه | Deputy for engineering and technical support | 2016-08-20 | AI | 6.5
6EP.2-1 | 6 | EP.2-1 | 6.7 | Determining the responsible entities and owners of the equipment provided for mergency situations to be kept in ready-to-work mode. | تعيين متوليان و صاحبان تجهيزات تامين شده شرايط اضطراري جهت نگهداري در شرايط آماده بکار | Deputy for Safety / managing director | 2016-07-20 | SAT | 6.6
6EP.2-1 | 6 | EP.2-1 |  | Preparing the requirements of reliable information system in emergnency. | تهيه الزامات سيستم ارتباطي مطمئن در شرايط اضطراري | ICT manager | 2016-03-10 | FAR | 6.7
6EP.2-1 | 6 | EP.2-1 | 6.8 |  |  | Deputy for Safety / Managing director |  | FAR
6EP.2-1 | 6 | EP.2-1 | 6.9 | Pursuing and inquiring from nuclear protection and security office for permit and provision of reliable communication system in emergency. | پي گيري از دفتر امنيت و حفاظت هسته اي در رابطه با مجوز و امکان تامين سيستم ارتباطي مطمئن در شرايط اضطراري | ICT manager, Managing director | 2016-06-09 | FAR | 6.8
6EP.2-1 | 6 | EP.2-1 | 6.1 | Pursuing for preparing and establishing reliable communication system during accident. | تهيه و برقراري سيستم مطمئن اطلاع رساني در زمان حادثه | ICT manager | 2016-03-10 | FAR | 6.9
6EP.2-1 | 6 | EP.2-1 |  | Preparing the plan of performing emergency drills especial for operational teams. | تهيه برنامه و پلان انجام مانورهاي عمليات اضطراري مخصوص تيم هاي عملياتي | Deputy for M&R / M&R manager / TAPNA company | 2016-02-09 | SAT | 6.1
6EP.2-1 | 6 | EP.2-1 | 6.11 |  |  | Manager of emergency planning |  | SAT
6EP.2-1 | 6 | EP.2-1 |  | Designating the training subjects of specialized teams of emergency operation. | تعيين موضوعات آموزشي تيم‌هاي تخصصي عمليات اضطراري | M&R manager, TAPNA company, | 2016-10-21 | AI | 6.11
6EP.2-1 | 6 | EP.2-1 |  |  |  | Manager of emergency planning, Head of Human resources and Training center |  | AI
6EP.2-1 | 6 | EP.2-1 | 6.12 |  |  | Head of Training and human resources center |  | AI
6EP.2-1 | 6 | EP.2-1 |  | Organizing and executing the training of specialized teams of emergency operation. | سازماندهي و اجراي آموزش تيم‌هاي تخصصي عمليات اضطراري | M&R manager, TAPNA company, | 2016-11-20 | AI | 6.12
6EP.2-1 | 6 | EP.2-1 |  |  |  | Manager of emergency planning |  | AI
6EP.2-1 | 6 | EP.2-1 | 6.13 |  |  | Head of Training and human resources center |  | AI
6EP.2-1 | 6 | EP.2-1 | 6.14 | Revising the list of emergency equipment necessary in emergency and familiarity of personnel about how to use them. | بازنگري ليست تجهيزات اضطراري مورد نياز در شرايط حادثه و آشنايي افراد با نحوه‌ي استفاده از آن‌ها | Deputy for M&R | 2016-03-10 | AI | 6.13
6EP.2-1 | 6 | EP.2-1 | 6.15 | Preparing the graph of inspection and technical service and checking the availability of equipment and instruments related to emergency operations teams. | تهيه‌ي گراف بازرسي و سرويس فني و کنترل آماده بکار بودن تجهيزات و ابزار آلات مربوط به تيم هاي عمليات اضطراري | Deputy for M&R | 2016-05-09 | SAT | 6.14
6EP.2-1 | 6 | EP.2-1 | 6.16 | Inspecting Plan | تهيه برنامه بازرسي خارج از برنامه جامع از حوزه مديريت شرايط اضطراري | Manager of management system and supervision | 2016-03-20 | AI | 6.15
R.7
|  |  | 7.1 | AFI PI.2-1 Corrective measure - Corrective measures in the field of Performance Improvement | اقدامات اصلاحی AFI РI.2-1 | Responsible entity Head of Operating Experiences Group | Deadline |  | R.7
7PI.2-1 | 7 | PI.2-1 |  | Developing a complete software and the database to register all the domestic and foreign events and corrective measures. | پی­گیری اجرای توافقات صورت پذیرفته با شرکت توانا در زمینه تهیه نرم افزار جامع به منظور ثبت تمامی حوادث داخلی، خارجی و بانک اقدامات اصلاحی تا حصول نتیجه. | Manager of management system and supervision | 2016-12-21 | AI | 7.1
7PI.2-1 | 7 | PI.2-1 | 7.2 |  |  | ICT manager |  | AI
7PI.2-1 | 7 | PI.2-1 | 7.3 | Developing procedure for assessing corrective measures of reports of accident investigation. | تدوین دستورالعمل ارزیابی اثر بخشی اقدامات اصلاحی گزارش­های بررسی حوادث. | Manager of management system and supervision / (Head of Operating experiences group) | 2015-09-21 | SAT | 7.2
7PI.2-1 | 7 | PI.2-1 | 7.4 | Pursuing specialized training in the field of methods of investigating the accidents, the causes of accidents (direct and root cause) and training the correct method of developing and preparing reports of accident investigation for operation experiences group and the group for supervising the equipment and operation of management of supervision and management system and human resources and training center. | پی­گیری انجام آموزش تخصصی در زمینه متدهای بررسی حوادث، دلایل بروز حوادث (مستقیم و ریشه­ای) و آموزش شیوه صحیح تهیه و تدوین گزارش­های بررسی حوادث برای گروه تجارب بهره­برداری و گروه نظارت بر تجهیزات و بهره­برداری مدیریت سیستم مدیریت و نظارت و مرکز آموزش و منابع انساني. | Manager of management system and supervision / Head of Human resources and training center | 2016-03-11 | FAR | 7.3
7PI.2-1 | 7 | PI.2-1 |  | Analyzing the trending of near misses every 6 months. | انجام آنالیز روندیابی رویدادهای بخیر گذشته هر 6 ماه یک بار. | Manager of management system and supervision / Head of Operating experiences group | From October 13, 2015 | SAT | 7.4
7PI.2-1 | 7 | PI.2-1 | 7.5 |  |  |  | Permanently | SAT
7PI.2-1 | 7 | PI.2-1 | 7.6 | The proposed corrective measures and conclusion at the end of every self-assessment report and annual report was provided. | درج اقدامات اصلاحی پیشنهادی و نتيجه گيري در انتهای هر گزارش خود ارزیابی تهیه شده. | Manager of management system and supervision / Head of Operating experiences group | Permanently | SAT | 7.5
7PI.2-1 | 7 | PI.2-1 | 7.7 | Developing procedure in the field of methods of analyzing and trending the reports of accident investigation ( Accidents, deviations, low level events, near miss) in NPP and also mentioning the details, format of report and how to develop it). | تدوین دستورالعملی در زمینه آموزش روشهاي تهیه، آنالیز و روندیابی گزارش­های بررسی حوادث (اختلال، انحراف، کم­پیامد، بخیر گذشته) در نیروگاه با ذکر جزئیات، فرمت گزارش و چگونگی تدوین آن. | Manager of management system and supervision / Head of Operating experiences group | 2016-02-04 | SAT | 7.6
7PI.2-1 | 7 | PI.2-1 | 7.8 | Making it possible to use psychological services in the committee of accidents investigation ( in all the cases which human error is the main cause of the accident) | فراهم نمودن امکان بکارگیری خدمات روانشناسی در کمیته بررسی حوادث (در تمامی مواردی که خطای انسانی عامل اصلی بروز حادثه می­باشد). | Head of Human resources and training center | Permanently | AI | 7.7
7PI.2-1 | 7 | PI.2-1 | 7.9 | In case of need to extend corrective measures of accident investigation reports in NPP in accordance with the procedure of accident investigation report in NPP (ATEX 863), submitting the causes of extending the time of performing corrective measures along with the approval of chief engineer of NPP one day before deadline for doing it for Operating experiences group. | در صورت نیاز به تمدید اقدامات اصلاحی گزارش­های بررسی حوادث در کار نیروگاه، مطابق با دستورالعمل بررسی حوادث در نیروگاه (ATEX 863)، ارسال دلایل تمدید مدت زمان انجام اقدام اصلاحی به همراه تایید سرمهندس محترم نیروگاه، یک روز پیش از موعد سررسید انجام آن برای تجارب بهره­برداری . | Head of Operating experiences group / All of the managements of NPP | December 21, 2015 and Permanently control | AI | 7.8
7PI.2-1 | 7 | PI.2-1 |  | Making it possible to record the backlog in the software of managing personnel performance by NPP relevant managers. | ايجاد امکان درج موارد انجام نشده در برنامه نرم افزاري مديريت عملکرد کارکنان توسط سيستم مديريت نيروگاه | Head of Human resources and training center / ICT management | 2016-01-21 | SAT | 7.9
7PI.2-1 | 7 | PI.2-1 | 7.1 | Performing corrective measures of accident investigation report (disruption, deviation, low level) which were not performed in due time or need time extension for different causes but nothing has been done for them yet . | انجام اقدامات اصلاحی گزارش­های بررسی حوادث (اختلال، انحراف، کم­پیامد) که در موعد تعیین شده در گزارش به انجام نرسیده­اند و یا به علل مختلف نیاز به تمدید داشته ولی تا کنون اقدامی در ازای آن صورت نپذیرفته است | Managers specified in the report | 2015-07-23 | AI
7PI.2-1 | 7 | PI.2-1 | 7.11 |  |  | Manager of management system and supervision (Head of Operating experiences group) | Q1 2016 | SAT | 7.1
7PI.2-1 | 7 | PI.2-1 | 7.12 | [5 empty] | 7.11
R.8
|  |  | 8.1 | AFI RP.3-1 Corrective measure - Corrective measures in the field of Radiation Safety | اقدامات اصلاحی AFI RР.3-1 | Responsible entity Radiation safety manager | Deadline |  | R.8
8RP.3-1 | 8 | RP.3-1 | 8.2 | Repair and necessary setting of КИД installed on the rooms and also preparing the chart of technical service and checking their efficiency. | تعمير و انجام تنظيمات لازم بر روي КИД هاي نصب شده بر روي اتاقها و همچنين تهیه گراف سرويس فني و سرکشی كارآیی آنها | Ventilation manager | July 20, 2016 and periodically according to the graff | SAT | 8.1
8RP.3-1 | 8 | RP.3-1 | 8.3 | Preparing the checklist of visits of inspectors and radiation safety dosimeters and taking into account the monitoring of КИД hatches. In case of defect, informing the ventilation management and registering in operation logbook of radiation safety shift. | تهيه چک ليست بازديد اپراتورها و دزيمترهاي ايمني پرتوي و لحاظ نمودن کنترل وضعيت دريچه هاي КИД . در صورت خرابي اطلاع به مديريت چيلر و تهويه و ثبت در دفتر اپراتوري شيفت ايمني پرتوي | Radiation safety manager | 2015-09-21 | SAT | 8.2
8RP.3-1 | 8 | RP.3-1 | 8.4 | Inspecting the direction of air in locations and correcting cases in which the direction of air is from contaminated area to clean area. In order to prevent dissemination of radioactive material to cleaner areas, ventilation management should always take measures so that air direction would always be from radiation contaminated area to more contaminated area. | بررسي جهت حرکت هوا در محل ها و اتاق ها و اصلاح مواردي که جهت حرکت هوا از منطقه آلوده به منطقه تميز مي باشد. مدير چيلر و تهويه مي بايست همواره جهت جلوگيري از انتشار مواد راديواكتيو به مناطق تميزتر ، تدابيري اتخاذ نمايد تا جهت جريان هوا همواره از منطقه آلوده پرتوی به منطقه آلوده تر باشد؛ | Ventilation manager | 2016-03-05 | SAT | 8.3
8RP.3-1 | 8 | RP.3-1 | 8.5 | Considering the direction of air movement in the checklist of dosimeter visits and staff of radiation safety management. In case of movement of air vice versa , the shifts should be informed and it should be recorded in the operation logbook of radiation safety shift. | لحاظ نمودن بررسي جهت حرکت هوا در چک ليست بازديد دزيمترها و کارکنان مديريت ايمني پرتوي. در صورت مشاهده جهت حرکت هوا به صورت برعکس به شيفت تهويه اطلاع رساني گردد و در دفتر اپراتوري شيفت ايمني پرتوي درج گردد. | Radiation safety manager | Permanently | SAT | 8.4
8RP.3-1 | 8 | RP.3-1 | 8.6 | Briefing all the personnel about how to use СИЗ properly in controlled access area also taking necessary for using safety helmet in controlled access area and marking the necessary tools in controlled access area measures in order to prevent them from being removed from controlled access area. | توجيه كليه کارکنان در مورد استفاده صحيح از СИЗ در منطقه تحت كنترل و همچنين ارائه تدابیر لازم جهت استفاده از كلاه ايمني توسط كليه كاركنان در ناحيه تحت كنترل و علامت گذاری وسایل مورد استفاده در ناحیه تحت کنترل برای جلوگیری از خروج آنها از این ناحیه. | Radiation safety manager / Occupational health and industrial safety manager / All BNPP managers | 2015-08-22 | SAT | 8.5
8RP.3-1 | 8 | RP.3-1 | 8.7 | Marking and coding all the repair tools used in the radiation controlled access area. | علامت گذاري و کد گذاری كليه ابزارآلات تعميراتي مورد استفاده در ناحيه تحت كنترل پرتوی | TAPNA company | 2015-09-21 | SAT | 8.6
8RP.3-1 | 8 | RP.3-1 | 8.8 | Optimizing the process of radiation monitoring of personnel and tools in in the exits of controlled access area and also equipping the radiation monitoring machines РЗБ-04-04 to entrance door in order to prevent the unauthorized exit of people and installing a set of UIM2-21 with its guidebook in the room 1ZC-09.22 in order to measure the arms and sides of people and also safety helmet. | بهينه سازي فرآيند كنترل پرتوي افراد و وسايل در خروجي هاي ناحيه تحت كنترل و همچنين تجهيز دستگاههاي كنترل پرتوي РЗБ-04-04 به درب ورودي جهت جلوگيري از خروج غير مجاز افراد و نصب يك دستگاه UIM2-2I به همراه راهنماي استفاده از آن در اتاق 1ZC-09.22 جهت اندازه گيري بازوها و پهلوی افراد و همچنین كلاه هاي ايمني | Radiation safety manager | 2016-03-10 | AI | 8.7
8RP.3-1 | 8 | RP.3-1 |  | Providing and installing the reserve sensor of radiation measurement of exit door of NPP , | تامين و نصب سنسور رزرو اندازه گيري پرتوي در خروجي از نيروگاه | Radiation safety manager | Done | SAT | 8.8
8RP.3-1 | 8 | RP.3-1 | 8.9 | Installing the monitor which shows theses sensors are sound. | نصب نمايشگر سالم بودن سنسورهاي اندازه گيري پرتوي در خروجي نيروگاه |  |  | SAT
8RP.3-1 | 8 | RP.3-1 | 8.10 | Briefing the personnel about the monitoring radiation monitoring sensors in the exit of NPP | توجيه كاركنان در رابطه با كنترل وضعيت سنسورهاي كنرل پرتوي در خروجي نيروگاه | Radiation safety manager | Done | SAT | 8.9
8RP.3-1 | 8 | RP.3-1 | 8.11 | Removing the defect of sensors which measure the radiation in exit door | رفع خرابي سنسورهاي اندازه گيري پرتوي درب خروجي | Radiation safety manager | Done | SAT | 8.10
8RP.3-1 | 8 | RP.3-1 | 8.12 | Sending letter to NPPD about the necessity of optimization (updating) the radiation contamination monitoring machines in the exit of controlled access area. In this letter, the suggestions of BNPP about removing the problems were also submitted to NPPD. | ارسال نامه به شركت توليد و توسعه مبني بر لزوم بهينه سازي (بروز رساني) دستگاه هاي كنترل آلودگي پرتوي در خروجي ناحيه تحت كنترل. در نامه مذكور پيشنهادات نيروگاه نيز براي رفع مورد به شركت توليد و توسعه ارائه گردد. | Radiation safety manager | 2015-09-21 | AI | 8.11
8RP.3-1 | 8 | RP.3-1 | 8.13 | Preparing report from current status of radiation monitoring equipment existing in the system and equipment and sending to NPPD in order to [pursue the removal of defects. | تهيه گزارش از وضعيت كنوني تجهيزات كنترل پرتوي و ايرادات موجود در سيستم و تجهيزات و ارسال به شركت توليد و توسعه جهت پي گيري رفع ايرادات | Radiation safety manager | 2015-09-21 | SAT | 8.12
8RP.3-1 | 8 | RP.3-1 | 8.14 | Registering the equipment and spare parts necessary in the area of radiation safety from equipment and commercial management. | ثبت تجهيزات و قطعات يدكي مورد نياز در حوزه ايمني پرتوي از مديريت بازرگاني و تجهيزات | Radiation safety manager | 2015-09-21 | SAT | 8.13
8RP.3-1 | 8 | RP.3-1 | 8.15 | Providing the necessary spare parts and equipment in the area of radiation safety , submission of report of provision condition in a monthly basis to safety division and chief engineer of NPP about the provision of necessary equipment and spare parts. | تامين تجهيزات و قطعات يدكي مورد نياز در حوزه ايمني پرتوي. ارسال گزارش وضعيت تامين بصورت ماهانه به معاونت ايمني و سرمهندس نيروگاه در مورد وضعيت تامين تجهيزات و قطعات يدكي مورد نياز | Commercial and equipment manager | February 19, 2016 unitl the time of provision | FAR | 8.14
8RP.3-1 | 8 | RP.3-1 | 8.16 | Briefing all the staff about how to use СИЗ properly , providing necessary measures for using the safety helmet by all the staff and making the tools which are used in the accidents. | توجيه كليه کارکنان در مورد استفاده صحيح از СИЗ و همچنين ارائه تدابیر لازم جهت استفاده از كلاه ايمني توسط كليه كاركنان و علامت گذاری وسایل مورد استفاده در زمان حادثه | Environmental monitoring laboratory manager | 2015-10-22 | SAT | 8.15
8RP.3-1 | 8 | RP.3-1 | 8.17 | Revising the training documents, time of training and reviewing the effectiveness of training in the area of radiation safety. | بازنگري مدارك آموزشي، زمان آموزش و بررسي موثر بودن آموزش در حوزه ايمني پرتوي | Head of Human resources and training center | 2016-06-19 | AI | 8.16
8RP.3-1 | 8 | RP.3-1 | 8.18 | Briefing the managers and deputy managers in the area of radiation safety examinations. | توجيه مديريت ها و معاونين در حوزه آزمون هاي ايمني پرتوي | Manager of management system and supervision | 2015-11-21 | SAT | 8.17
8RP.3-1 | 8 | RP.3-1 | 8.19 | Monitoring more the information in the field of radiation safety especially for staff who have toing and froing to controlled access area. | كنترل بيشتر وضعيت اطلاعات در زمينه ايمني پرتوي خصوصا براي كاركناني كه به ناحيه تحت كنترل تردد دارند | Head of Human resources and training center / Training committees | Permanently | AI | 8.18
8RP.3-1 | 8 | RP.3-1 | 8.20 | Requesting and receiving the spare parts which are used more in the area of repairing the equipment of radiation monitoring and minimum maintenance in locations in order to repair the equipment in less time duration. | درخواست و دريافت قطعات يدكي كه در حوزه تعميرات تجهيزات كنترل پرتوي بيشتر استفاده مي گردد و نگهداري حداقلي در محل هاي كاري به منظور تعمير تجهيزات در زمان كمتر | Radiation safety manager | 2016-05-19 | SAT | 8.19
8RP.3-1 | 8 | RP.3-1 | 8.21 | Preparing the requirements traning Sending letter to Manager of human resources and training center. | تهيه الزام در رابطه با برنامه حفظ صلاحيت كاركنان در سال 95 و ارسال به مركز آموزش | Radiation safety manager | 2016-01-20 | SAT | 8.20
8RP.3-1 | 8 | RP.3-1 | 8.3 | Taking into account the radiation safety in the order issued by the manager of NPP in the area of program of staff competence. | لحاظ نمودن الزامات ايمني پرتوي در دستور صادره از طرف رياست نيروگاه در حوزه برنامه حفظ صلاحيت كاركنان | Head of Human resources and training center | 2016-03-19 | SAT | 8.21
R.
|  |  | 8.22 | AFI RP.4-1 Corrective measure - Corrective measures in the field of Radiation Safety | اقدامات اصلاحی AFI RР.4-1 | Responsible entity Radiation safety manager | Deadline |  | R.
8RP.4-1 | 8 | RP.4-1 | 8.23 | Determining the location and suitable equipment of temporary sanitary path in Control Access Area of NPP in a way that it would be possible to separate clean and contaminated СИЗ with complete guide about how to use radiation contamination monitoring machine and two containers for clean and contaminated tools. | تعیین محل و تجهیز مناسب گذرگاه­های بهداشتی موقت در ناحیه تحت کنترل نیروگاه بطوری که امکان تفکیک СИЗ آلوده و تمیز وجود داشته باشد با راهنمای کامل استفاده از دستگاه کنترل آلودگی پرتوی و و دو عدد کانتینر برای وسایل تمیز و آلوده؛ | Radiation safety manager / Waste treatment workshop manager | 2016-03-19 | SAT | 8.22
8RP.4-1 | 8 | RP.4-1 | 8.24 | Provision of rubbish bags in different colors for clean and contaminated wastes and preparing a guidebook how to use them and also briefing the staff as for separation of wastes and decreasing solid waste. | تامین کیسه های زباله با رنگ هاي مختلف برای پسماندهای تمیز و آلوده و تهیه راهنمای استفاده از آنها با توجیه کلیه کارکنان در این خصوص در جهت تفکیک پسماندها و کاهش پسماندهای جامد | Waste treatment workshop manager / All of managers | 2015-08-22 | SAT | 8.23
8RP.4-1 | 8 | RP.4-1 | 8.25 | Installing contamination monitoring machine in the exit of ZA in order to separate clean and contaminated СИЗ in the exit of reactor building in order to decrease solid waste. | نصب دستگاه کنترل آلودگی در خروجی ZA برای تفکیک СИЗ آلوده و تمیز هنگام خروج از ساختمان راکتور در جهت کاهش پسماندهای جامد | Radiation safety manager | 2015-08-22 | SAT | 8.24
8RP.4-1 | 8 | RP.4-1 |  | Determining the responsible entity for collecting the wastes in control access area and determining a clear procedure for collecting wastes in a way that no waste would be abandoned uncontrolled in the control access area. | مشخص کردن متولی جمع­آوری پسماندها در ناحیه تحت کنترل و تعیین رویه مشخص برای جمع­آوری پسماندها بطوریکه هیچ­گونه پسماندی در ناحیه تحت کنترل بدون کنترل رها نشده باشند | Radiation safety manager, | 2016-02-19 | SAT | 8.25
8RP.4-1 | 8 | RP.4-1 | 8.26 |  |  | Waste treatment workshop manager |  | SAT
8RP.4-1 | 8 | RP.4-1 | 8.27 | Checking the condition of radiation safety labels in control access area and removing the defects related to radiation safety labels. | بررسي وضعيت برچسب هاي ايمني پرتوي در ناحيه تحت كنترل و رفع ايرادات مربوط به برچسب هاي ايمني پرتوي | Radiation safety manager | 2016-01-20 | SAT | 8.26
8RP.4-1 | 8 | RP.4-1 |  | Preparing a manual about separating radioactive and non-radioactive wastes from wastes with different reactivity. | تهيه راهنما در زمينه تفكيك پسماندهاي اكتيو و غيراكتيو يا پسماندهاي با اكتيويته متفاوت | Waste treatment workshop manager | 2016-02-19 | SAT | 8.27
8RP.4-1 | 8 | RP.4-1 | 8.28 |  |  | Radiation safety manager |  | SAT
8RP.4-1 | 8 | RP.4-1 | 8.29 | Preparing order for the location for collection rubbish and waste in control access area and receiving the approval of safety deputy and notification of chief engineer. | تهيه دستور در زمينه محل جمع آوري زباله ها و پسماندها در منطقه تحت كنترل و دريافت تاييد معاونت ايمني و ابلاغ سرمهندس نيروگاه | Waste treatment workshop manager / Radiation safety manager | 2016-02-14 | SAT | 8.28
8RP.4-1 | 8 | RP.4-1 |  | Organizing the place of collecting according to the notification of chief engineer. | سازماندهي محل هاي جمع آوري طبق ابلاغ سرمهندس نيروگاه | Waste treatment workshop manager | 2016-02-19 | SAT | 8.29
R.9
|  |  | 9.1 | AFI HU.1-1 Corrective measures - Corrective measures in the field of Human Resources and Training | اقدامات اصلاحی AFI HU.1-1 | Responsible entity Head of Human resources and Training center | Deadline |  | R.9
9HU.1-1 | 9 | HU.1-1 | 9.2 | Preparing and submitting the draft of project called “prevention of incorrect performance of the staff” for independent deputies and managers. | تهیه و ارسال پیش نویس طرح "جلوگیری از عملکرد نادرست کارکنان " برای معاونین و مدیران مستقل | Head of Human resources and training center | 2016-01-10 | SAT | 9.1
9HU.1-1 | 9 | HU.1-1 | 9.3 | Reviewing the draft of project and evaluating the activities and submitting the viewpoints related to this project (9.1) on each area. | بررسی طرح و ارزیابی فعالیتها و ارایه نقطه نظرات مرتبط با حوزه های سازماندهی فعالیتهای بهره برداری ، تعمیرات و نگهداری ، ایمنی ، شرایط کار و نحوه کنترل و نظارت به سيستم مديريت و نظارت | All deputies and All Independent managers | 2016-02-10 | SAT | 9.2
9HU.1-1 | 9 | HU.1-1 | 9.4 | Reviewing the project, evaluating the activities and submitting the viewpoints related to services compensation, payment and welfare affairs to human resources and training center. | بررسی طرح و ارزیابی فعالیتها و ارایه نقطه نظرات مرتبط با حوزه های جبران خدمات ، دستمزد و امور رفاهی به مرکز منابع انسانی و آموزش | Deputy for support and development | 2016-02-10 | SAT | 9.3
9HU.1-1 | 9 | HU.1-1 | 9.5 | Reviewing and summing up the viewpoints of deputies and managers. | بررسی و جمع بندی نقطه نظرات معاونت ها و مدیریتها | Head of Human resources and training center / Manager of management system and supervision | 2016-02-20 | SAT | 9.4
9HU.1-1 | 9 | HU.1-1 | 9.6 | Finalizing the order of the project “ prevention from the incorrect performance of staff”. | نهایی کردن ابلاغیه طرح "جلو گیری از عملکرد نادرست کارکنان " | Head of Human resources and training center / Manager of management system and supervision | 2016-03-10 | AI | 9.5
9HU.1-1 | 9 | HU.1-1 | 9.7 | Preparing and notifying the guide paper of managers in order to prevent the wrong performance of the staff. | تهیه و ابلاغ برگ راهنمای مدیران برای جلو گیری از عملکرد اشتباه کارکنان | Head of Human resources and training center | 2016-01-10 | SAT | 9.6
9HU.1-1 | 9 | HU.1-1 | 9.8 | Preparing and notifying the guide paper of staff in order to prevent the wrong performance of the staff. | تهیه و ابلاغ برگ راهنمای کارکنان برای جلو گیری از عملکرد اشتباه کارکنان | Head of Human resources and training center | 2016-01-10 | SAT | 9.7
9HU.1-1 | 9 | HU.1-1 | 9.9 | Preparing training material for preventing the wrong performance of staff. | تهیه متون آموزشی جلو گیری از عملکرد اشتباه کارکنان | Head of Human resources and training center | 2016-01-20 | SAT | 9.8
9HU.1-1 | 9 | HU.1-1 | 9.1 | Including the method “prevention from wrong performance of staff” in the standard training program of jobs and executing it. | گنجاندن متد "جلو گیری از عملکرد اشتباه کارکنان" در برنامه آموزشی استاندارد مشاغل و اجراي آن | Head of Human resources and training center / training planning manager | 2016-06-19 | SAT | 9.9
9HU.1-1 | 9 | HU.1-1 | 9.11 | Preparing the procedure “ instruments for decreasing the error of staff”. | تهیه دستورالعمل " ابزارهای کاهش خطای کارکنان " | Head of Human resources and training center | 2016-08-20 | AI | 9.1
9HU.1-1 | 9 | HU.1-1 | 9.12 | Submitting the report of establishing and using the methods of decreasing error to human resources development management. | ارسال گزارش استقرار و استفاده از متدهاي کاهش خطا به مديريت توسعه منابع انساني | All of the executing managers of BNPP | 2016-09-20 | AI | 9.11
9HU.1-1 | 9 | HU.1-1 | 9.13 | Including the supervision on using methods of decreasing error in inspection and supervision programs. | گنجاندن نظارت بر استفاده از متدهاي کاهش خظا در برنامه هاي بازرسي و نظارت | Manager of supervision and management system | 2015-10-21 | FAR | 9.12
9HU.1-1 | 9 | HU.1-1 | 9.14 | Organizing and executing self-assessment in the field of using methods for decreasing error. | سازماندهي و اجراي خودارزيابي در حوزه استفاده از متدهاي کاهش خطا | Head of Human resources and training center | 2016-12-20 | AI | 9.13
R.
|  |  | 9.15 | AFI TR.1-1 Corrective measures - Corrective measures in the field of Human Resources and Training | اقدامات اصلاحی AFI TR.1-1 | Responsible entity Head of Human resources and Training center | Deadline |  | R.
9TR.1-1 | 9 | TR.1-1 |  | List of all the non-complinces of MCR with FSS existing until mid-life repairs ( video-cadres, protection panels and blockings … ) were prepared and the process of modernization will be carried out according to plan. | پي گيري بروز رساني شبيه ساز تمام عيار و رفع كامل مغايرت ها بر اساس قرارداد و توافقات صورت پذيرفته با پيمانكار و ارسال گزارش ماهانه پيشرفت فعاليت ها به رييس نيروگاه | BNPP Construction Project Manager / Operating Company / Human resources and Training center | 2016-09-20 | SAT | 9.15
R0
11SAM | 11 | SAM |  | Самооценка по Руководствам ВАО АЭС • GL 2012-01: Guidelines for Training and Qualification of Emergency Response Organisation Personnel |  | Head of Human resources and Training center / Deputy for safety / Manager of Managing system and supervision | اسفند 1394 | FAR | 11
11SAM | 11 | SAM |  | Целевое наблюдение Представителя ВАО АЭС-МЦ на площадке АЭС |  | Deputy for safety / Head of Human resources and Training center / Manager of Managing system and supervision / WANO OSR | اسفند 1395 | AI
توضیحات: رنگ سبز در ستون وضعیت: اقدام اصلاحی به نحو رضایتبخش انجام شده است. رنگ زرد در ستون وضعیت: اقدام اصلاحی کامل انجام نشده و در حال پیگیری است. رنگ قرمز در ستون وضعیت: اقدام اصلاحی بموقع یا بطور کامل انجام نشده یا نتایج اجرا رضایتبخش نبوده است و نیاز به توجه مجدد دارد. رنگ سفید یا بدون رنگ: موعد انجام اقدام و یا موعد بررسی وضعیت فرا نرسیده است.

## Sheet4
رديف | حوزه | حوزه | عنوان شغلي | نام و نام خانوادگي
1 | Manager of management system and supervision | مديريت و سازماندهي | مدير سيستم مديريت و نظارت | کاظم خضری
2 | Deputy for production | بهره‌برداري | معاون توليد | بهنام فرضی
3 | Deputy for M&R | نگهداري و تعميرات | جانشين معاون نگهداري و تعميرات | عباسعلي روشنكار
4 | Deputy for technical and engineering | پشتيباني فني و مهندسي | معاون فني و مهندسي | ابراهيم ديلمي
5 | Chemistry manager | شيمي | مدير شيمي | ابراهيم مصلي نژاد
6 | Manager of emergency planning | آمادگي اضطراري | مدير برنامه‌ريزي شرايط اضطراري | محمدهادي جعفري
7 | Head of Operating Experiences Group | بهبود عملکرد، تجارب بهره برداري و SOER | مدير سيستم مديريت و نظارت - رييس گروه تجارب بهره برداري | احمد سعدي
8 | Radiation safety manager | ايمني پرتويي | مدير ايمني پرتويي | محمد جعفري
9 | Head of Human resources and Training center | آموزش و منابع انساني | رييس مركز منابع انساني و آموزش | سيامك طالبيان زاده
10 | Deputy for Safety | ایمنی | معاون ایمنی | هدایت عباسپور
11 | SAM management | مدیریت حوادث شدید | معاون فني و مهندسي | ابراهيم ديلمي