### AMP154 WWER Pressurizer (2015)

### Programme Description

The approach used by some operators (e.g. WWER, CANDU) to AMPs development is focused on components (such as RCP, RPV, SG, Pressurizer, etc.) and not on individual degradation mechanisms. These “umbrella type” programmes are based on understanding of all degradation mechanisms relating to the specific component and describing all activities necessary to manage ageing. The main advantage of such an approach is knowledge of the overall state of the components.

This ageing management programme is a component-specific AMP for the pressurizer, that covers multiple degradation mechanisms the pressurizer may be subjected to and the activities necessary to manage the ageing mechanisms. As such, this AMP refers to other degradation-specific and/or monitoring type of AMPs that deal with particular degradation mechanisms and ageing effects.

The pressure boundary of the pressurizer is safety class 1 component therefore it is included in the scope for LTO in accordance with the IAEA Safety Report Series No. 57 [1].

### Evaluation and Technical Basis

- Scope of the ageing management programme based on understanding ageing:

The programme controls ageing of the pressurizers of WWER 440 and WWER 1000 NPPs. The following ageing degradation mechanisms are considered in this AMP:

- fatigue

- general corrosion

- boric acid corrosion

- stress corrosion cracking

- wear

- loss of preload

Examples of critical locations for fatigue of pressurizer are nozzles and the flanged joints.

Examples of critical locations for	general corrosion of pressurizer are the external surfaces and the support structures.

Bolting and support structures used on Pressurizer could be in carbon steel thus boric acid corrosion is a potential degradation mechanism.

Stress corrosion cracking can happen in stagnant localized corrosion susceptible location, e.g. nozzles, collectors, surge-line of Pressurizer.

Degradation due to wear or stress relaxation could be applicable to fitted connections such as bolts, internal parts of Pressurizer.

Degradation due to loss of preload could be applicable to fitted connections such as bolts and keys.

- Preventive actions to minimize and control ageing degradation:

The preventive actions are carried out during normal operation via monitoring and management of water chemistry conditions. These actions could eliminate potential adverse effects of water chemistry on the ageing mechanisms. The programme description, evaluation and technical basis for monitoring and maintaining of reactor coolant chemistry are addressed in IGALL AMP103 “Water Chemistry”.

Other preventive action is regular maintenance according to approved schedule (such as general repair, inspection of sealing screw tightness and inspection program of the hermetic area).

Preventive actions for low cycle fatigue include reduction of transients and keeping limits and conditions.

- Detection of ageing effects:

The pressurizer is inspected and tested according to the requirements of AMP102 “In-service Inspection/Periodic Inspection”. Non-destructive methods such as visual examination, capillary test to detect surface cracks, dimensional control and ultrasonic examination may be used. It is expected that visual, surface or volumetric inspection performed within AMP102 “In-service Inspection/Periodic Inspection” programme will detect cracking due to SCC, fatigue, growth of manufacturing defects, or common wear by inspecting for loose connections or missing parts.

The impact of boric acid leakage on bolting materials is addressed by IGALL AMP 110 “PWR Boric Acid Corrosion.”

The cumulative effect of fatigue is addressed by IGALL AMP101, “Fatigue Monitoring.”

- Monitoring and trending of ageing effects:

Timely and reliable detection of ageing degradation is provided by implementation of inspection and testing schedules in accordance with the referred AMPs in attribute 3, reliable examination methods, and qualified inspection. Monitoring and trending is performed as per the AMPs listed in attribute 3.

- Mitigating ageing effects:

Recommendations for mitigation of ageing effects are based on referred AMPs in attribute 3, and on results from performed analyses of possible degradation developments.

- Acceptance criteria:

Acceptance criteria are part of referred AMPs in attribute 3, and maintenance procedures.  Any indication or relevant conditions of degradation may be evaluated for acceptance in accordance with the governing requirements or guidance documents as for example [2], [3], [4].

- Corrective actions:

In order to satisfy the safety requirements, further evaluation to demonstrate fitness-for-service of the component until the end of the next periodic inspection interval may be required. Examination results and flaws that exceed the acceptance criteria given in the governing requirements or guidance documents may require activities such as repair or replacement.

For each acceptance criterion which is not satisfied, the procedure for resolution is defined or elaborated and consequently implemented, according to the referred AMPs in attribute 3. At the end of the process the criterion is fulfilled and the requested state of the component is restored. Repair and replacement according to requirement of technical documentation of the components and according to guiding documents of the plant are part of possible corrective actions.

When suitable in some cases, changes of operational regimes could be applied.

- Operating experience feedback and feedback of research and development results:

The values of ageing management parameters and corresponding analysis (in case that they were performed) are evaluated according to the referred AMPs in attribute 3.

The operational history of the component should be analyzed once per inspection or test cycle according to the member states practice. There should be a system in place to incorporate feedback from internal and external operating experiences.

Research and development efforts and an effective experience exchange are important elements for implementing continuous improvement in this program and in defining adequate corrective actions.

- Quality management:

The AMP is carried out in agreement with site QA procedures, review and approval processes, and administrative controls, which are implemented in accordance with the different national regulatory requirements for example [5]-[6], or the different national standards, and regulatory requirements [7].

- Requirements

Pressurizer Pre-Service Inspection (PSI) and In-Service Inspection should be performed by the same instruments, devices, tools, methods and experts as possible as to reduce probability of extra error occurrences.

The inspector and specialists who performs these inspections should be qualified by international or national legal organization. Qualification process should contain necessary education, work experience and other abilities.

### References

- INTERNATIONAL ATOMIC ENERGY AGENCY, Safe long term operation of nuclear power plants, Safety Report Series No. 57, IAEA, Vienna, 2008.

- Unified Procedure for Lifetime Assessment of Components and Piping in WWER NPPs during Operation, European Commission, COVERS – WP-D4.10, project VERLIFE, 2008.

- NUCLEAR REGULATORY AUTHORITY OF THE SLOVAK REPUBLIC, Aging management of NPP - requirements, National safety guide BNS I.9.2/2014, UJD-SR, 2014.

- STATE OFFICE FOR NUCLEAR SAFETY OF CZECH REPUBLIC, Aging management of NPP, National safety guide BN-JB-2.1, SUJB, 2010.

- STATE OFFICE FOR NUCLEAR SAFETY OF CZECH REPUBLIC, Decree No.132/2008 on Quality Assurance System in carrying out activities connected with utilization of nuclear energy and radiation protection, SUJB, 2008.

- NUCLEAR REGULATORY AUTHORITY OF THE SLOVAK REPUBLIC, Regulation No. 431/2011 on a quality management system, 2011, UJD-SR.

- Hungarian Atomic Energy Agency: Guideline 4.12. Ageing management during the operation of NPPs