MEMORANDUM

Of the WANO-MC International Workshop on the topic: "Station self-assessment in the emergency preparedness and severe accident management", held in Moscow, Russia, WANO-MC, 3-4 March 2015

- Introduction

The workshop was organized by the WANO Moscow Center in March 3-4, 2015 in Moscow.

The workshop was attended by 39 experts from 10 countries:

• Representatives from the operating organizations / NPPs (NPP) from Armenia, Bulgaria, Hungary, India, China, Russia, Slovakia, Ukraine, Finland, Czech Republic.

• Representatives from design and scientific organizations: OKB "Gidropress" and VNIIAES.

The list of participants is presented in Appendix.

The workshop was conducted in Russian and English languages through simultaneous translation.

- The purpose of the workshop

To share experience and knowledge on station self-assessment in the emergency preparedness and severe accident management.

The following topics were addressed:

- • Presentations of the NPPs participants on self-assessment results in the emergency preparedness, including:

- Gaps or areas in need of improvement.

- Good practice.

- Corrective actions.

- Presentations of the NPPs participants on self-assessment results in the severe accident management, including:

- Gaps or areas in need of improvement.

- Good practice.

- Corrective actions.

- WANO-MC presentations – analysis results of the provided station’s self-assessment reports in the emergency preparedness and severe accident management.

- Recommendations for the Memorandum of the Workshop.

- The conduct of workshop

WANO-MC Director Mr. Aksenov addressed the participants in his welcome speech. He stressed the importance of the topic of the workshop and wished all the participants fruitful work.

The following presentations were presented in the workshop:

- Podoprigora Andrey, WANO-MC presentation: “Results of the WANO-MC station self-assessment in the emergency preparedness and severe accident management”

- Naňo Ján, Slovenske Elektrarne Company (Slovakia) presentation.

- Forsberg Kari and Tuomisto Harri, Fortum (Finland) presentation.

- Pashynskyi Valerii,   NAEC "Energoatom" (Ukraine) presentation.

- Endlicher Bohumir and Hončarenko Radim, CEZ company (Czech Republic) presentation.

- Bana János,  MVM Paks NPP (Hungary) presentation.

- Kolevatyh Aleksandr, JSC "Concern Rossenergoatom" (Russia) presentation.

- Kuzmin Sergey, JSC "Concern Rossenergoatom" (Russia) presentation.

- Balakhnin Eugeniy, Beloyarsk NPP, JSC "Concern Rossenergoatom" (Russia) presentation.

- Raspopov Artem, Smolensk NPP, JSC "Concern Rossenergoatom" (Russia) presentation.

- Bezgodov Nikolay, Kursk NPP, JSC "Concern Rossenergoatom" (Russia) presentation.

- Shamambaev Maksim, Balakovo NPP, JSC "Concern Rossenergoatom" (Russia) presentation.

- Wu Jie, WANO-MC and Tianwan Company JNPC (China) presentation.

- Bonov Nikolay Petrov  and Topalov Tsvetan Petkov, Kozloduy NPP (Bulgaria) presentation.

- ARUSTAMYAN Maksim, Armenian NPP (Armenia) presentation.

- PANTYUSHIN Stanislav, OKB "Gidropress" (Russia) presentation.

- Brief information on the workshop:

- The review of the preliminary EP self-assessment reports indicates that the most common issues or weaknesses in EP are as follows:

  - Engineering and maintenance support for the emergency mobile equipment and other emergency equipment.

  - Insufficient staffing of the emergency response organization with qualified personnel, including the possibility of on-call duty during plant emergencies and multi-unit accidents.

  - Not all emergency response personnel possess skills and capabilities needed to implement emergency response functions during prolonged emergencies.

  - The main skills of the emergency responders are not sufficiently practiced during training. Issues related to prolonged events are not sufficiently covered.

  - The constructing and equipping of Emergency Command Centers (including back-up command centers) should be completed to ensure the possibility of using them during multi-unit events.

  - Emergency equipment configuration management programs should be established and implemented.

  - Emergency documentation such as Beyond-Design-Based Accident Management Guideline and Emergency Operating Procedures should be updated; the In-Depth Safety Assessment Report should updated based on the results of design changes; the Probabilistic Safety Assessment should be updated with consideration of severe external events.

- The “weakest” EP criteria which received the most UNSAT ratings are as follows:

  - development of the skills and capabilities of the emergency response personnel for carrying out sustained emergency response duties during prolonged events or severe accidents;

  - expansion of emergency plans, procedures and processes to cover a wide range of events from minor events to severe accidents, including multi-unit accidents;

  - development of alternative methods for performing key response functions that could be precluded by disruptions to infrastructure or to the availability of resources;

  - availability of emergency response facilities and supplies to support continuous, long-term response to a wide range of conditions and events;

  - equipment important to emergency response is identified and managed within station programmes and processes for configuration control, work management and corrective actions to ensure it is available and operable.

- The review of the preliminary SAM self-assessment reports indicates that the most common issues or weaknesses in SAM are as follows:

  - Development and implementation of the SAM Guidelines (SAMGs) have not been completed for all major reactor modes and for spent fuel pools.

  - Documents have not been developed and implemented which would define duties and responsibilities both in using the SAMGs and for the entire SAM program. No criteria have been established for transitions among the emergency procedures.

  - Keeping emergency documentation up to date, including consideration of reports from scientific and research organizations.

  - Initial and continuous training should be provided both for the technical support group personnel and for all personnel involved in SAM.

  - Analytical work has not been completed to evaluate the severe accident phenomenology for spent fuel pools and open reactor vessel.

  - Issues of expanding the SAM strategies after modifications have been implemented at the stations.

  - Station capabilities for simultaneous multi-unit response to severe accidents.

  - Work has not been completed to provide additional independent equipment, containment protection systems and systems for long-term plant status monitoring during severe accidents.

  - Work has not been completed to install permanent interfaces (in addition to temporary connections) for the additional emergency equipment.

  - An engineering evaluation has to be performed for the existing systems and equipment designed for preventing formation of explosive hydrogen-containing mixtures.

  - Work is still to be completed to install accident and post-accident containment sampling systems, containment hydrogen monitoring systems, post-accident monitoring systems capable of operating in beyond-design-basis conditions.

  - The existing monitoring capabilities do not ensure receiving a complete set of critical parameters needed for control and decision-making during severe accidents.

  - The construction of off-site back-up emergency command centers has not been completed.

  - The use of analytical and, if appropriate, full-scope simulators for severe accident training.

- The “weakest” SAM criteria which received the most UNSAT ratings are as follows:

  - The station’s severe accident management program has been developed and is implemented as one of the station’s objectives to enhance safety.

  - The station’s capabilities are sufficient to perform specified SAM functions and responsibilities.

  - Guidelines have been developed to maintain and restore critical safety functions using permanent and portable equipment during the initial response to an extended loss of electrical AC power, without off-site support.

  - The SAM guidelines address beyond-design-basis faults and all possible plant operating states (power operation, shutdown, refueling, etc.) depending on the type of the reactor or nuclear facility

  - At a multi-unit site, there are strategies to deal with beyond-design-basis and severe accidents simultaneously at each unit.

  - Provision is made for obtaining the critical parameters needed for decision making and monitoring during severe accident response.

  - A full-fledged station program or system is established for maintaining SAM role holder competencies including training, periodic drills and exercises to confirm the capability of the groups and personnel involved in SAM and effective interfaces between them.

  - 29.      Desktop and, if appropriate, full-scale simulators are used to assist operators in preparing for severe accidents.

  - Availability and sufficiency of facilities, equipment, I&C systems and resources for SAM; their periodic surveillance and testing.

The information provided in the presentations indicate that the WANO Moscow Region stations are paying considerable attentions to the emergency preparedness and severe accident management issues.

At the closure of the Workshop the participants discussed the presented information and summed up the results.

- CONCLUSIONS AND RECOMMENDATIONS

- The workshop participants have noted the openness demonstrated by the representatives of the utilities/plants from Armenia, Bulgaria, China, the Czech Republic, Finland, Hungary, India, Russia, Slovakia, Ukraine, as well as representatives of design and scientific organizations (Gidropress Design Bureau and the VNIIAES Research Institute), while discussing the SAM and EP self-assessment results.

- The workshop participants recognize that the degree of impartiality in the self-assessment results will inevitably vary among the different plants. Nevertheless, the self-assessment process has on the whole proved to be useful for the stations and helped them identify possibilities for improvement.

- The workshop participants have taken consideration of the information about the station self-assessments in SAM and EP presented at the workshop.

- All the member stations and utilities (except the Kudankulam NPP and Bushehr NPP) have provided the preliminary self-assessment reports in SAM and EP.

- The Kudankulam NPP and the Bushehr NPP shall provide their preliminary SAM and EP self-assessment reports to WANO-MC by 31 March 2015.

- By 15 March 2015, WANO-MC shall send the utilities/stations the results of the review of the self-assessment reports to be incorporated in the final self-assessment reports.

- By 31 March 2015, the following stations shall provide visualizations of the self-assessment results, including the assessment of the EP performance objectives, to WANO-MC:

- Beloyarsk

- Kalinin

- Kola

- Taking consideration of the discussions during the workshop and the results of the review of the preliminary reports by WANO-MC, before 1 May 2015, all the WANO-MC member utilities/stations shall provide the final SAM and EP self-assessment reports, including corrective actions as per the proposed form.

- All the member utilities/stations shall provide their comments and suggestions on the SAM PO&Cs by 1 May 2015.

- CONCLUSION

The participants highly appreciated the results of the workshop. Participants also pointed out the highly qualified translation skills that contributed to the success of the Workshop.

The participants expressed their gratitude to the leadership of the Moscow Center of WANO for its excellent organization and hospitality.

Workshop Coordinator			Andrey Lukyanenko

Appendix

Participants List

Workshop

Station self-assessment in the emergency preparedness and severe accident management

3-4 March 2015, Moscow, Russia WANO-MC

| # | Name | Organization/ Position | e-mail |
| --- | --- | --- | --- |
|  | ENDLICHER Bohumir | CEZ, a. s. – NPP Dukovany Ing./Emergency Preparedness Specialist, Czech Republic | bohumir.endlicher01@cez.cz |
|  | ZAHRADNÍK Pavel | CEZ, a. s. – NPP Temelin Ing./Emergency Preparedness Specialist, Czech Republic | pavel.zahradnik@cez.cz |
|  | HONČARENKO Radim | ČEZ, a.s., Temelin NPP Accident Management Expert, Czech Republic | radim.honcarenko@cez.cz |
|  | FORSBERG Kari | Fortum Nuclear and Thermal / Emergency Planning and Preparedness, Finland | kari.forsberg@fortum.com |
|  | TUOMISTO Harri | Fortum/Senior Nuclear Safety Officer, Finland | harri.tuomisto@fortum.com |
|  | ARUSTAMYAN Maksim | Head of the EP department, Armenian NPP, Armenia | anpp@anpp.am erd@anpp.am |
|  | BEZGODOV Nikolay | Head of the laboratory, Kursk NPP, Russia | bna@kunpp.ru |
|  | MANČÍKOVÁ Mariana | Head of Emergency Preparedness and Environment Protection Dept., SE- ENEL, NPP Mochovce, Slovakia | mariana.mancikova@enel.com |
|  | DANILOV Alexander | Head of the laboratory, Kola NPP, Russia | DanilovAM@kolatom.murmansk.ru |
|  | SMIRNOV Vladimir | Laboratory senior engineer, Kola NPP, Russia | SmirnovVV@kolatom.murmansk.ru |
|  | GOLUBKIN Vladimir | Chief technologist, OJSC Concern Rosenergoatom, Russia |  |
|  | KOLEVATYH Aleksandr | Chief technologist, OJSC Concern Rosenergoatom, Russia | kolevatyh@rosenergoatom.ru |
|  | KUZMIN Sergey | Chief technologist, OJSC Concern Rosenergoatom, Russia |  |
|  | MALYAR Gennadiy | Shift unit supervisor, Smolensk NPP, Russia | BazarevDN@SAES.RU |
|  | RASPOPOV Artem | Reactor operator, Smolensk NPP, Russia | raspopov_av@yahoo.com |
|  | PASHYNSKYI Valerii | Leading engineer, Khmelnitskaya NPP, Ukraine | pashynskyy.valeriy@khnpp.atom.gov.ua |
|  | KOLESOV Sergiy | Director Department, ENERGOATOM Company, Ukraine | s.kolesov@direkcy.atom.gov.ua |
|  | NAŇO Ján | Senior Specialist Research and Development Center Ltd. ENEL , Slovakia | Jan.nano@enel.com |
|  | KUKHAR Sergei | Deputy Department Head, Leningrad NPP, Russia | psa-ksv@laes.ru |
|  | TOPALOV Tsvetan Petkov | Department Head, Kozloduy NPP, Bulgaria | cptopalov@npp.bg |
|  | BONOV Nikolay Petrov | EP Department Head, Kozloduy NPP, Bulgaria | npbonov@npp.bg |
|  | SHAMAMBAEV Maksim | Chief Inspector, Balakovo NPP, Russia | msmaxcore79@rambler.ru |
|  | BERNAT Miroslav | Head of reactor Unit of Slovenske Elektrarne, Slovakia | miroslav.bernat@enel.com |
|  | BANA János | EP Department Head, Paks NPP, Hungary | banaj@t-online.hu |
|  | BALAKHNIN Eugeniy | Deputy Department Head, Beloyarsk NPP, Russia | ojb-zn@belnpp.ru |
|  | SHYTOV Volodymyr | Leading engineer, ENERGOATOM Company, Ukraine | v.shitov@direkcy.atom.gov.ua |
|  | PANTYUSHIN Stanislav | Head of group, OKB Gidropress, Russia |  |
|  | AKSENOV Vasiliy | WANO-MC Director |  |
|  | GALKIN Vasiliy | WANO-MC | galkin@wanomc.ru |
|  | Wu Jie | WANO-MC |  |
|  | PODOPRIGORA Andrey | WANO-MC |  |
|  | LUKYANENKO Andrey | WANO-MC | lukianenko@wanomc.ru |
|  | LOKTIONOV Sergey | WANO-MC |  |
|  | SABIROVA Indira | WANO-MC |  |
|  | LIUDVIKOVSKAYA Viktoria | WANO-MC |  |
|  | GREENEVICH Olga | WANO-MC |  |
|  | KVSBV Prasad | WANO-MC |  |
|  | Kosov Aleхsei | Department Head, VNIIAES, Russia |  |
|  | Orekhov Aleksandr | Engineer, VNIIAES, Russia |  |