TLAA 120	PWR RPV INTERNALS VIBRATIONS

Mechanical vibration of RPV internal parts (RPVI) occur during operation of nuclear reactors. The causes of these vibrations are acoustic and hydrodynamic loading which cause interaction between the cooling water and the reactor internal parts (fluid structure interaction).

The main sources of RPVI vibrations are:

- seismic events,

- design basis accident (e.g. LOCA),

- hydro-dynamic reactions in flowing primary coolant.

Seismic events and design basis accidents cause few cycles of vibration loading because of their limited duration and occurrence. Therefore, these sources principally affect the static stability of RPVI, not cyclic loading (damage).

Hydrodynamic reactions are generated during normal operation conditions and during invasion of normal operation conditions. Vibration loading in these regimes is characteristic by timing changes of surface strengths, inertial strengths and internal structural frictional strengths as well as kinetic parameters (displacement, velocity and acceleration), stresses and deformations caused by these strengths.

Assessment of this ageing phenomenon requires calculation model prepared from structural part representative of RPV internal parts (reactor basket, guide tubes assembly, core basket and core basket bottom) and primary cooling water surrounds of internal parts inside of reactor pressure vessel. Fluid structure interaction (FSI) is defined on junction surfaces of internals so by this calculation was possible to calculate stress-deformation reactions of steel constructions on pressure pulses generated by reactor cooling pumps.

Time dependent parameter is count of stress range caused by pulse generated by the reactor coolant pump with reference radiation damage of RPVI materials.

For RPVI vibrations analyses, the TLAA is found acceptable under (i), (ii), or (iii) based on the following:

- Acceptance by (i):

For this case, design basis analyses did not include assessment of this degradation mechanism.

- Acceptance by (ii):

In this case, the TLAA analysis based on national requirements and different standards (as [1-5]) is focused on:

- Assessment of deformation and stress reaction of RPVI due to vibrations and determination of critical locations.

- Determination of overall count of cycles, binned by the stress range, caused by operation of reactor pumps to the end of the intended period of operation with reference to expected radiation damage.

- The allowable cycles is based on a radiation damage assessment (dpa) based on neutron fluence measurements and prediction for the intended period of operation .

If the analysis shows that cycle count meets the limits, then the TLAA is acceptable for the intended period of operation according to (ii) and no additional actions are needed.

- Acceptance by (iii):

In this case, the TLAA proved significance of vibrational effects and achievement of limits during the intended period of operation. This ageing mechanism can be managed by AMP 102 and AMP 113. If necessary, corrective actions are used such as repairs or replacement.

References

- AMERICAN SOCIETY of MECHANICAL ENGINEERS, ASME Section III, Rules for Construction of Nuclear Facility Components, 2001.

- MSZ 27003 Rules for Construction of Nuclear Facility Components, Hungarian Standardization Institution, 2013.

- PNAE G-7-002-87 “Standards for Strength Calculation of Equipment and Pipelines of Nuclear Power Plants”.

- VERLIFE Unified Procedure for Lifetime Assessment of Components and Piping in WWER NPPs. Final Version, 2003, EC.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: PWR Vessel Internals (2007 Update), IAEA-TECDOC-1557, IAEA, Vienna (2007).