- WANO

July 2005

Analysis of Events Caused by Human Errors

### WANO Operating Experience Central Team

LIMITED DISTRIBUTION

‘CONFIDENTIALITY NOTICE: Copyright - 2005 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale. This document is protected as an unpublished work under the copyright laws of all countries, which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. This document and its contents are confidential and shall be treated in strictest confidence. In particular, except with the prior written consent of the WANO Coordinating Centre, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations.’

‘LIABILITY DISCLAIMER NOTICE: This information was prepared in connection with work sponsored by WANO. Neither WANO, WANO members, nor any person acting on the behalf of them (a) makes warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that use of any information, apparatus, method or process disclosed in this document may not infringe on privately owned rights, or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of any information, apparatus, method, or process disclosed in this document.’

CHAPTER	PAGE

Table of Contents

Summary	2

A.  Analysis Details	4

1.  Search result	4

2.  Event selection	5

3.  Consequences of the events	5

B.  Common weaknesses	7

1.  Verbal communication	7

2.  Personnel work practices	9

3.  Written procedures and documents	13

4.  Supervisory methods	15

5.  Work organisation	16

6.  Decision process	17

C.  Event summaries	19

1.  EAR PAR 03-073; Maximum reactor vessel temperature rise exceeded	19

2.  EAR ATL 03-001; Wrong Chemicals Added to Steam Generators	20

3.  MER ATL 04-044; Endangered Diver Prompts Manual Trip	21

4.  EAR MOW 02-012; Automatic reactor scram due to a reactor operator's error	22

5.  EAR MOW 03-010; Technical specifications breach during essential service water pumps tests	23

6.  EAR PAR 04-002; Tech. Spec. violation during fuel unloading	25

7.  EAR PAR 04-007; Primary Circuit Leak Rate Exceeds Tech. Spec Limits	26

8.  EAR PAR 04-010; Reactor trip due to incorrect electrical restoration	26

9.  EAR PAR 04-018; Unmonitored waste gas release	27

10.  EAR PAR 04-053; Rector Trip during Rod Control System Power Supply Replacement	28

11.  MER PAR 03-028; Generator power adjustment result in tech. Spec. violation	29

12.  MER PAR 04-058; Reactor Trip due to Blower Speed Control Switch inadvertently remaining in the lower position	30

References	32

Event reports	32

## Summary

This report contains an analysis of human performance related events reported to WANO during 2002-2004. The purpose of this analysis was seek to understand the underlying causes of events that were reported as having human performance causes or casual factors. The main conclusion of the analysis is that improper or lack of use of known and accepted error prevention techniques is a significant contributor to human error related events.

#### Background

Most root causes and causal factors of human performance related events in the WANO database were attributed to the following factors:

- verbal communication

- personnel work practices

- written procedures and documents

- supervisory methods

- work organisation and decision process

These five areas were further divided to determine significant underlying contributors. See Sections A and B for details of the analysis.

#### Conclusions

- The analysis clearly shows that member plants and utilities need to place further emphasis and take more aggressive action on preventing errors. For example:

- At Oskarshamn unit 3, an operator inadvertently moved a switch governing a valve in the condensate demineraliser system too far, thereby causing the valve to open. The condenser was subsequently drained of water forcing the operators to manually trip the plant. The loss Oskarhamn unit 3, together with a subsequent disconnector failure in the switchyard connecting Ringhals unit 3 & 4 to the national grid, led to an electrical blackout in the south of Sweden and parts of Denmark. Self-checking was identified as one the tools that, if properly used, could have prevented this event.

- At the Vogtle NPP both units were shut down and brought to cold shutdown conditions after chemistry personnel inadvertently added the wrong chemical, sodium phosphate, to the condensate chemical injection systems of both units instead of methoxypropylamine (MPA). The plant concluded that multiple error prevention tools including procedure adherence, self- and peer-checking, pre-job briefing, questioning attitude and supervisory oversight were available but not applied.

- In many cases, known and effective error prevention techniques were not used or used improperly. The predominant techniques identified in the analysis were:

- pre-job briefings and post-job debriefs

- self-checking and peer-checking

- concurrent verification and independent verification

#### Selected Events

Twelve events were selected from the WANO data base as representative of events involving human errors. Aspects of these events were used throughout this report to highlight the significant impact that error prevention techniques could have on reducing errors. See Section C for summaries of these twelve events.

Key aspects and practical suggestions that promote excellent human performance are also provided in WANO Guidelines GL 2002-02, ‘Principles for Excellence in Human Performance’.

## A.	Analysis Details

An analysis of events reported to WANO during 2002-2004 and subsequently included in the WANO event data base was performed. The following criteria were used for this data base search:

- root causes and causal factors search fields were searched

- human performance related codes were included

- event reports during the years 2002-2004 were included (based on report date)

### 1.	Search result

The search provided the following overall result:

- 928 root causes and causal factors hits in total

- 477 root causes hits

- 451 causal factors hits

- from estimated 200-300 events

The explanation to why there are fewer events found compared to the number of root causes and causal factor hits is that several factors are often identified as root causes and causal factors for each event.

This search provided the following distribution of ‘root causes’ and ‘causal factors’ (detailed description of the ‘root causes’ and ‘causal factors’ codes used in this document is provided in WANO Operating Experience Programme Reference Manual, ref. 2):

| Human Performance Related (01** to 10** inclusive) | Management Related (11** to 18** inclusive) |
| --- | --- |

| 0100 | Verbal Communications |  | 1100 | Management Direction |
| --- | --- | --- | --- | --- |
| 0200 | Personnel Work Practices |  | 1200 | Communication or Co-ordination |
| 0300 | Personnel Work Schedule |  | 1300 | Management Monitoring and Assess’ |
| 0400 | Environmental Conditions |  | 1400 | Decision Process |
| 0500 | Man-Machine Interface |  | 1500 | Allocation of Resources |
| 0600 | Training / Qualification |  | 1600 | Change Management |
| 0700 | Written Procedures and Documents |  | 1700 | Organisational/Safety Culture |
| 0800 | Supervisory Methods |  | 1800 | Management of Contingencies |
| 0900 | Work Organisation |  |  |  |
| 1000 | Personal Factors |  |  |  |

As seen in the diagram above the most hits were received in the following group of factors:

- 0100 Verbal communication

- 0200 Personnel work practices

- 0700 Written procedures and documents

- 0800 Supervisory methods

- 0900 Work organisation

- 1400 Decision process

These groups are further discussed in the ‘common weaknesses’ section, below.

### 2.	Event selection

Twelve events were selected for more in-depth analysis from the over 200 events that was the result of WANO event data base. These events were selected in order to provide examples related to the most common root causes and causal factors as found in this study. Summaries of these events are provided in Appendix 1 of this report. The event descriptions are supplemented with analyses of root causes and contributing (or causal) factors.

### 3.	Consequences of the events

The consequences of the 12 events selected are as follows:

- automatic reactor trips (5 events)

- manual reactor trips (2 events)

- violation of technical specifications (5 events)

- forced shutdown for more than 2 weeks (2 events)

In addition, the following specific consequences were identified:

Rapid vessel temperature transient - One event resulted in a rapid vessel temperature transient, causing an extra significant level of technical specifications violation. The plant was remained shut down for around two months due to regulatory intervention (EAR PAR 03-073).

Contribution to a ‘loss of grid’ event - The same event as above contributed, together with a disconnector failure in the switchyard at another nuclear plant, to a ‘loss of grid’ event (EAR PAR 03-073).

Unmonitored radioactive release - One event resulted in an unmonitored radioactive release of radioactive waste gas. The actual release of radioactive waste gas did not reach any authorised statutory limits, although the event did not comply with technical specifications requirements (EAR PAR 04-018).

Secondary circuit chemical excursion - One event involved adding the wrong chemical into the steam generators of two units. This event resulted in chemical excursion in the secondary feedwater circuit and forced shut downs of two units that lasted 7 and 17 days, respectively (EAR ATL 03-001).

Life endanger situation - One event involved a diving activity in the plant’s water intake structure. The diver ended up being forced against the operating intake structure, after that the diver's communication line became stuck on a pipe support. This situation meant that the diver was placed in grave danger.

## B.	Common contributors

### 1.	Verbal communication (cause code group 0100)

Detailed analysis of the group ‘verbal communication’ shows the following distribution of root causes and causal factors:

As seen in the diagram the following factors received the most hits:

- 0102 Pre-job briefing inadequate / not performed

- 0107 Internal team communication inadequate

The following examples related to these factors were found in the depth analysis of the events.

#### a)	Pre-job briefing inadequate or not performed (cause code 0102)

Description Pre-job briefings are conducted for non-routine work, safety-critical work, and routine work when change is involved. Not only should the goals, or what is to be accomplishment, be discussed, but what should be avoided should also be discussed. More effective pre-job briefings engage the workers assigned to the task. At some stations the lead worker conducts the briefing with or without the first-line supervisor (reverse pre-job briefing). If the supervisor is present, he or she functions in an oversight and facilitative role. Along with task’s technical aspects, factors influencing human performance are also explored using following approach: - safety-critical elements of the task - just-in-time operating experience - performance modes and respective error modes - error-likely situations and associated error precursors - assumptions - potential consequences and worst-case situation - back-up plans, abort criteria, and key defences Effective pre-job briefings with respect to human performance should as a minimum use the SAFE conversation to identify as many error-likely situations as possible. More detailed information about how to perform pre-job briefings is provided in WANO document ‘Conduct of Pre-job Briefings and Post-job Debriefs’ – March 2004, ref. 3.

No pre-job briefing was held with the fuel handling team at Olkiluoto unit 1 before starting fuel handling during the night shift. The plant is considering require pre-job briefings with the fuel handling teams at the beginning of each shift.

An informal pre-job briefing was conducted at the Vogtle plant, which was contradictory to station administrative procedures that required a more formal briefing. The pre-job briefing was conducted by the duty chemistry supervisor, who primarily focused on forklift safety because the new container would be moved through the unit 1 and 2 turbine building. The pre-job briefing did not discuss all the aspects of obtaining and off-loading the chemicals and it did not heighten the chemists' awareness or reinforce a questioning attitude.

The Dukovany unit 1 shift supervisor did not perform a pre-job briefing before the protection logic test of the pumps in the essential service water system (ESW) and did not advise the staff involved in the protection logic tests (PLT) testing to follow the appropriate procedure so that the relevant LCO criteria was met during the test. If the ESW pumps were de-energized consecutively, train by train, it would have resulted in entering the condition A1, which was allowed for 72 hours and the Technical Specifications would not have been violated. The informal pre-job briefing held using telephone was not sufficient to identify the risks with performing the PLT test at this occasion.

#### b)	Internal team communication inadequate (cause code 0107)

During the discussions between the Dukovany unit 1 shift supervisor, the control room operator and the central pumping station (CPS) operator, no one questioned whether the logic test was suitable to be executed with two essential service water system (ESW) pumps inoperable. In addition, no one proposed alternative ways to perform the test. During the protection logic test, the secondary circuit operator did not inform the shift supervisor that there were two pumps secured in two different ESW trains simultaneously.

The Dungeness A unit 1 reactor operator left the control room without handing over proper information to the shift supervisor or the unit 2 reactor operator about the blower speed reduction that he had previously executed. Therefore, no one still present in control room noticed that the blower continued to reduce speed, due the stuck control switch. In addition, when the shift manager returned to the control room he started to take different actions without contacting the absent reactor operator.

The event investigation at Point Beach unit 2 concluded that team communication was vague and inconsistent throughout the entire diving evolution leading to the plant personnel, the diving liaison and the dive crew not being aligned on expectations and requirements and consistent understanding of the dive scope and specifically where the divers were located.

The turbine operator at Daya Bay unit 1 did not inform the reactor operator about the electrical output change that he was about to initiate. As a result, the reactor operator failed to discover immediately that the thermal power exceeded the allowed limit.

#### c)	Inter-team communication inadequate (cause code 0108)

Weaknesses existed at the Olkiluoto plant in communication within the fuel handling team and between the fuel handling supervisor, the control rod drive mechanisms maintenance foreman, the control room shift manager and the on duty nuclear fuel engineer.

### 2)	Personnel work practices (cause code group 0200

Detailed analysis of the group ‘personnel work practices’ shows the following distribution of root causes and causal factors:

As seen in the diagram the following factors received the most hits:

- 0201 Self-checking not used or ineffectively applied

- 0203 Required procedures, drawings, or other references not used

- 0211 Independent checking not used or ineffectively applied

- 0217 Lack of questioning attitude

The following examples related to these factors were found in the depth analysis of the events.

#### a)	Self-checking technique not used or improperly used (cause code 0201)

Definition The self-checking technique is designed to enhance one’s attention before performing a specific action on plant equipment. Self-checking is an individual work practice in which a person consciously and deliberately reviews the intended action and expected response before performing the action in question. A more detailed description of the self-checking technique is provided in WANO document ‘Verification Techniques’ – July 2005, ref. 4.

The L/C switch at Oskarshamn unit 3 that the operator was about to manoeuvre had three different positions, to the left position for local manoeuvre, ‘up’ position for manoeuvre from the main control room and to the right position for opening the associated valve. The self-checking technique includes an action of visualising the step that the individual was about to take. In this case, the operator did not succeed to visualise that the correct manoeuvre of the L/C switch was from the left to the up position, while a left to right manoeuvre would inevitable lead to a plant trip. The operator was aware of that this kind of switch could be hard to manoeuvre. Although, this knowledge should have made him even more aware of the danger of moving the switch too far.

At Bugey unit 4 & 5, the initial error was made by the chemistry supervisor, who mistakenly submitted to the unit 4/5 control room a unit 9 release form containing analysis results for units 4/5. Subsequently, neither the shift manager of units 4/5, nor the two shift supervisors of units 4 and 5, nor the unit 5 control room operator detected the wrong unit identification. None of these six persons involved in the handling of the documents imposed enough rigour self-checking to be able to identify that the release order contained a wrong tank.

The reactor operator at Mochovce unit 2 switched the dials on two setting units of the same neutron flux monitoring system (NFMS) below the actual reactor power level (from 98 to 0% and from 98 to 8 %, respectively). He carried out the set-point adjustments quickly, without confirming the correct actions using light signals on the control room panels and without checking the adjusted values on the NFMS monitor. While doing so, the reactor operator did not adhere to requirements in plant operating procedures. The plant concluded that self-checking technique was not properly applied during the sequence.

#### b)	Use of the ‘two minute rule’ (part of the self-checking technique)

Another error prevention tool that would have been suitable to apply during the Daya Bay unit 1 event is the ‘two minute rule’. Both the turbine operator and the reactor operated should have monitored the appropriate instrumentation and process recorders for a couple of minutes in order to verify the result of the set-point adjustment. Two minutes would have been enough in this case.

The characteristics of the blower speed control at Dungeness A are such that an initial reduction in blower speed is followed by a short period in which the blower speed may stabilise or even temporarily increase. This is then followed by a prolonged reduction in blower speed. After initiating a blower speed reduction, the reactor operator did not wait long enough to notice that the blower speed continued to drop after a period of stabilisation.

#### c)	Peer-checking technique not used (cause code 0211)

Definition Peer-checking is a series of actions by two individuals working together at the same time and place, before and during a specific action, to prevent an error by the performer, ref. 4.

The maintenance crew involved in the Nogent unit 1 event consisted of a craftsman and a work supervisor. This was an ideal situation for using the peer-checking technique during the work, with the craftsman acting as the performer and the work supervisor acting as the peer verifying that the right actions were taken. By applying proper peer-checking, the crew should have been able to identify the proper valve for the repair work.

Three different persons were involved in the latter part of the chemical refilling activity at the Vogtle plant, the junior chemistry technician, the duty chemistry foreman and a senior chemistry technician. Therefore, it would have been easy for them to perform peer-checking that the container contained the proper chemical, with the junior technician as the performer and either of the foreman or the senior technician as the verifier. The plant has a peer-checking programme in place and the procedure in question required peer-checking, so this error was attributed to the staff involved in the event.

Adjusting the electrical output with the thermal power being close to the maximum allowed output limit is an action involving a significant risk for exceeding licensing conditions. Peer-checking is a suitable tool to use to avoid a single personal error during set-point adjustments. Independent verification would be an even stronger tool to use. Neither peer-checking, nor independent verification where required by the Daya Bay plant to be used during this event.

#### d)	Concurrent verification technique not used (cause code 0211)

Definition Concurrent verification is a series of actions by two individuals working together at the same time and place to confirm separately the condition of a component before, during and after an action. Concurrent verification is especially useful to apply for activities that involve an action or manipulation, where an incorrect action could lead to immediate and irreversible harm to the plant, ref. 4.

The event at Saint Alban unit 2 involved isolating and restoring control rod drive mechanisms (CRDM) power supply. While isolating and restoring the CRDM power supply, the tagging officer used a computer-aided procedure and applied an operating instruction. The engineer was familiar with the job, which he had performed twice a year on average. He was familiar with risks and challenges associated the manipulation of CRDM power supply.

Although, the isolation of train 2 of the electrical supply was interrupted when the engineer realised that he had forgotten to remove the padlock from the train1 supply cabinet. Subsequently, a reactor scram occurred caused by the manipulation error performed by the engineer. If concurrent verification would have been applied, the likelihood of this to happen would have been decreased, since this technique emphasize on each step in a procedure or an instruction to be executed before moving to the next step. Plant procedures did not require concurrent verification for this activity.

At Mochovce unit 2, the operator adjusted set-points in the neutron flux monitoring system (NFMS), which provides signal input into the reactor protections system (RPS) logic. Adjusting set-points in the NFMS is an activity where an incorrect action would lead to immediate and irreversible harm to the plant. Therefore, RPS logic set-points adjustments is a typical activity were concurrent verification should be required to be applied. Subsequently, a reactor scram occurred because of the manipulation error performed by the staff individual. Concurrent verification was required by the plant in this case.

#### e)	Independent verification technique not used (cause code 0211)

Definition Independent verification is a series of actions by two individuals working independently to con-firm the condition of a component after the original act that placed it in that condition, ref. 4.

Mixing control rod drive mechanism (CRDM) maintenance with fuel unloading involves different risks related to reactivity control, risk of radioactive releases and equipment damages. Independent verification would have been suitable to be performed at Olkiluoto unit 1 to verify that all requirements were fulfilled before the start of fuel unloading and mistakenly continuing with fuel unloading in super cells affected by the CRDM maintenance. The shift manager or the on duty nuclear fuel engineer could have been used as verifier. Although, neither peer-checking, nor independent verification where required by the plant to be used in this situation.

The Bugey plant did not require any independent verification to be performed to check whether the release order was correct or not. Such an independent verification could have been set up with the chemistry supervisor as the performer and either of the shift manager or the shift supervisors as the verifier. Had an independent verification been applied in this situation, it is likely that the mistake with choosing the wrong tank would have been disclosed.

There are two risk involved in any release of radioactive waste. One risk is the potential release of waste that exceeds regulatory limits and the second is the fact that any uncontrolled or unauthorised release of radioactivity could impair public confidence in the plant and the industry. Therefore, release of radioactive waste is an activity that involves a significant risk for which independent verification a suitable tool to be used.

#### f)	Use of procedures and documentation (cause code 0203)

The control room operators at Dukovany unit 1 did not refer to the written procedure for the logic test, because the protection logic tests (PLT) was always managed by the central pumping station (CPS) operator. No printed copy of the procedure was available in the unit 1 control room, although, it was available on the plant computer LAN.

The first step of the related PLT procedure required informing the shift supervisor, if any essential service water system (ESW) pump was inoperable and postponing the PLT until all pumps were operable. The CPS 1 operator did not consistently perform this step and proceeded with the test. Neither the secondary circuit operator nor the CPS 1 operator referred to the plant Technical Specifications to verify that pertinent LCO criteria would be met during the PLT, with two ESW pumps being out of service.

The chemistry personnel involved in the chemical filling activity at Vogtle did not use the approved procedure for refilling the chemical addition tanks. The procedure contained appropriate steps for verifying that the correct chemical was being added.

The I&C technicians at Krško followed the power cabinet schematic diagram provided by the vendor instead of using plant wiring diagram. Training at the vendor was based on these schematic diagrams rather than approved wiring diagrams. The difference, although minimal, led to the disconnection of the additional wire, thus causing a reactor trip.

Principles about the use of procedure and documents are further described in WANO Guidelines GL 2001-02, ‘Guidelines for the Conduct of Operations at Nuclear Power Plants’, chapter IV, ref. 5.

#### g)	Lack of questioning attitude (non-conservative decision making) (cause code 0217)

Questioning attitude - description A questioning attitude encourages foresight to precede actions, to make sure planning, judgement and decision-making are appropriate for the situation. A questioning attitude promotes awareness of uncertainty and hazards and must overcome the temptation to rationalize away ‘gut feelings’ of something not right. Knowing that it is difficult for a worker to see their own mistake, colleagues, bosses and even subordinates are encouraged to question, without invitation, another’s action or decision if not understood. This method can be used to confirm the authenticity of a specific action and to validate the appropriateness of the action to achieve desired results.

During the Krško event, the technicians noticed a strange wiring (they were confused to see additional wire). Although, they did not stop the job to clarify the situation. They relied on the actions and statements of each other, as well as on a misleading instruction manual. A conservative decision making approach would have been to stop the work when facing a confusing situation and report the problem to their supervisor or the control room.

The Dungeness A unit 1 reactor operator and the operator trainee response to the low margin alarm was to adjust margins rather than question what had caused the alarm. This took them away from the reactor controls and instruments in the control room as the transient was developing.

After arriving back to the control room the Dungeness A shift manager assumed, based on a temperature error indication, that the gas blower had tripped and he started to operate control rods and closing a valve in the gas coolant circuit. It was only after doing this that the shift manager and the unit 2 reactor operator mentally questioned and considered the plant status and wondered why there were no blower emergency stop valve alarms triggered on the alarm panel (such alarms would normally be present in the event of a blower trip).

The technician at the Vogtle plant found four different stainless steel containers in the warehouse, none of them labelled with the proper product name. The technician should have questioned whether he had the proper information available in order to identify the correct chemical.

### 3.	Written procedures and documents (cause code group 0700)

Detailed analysis of the group ‘written procedures and documents’ shows the following distribution of root causes and causal factors:

As seen in the diagram the following factors received the most hits:

- 0701 No document available

- 0702 (Procedure) technically incorrect

- 0703 (Procedure) technically incomplete

- 0704 Cautionary information not included (in procedure)

Categories 0702, 0703 and 0704 can be combined into one category, procedures (or other technical guidance information) incomplete or incorrect. Examples related to these factors are presented below.

#### a)	Written procedure deficiencies (cause code 0702, 0703 or 0704)

In a boiling water reactor (BWR) all reactor recirculation pumps (RCP) are normally never stopped at the same time, except as a consequence of loss of off-site power. Therefore, restarting RCP pumps in the situation that existed at Oskarshamn unit 3 was an infrequently performed evolution. The procedure for re-establish the reactor coolant circulation did not include any cautions regarding the risk for stratification of water of different temperature.

The Point Beach procedure for intake structure inspections was vague and not written in accordance with the station writer's guide. In addition, the procedure was not adhered to at all times.

#### b)	Inadequate safety assessment provided (cause code 0712)

Even though all dives involve an environment 'Immediately Dangerous to Life and Health' according to the Point Beach procedures, general diving was normally classified as ‘medium risk’, not ‘high risk’. The intake structure diving evolution was classified as medium risk by the planner/diving liaison, but the root cause evaluation team classified the same evolution as high risk.

### 4.	Supervisory methods (cause code group 0800)

Detailed analysis of the group ‘supervisory methods’ shows the following distribution of root causes and causal factors:

As seen in the diagram the following factors received the most hits:

- 0802 Progress not adequately monitored

- 0807 Control of contractors inadequate

The following examples related to these factors were found in the depth analysis of the events.

#### a)	Progress not adequately monitored (cause code 0802)

The junior chemistry technician at Vogtle was recently qualified and it was the first time he was sent to the warehouse to pick up a container with the chemical in question. Although, the duty chemistry foreman did not follow the technician to the warehouse to explain the content and usage of the different chemicals in the containers. In addition, the foreman never confirmed that the container brought to the turbine building by the technician contained the proper chemical.

The unit 1 shift supervisor at Dukovany authorised the essential service water system (ESW) logic tests to be preformed according to the protection logic tests (PLT) schedule, even though two ESW pumps were secured for maintenance. His reason for this decision was to complete the task during the scheduled time frame so that it did not need to be postponed. Despite the fact that the condition of the ESW system was not appropriate for the PLT test and it was inevitable to enter a LCO during the test, the shift supervisor permitted the tests and did not explicitly advise the unit 1 shift supervisor of necessary actions to avoid breach of Technical Specifications.

The unit 1 shift supervisor, who was formally responsible for the PLT test, was busy with other activities during the tests and did not adequately supervise the progress of the test.

The Olkiluoto plant concluded that the on-duty control room shift manager has the overall responsibility of supervising both fuel unloading and control rod drive mechanisms (CRDM) maintenance. In order to do so, there is at Olkiluoto a computerised core mapping system, COROS. In addition, the shift manager had specific work orders with detailed step by step listings for the supervision of both the progress of the CRDM maintenance and the fuel unloading. Although, he failed to supervise these two activities close enough in order to avoid any deviations to occur.

There was little or no management oversight for the diving operation at Point Beach unit 2. Supervisory oversight was not adequate at all times.

#### b)	Supervisor too involved in tasks (cause code 0804)

When the Dungeness A shift manager returned to the control room and noticed the low blower speed he resumed the role of the absent reactor operator and started to take different actions. This meant that the shift manager got too involved in the unit 1 reactor desk tasks without having a proper oversight of the plant status. The shift manager had been away from the control room for a while and this aggravated the situation.

### 5.	Work organisation (cause code group 0900)

Detailed analysis of the group ‘work organisation’ shows the following distribution of root causes and causal factors:

As seen in the diagram the following factor received the most hits:

- 0902 Special conditions or requirements not identified

The following examples related to this factor were found in the depth analysis of the events:

#### a)	Special conditions or requirements not identified (cause code 0902)

The two essential service water system (ESW) pumps taken out for maintenance at Dukovany unit 1 and 2 had been inoperable for 5 and 7 days, respectively. Although there was no continuous work on the pumps, they remained secured even during the planned protection logic test (PLT). The maintenance on the pumps was completed within 1-2 days after the event.

The PLT test procedure for the ESW system involves performing the protection logic tests for all pumps belonging to one unit in all three trains during the same shift. According to the procedure, all odd or even pumps are secured simultaneously for the test. Technical Specifications requirements are met as long as all ESW pumps are operable. Although, if any ESW pump is inoperable, the parallel testing of pumps in all ESW trains will result in a Technical Specifications breach. This special condition was not recognised by the staff involved in the evolution.

A pre-dive checklist was not completed at Point Beach unit 2 before the diving work. The dive scope, hazards, abort criteria and access limitations were not fully understood and were not effectively communicated between the diving liaison and the dive company or crews. Plant personnel and the dive crew treated diving operations as a routine job. No heightened or special awareness was given to the diving operation.

### 6.	Decision process (cause code group 1400)

Detailed analysis of the group ‘decision process’ shows the following distribution of root causes and causal factors:

As seen in the diagram the following factor received the most hits:

- 1470 Inadequate operating experience feedback process

Examples related to this factor are presented below.

#### a)	Inadequate operating experience feedback process (cause code 1470)

An event similar to the second part of the event at Oskarshamn unit 3 occurred at the Gundremmingen unit C BWR in Germany. Information about this event was available to the plant. Forsmark unit 3, a unit of the same type and vintage as Oskarshamn unit 3, made a procedure change to incorporate a caution note about the risk of stratification based on the OE information from Germany. Although, the same procedure change was never adopted by the Oskarshamn plant.

Some elements of involved in the diving incident at Point Beach occurred in a previous diving incident in October 2000. The plant was unable to implement sufficient corrective actions in order to prevent a recurrence.

The Krško plant had already in 1987 received operating experience from the vendor notifying about the problems with the rod control power supply. The OE information included warnings about possible confusion over differences between the power cabinet schematic and the power cabinet wiring diagram These differences could indirectly cause a reactor trip, when a plant tries to replace a power supply with the plant at power.

Detailed guidelines about the use of operating experience are provided in WANO Guidelines GL 2003-01, ‘Guidelines for Operating Experience at Nuclear Power Plants’, ref. 6.

## C.	Event summaries

#### 1.	EAR PAR 03-073; Exceeding the maximum allowed limit for temperature rise for the reactor vessel (Oskarshamn unit 3, 23 September 2003)

##### Event 1

Cleaning of a back flushing tank in the condensate demineraliser system had been carried out at Oskarshamn unit 3 and an operator were about to restore line-up of the equipment included in the work permit. When the operator was about to change position of a ‘local/central manoeuvre’ switch (L/C switch) for an isolation valve back from local to central manoeuvring position, he inadvertently moved the switch too far to the right, and thereby initiated an opening signal to the valve. This caused the valve to open and water was drained from the condenser into the back flushing tank in the condensate demineraliser system, which was rapidly overfilled.

Within 3 minutes, a condenser low level alarm was received in the control room. The reactor operator initiated an automatic power runback and 15 seconds later, after consulting the shift manager, the plant was scrammed manually.

The loss Oskarhamn unit 3 caused substantial fluctuations in frequency and voltage in the southern part of the Swedish high-voltage grid. Five minutes after that Oskarhamn unit 3 tripped, a disconnector failed in the switchyard, which connect Ringhals unit, 3 & 4 to the grid. This caused two different electrical bus bars to trip, thereby causing disconnection of Ringhals unit 3 & 4 from the grid. This situation led to an electrical blackout in the south of Sweden and parts of Denmark.

##### Event 2

At Oskarhamn unit 3, all eight main reactor recirculation pumps (RRP) stopped as designed due to loss of non-essential power. The control room staff initiated restoration of plant systems and the residual heat removal system (RHR) was restored, providing a small flow (in total 12kg/s) of cold water into the bottom of the reactor vessel through the control rod drive mechanisms (CRDM). This caused cold water to accumulate in the bottom of the vessel. Four hours after the initial event, the control room staff restarted two RRP pumps. Shortly after, an alarm for ‘rapid temperature increase’ was received from a temperature switch located in one of the bottom gables of the vessel.

After analysing the temperature printout, plant staff concluded that a rapid temperature increase of around 140C in the bottom of the vessel had occurred. This meant that the maximum allowed limit according to the technical specifications for temperature rise of the reactor vessel could have exceeded the ‘maximum allowed limit’ (the so called ‘HTG-limit’) for rapid temperature change of the vessel. After decision by the safety review committee, the unit was brought to cold shut down the following morning for further analysis of the event.

##### Analysis

Improper self-checking - The L/C switch at that the operator was about to manoeuvre had three different positions, to the left position for local manoeuvre, ‘up’ position for manoeuvre from the main control room and to the right position for opening the associated valve. The self-checking technique includes an action of visualising the step that the individual was about to take. In this case, the operator did not succeed to visualise that the correct manoeuvre of the L/C switch was from the left to the up position, while a left to right manoeuvre would inevitable lead to a plant trip. The operator was aware of that this kind of switch could be hard to manoeuvre. Although, this knowledge should have made him even more aware of the danger of moving the switch too far.

Procedure technically incomplete - In a boiling water reactor (BWR) all reactor recirculation pumps (RCP) are normally never stopped at the same time, except as a consequence of loss of off-site power. Therefore, restarting RCP pumps in this situation was an infrequently performed evolution. The procedure for re-establish the reactor coolant circulation did not include any cautions regarding the risk for stratification of water of different temperature.

Inadequate use of operating experience - An event similar to the second part of the event occurred at the Gundremmingen unit C BWR in Germany. Information about this event was available to the plant. Forsmark unit 3, a unit of the same type and vintage as Oskarshamn unit 3, made a procedure change to incorporate a caution note about the risk of stratification based on the OE information from Germany. Although, the same procedure change was never adopted by the Oskarshamn plant.

#### 2.	EAR ATL 03-001; Incorrect Chemicals Added to Steam Generators Results in Dual-Unit Shutdown and Extended Outage (Vogtle unit 1 & 2 November 2002)

Vogtle unit 1 and 2 were shut down and brought to cold shutdown conditions after chemistry personnel inadvertently added the wrong chemical, sodium phosphate, to the condensate chemical injection systems of both units instead of methoxypropylamine (MPA).

A junior chemistry technician was assigned with the task of fetching the chemical at the warehouse. He there found four different stainless steel containers in close proximity. The containers were not labelled with any product names, but instead labelled with manufacture name and code numbers, reading ‘Nalco 7399’, ‘Nalco 94UF193’ and ‘Nalco 1336’. Nalco 7399 corresponded to sodium phosphate, while Nalco 94UF193 corresponded to MPA. The technician was uncertain which container contained MPA, because of the similarity of the labels. He therefore asked a warehouse worker for assistance, who retrieved the purchase requisition and purchase order. After reviewing the paperwork, the technician incorrectly determined that the container of sodium phosphate was an MPA container.

The junior technician was met in the turbine building by the duty chemistry foreman and a senior chemistry technician. The three proceeded to the unit 2 MPA addition tank where they refill the tank with the wrong chemical. The group then repeated the evolution on unit 1.

Within one hour of the inadvertent chemical addition, unit 2 entered an abnormal operating procedure for high sodium concentration in the feedwater system and began shutting down. The unit 1 feedwater sodium concentration began trending upward a short time later and the unit was also shut down. Both units were subsequently brought to cold shutdown conditions to drain and flush the steam generators. Unit 1 returned to service after a 7-day outage while unit 2 was out of service for 17 days. The potential long-term effects of the sodium intrusion are being analyzed.

##### Analysis

The analysis team concluded that the direct cause of the event was an inexperienced junior technician that picked the wrong chemicals from the warehouse. The root cause and contributing factors identified included insufficient use of the following error prevention tools:

Pre-job briefing - An informal pre-job briefing was conducted, which was contradictory to station administrative procedures that required a more formal briefing. The pre-job briefing was conducted by the duty chemistry supervisor, who primarily focused on forklift safety because the new container would be moved through the unit 1 and 2 turbine building. The pre-job briefing did not discuss all the aspects of obtaining and off-loading the chemicals and it did not heighten the chemists' awareness or reinforce a questioning attitude.

Questioning attitude - The technician found four different stainless steel containers in the warehouse, none of them labelled with the proper product name. The technician should have questioned whether he had the proper information available in order to identify the correct chemical.

Peer-checking not performed - Three different persons were involved in the latter part of the chemical refilling activity, the junior chemistry technician, the duty chemistry foreman and a senior chemistry technician. Therefore, it would have been easy for them to perform peer-checking that the container contained the proper chemical, with the junior technician as the performer and either of the foreman or the senior technician as the verifier. The plant has a peer-checking programme in place and the procedure in question required peer-checking, so this error was attributed to the staff involved in the event.

Inadequate supervisory oversight - The junior chemistry technician was recently qualified and it was the first time he was sent to the warehouse to pick up a container with the chemical in question. Although, the duty chemistry foreman did not follow the technician to the warehouse to explain the content and usage of the different chemicals in the containers. In addition, the foreman never confirmed that the container brought to the turbine building by the technician contained the proper chemical.

Procedures not used - The chemistry personnel involved in the activity did not use the approved procedure for refilling the MPA addition tanks. The procedure contained appropriate steps for verifying that the correct chemical was being added.

#### 3.	MER ATL 04-044; Endangered Diver Prompts Manual Trip (Point Beach unit 2, 15 May 2004)

At Point Beach unit 2, a five-person dive crew was inspecting damages at the circulating water intake structure that had been identified a couple of days earlier. During a dive, the diver's air and communication line was sucked into the intake structure and became stuck on a pipe support for a chlorine injection line. Neither the diver nor the assisting person on the boat were able to free the line. A rescue diver that was sent into the area was also unable to free the line. The diver ended up being forced against the operating intake structure.

After the diver's communication line was lost due to fretting against the pipe support and rescue efforts to free the line had failed, the head of the diving team contacted the main control room and requested the circulating water pumps to be stopped. The control room crew scrammed the unit manually from 100 percent and stopped both circulating pumps. After these actions, the rescue diver was able to free the snagged line and both divers could leave the water without further assistance. Neither diver required medical attention as a result of the event.

The event was mainly a matter of personnel safety, for which a diver was placed in grave danger. Based on a probabilistic risk assessment the plant concluded that the manual plant trip was of ‘very low risk significance’ in respect to nuclear safety.

##### Analysis

Work planning - A pre-dive checklist was not completed for this dive. The dive scope, hazards, abort criteria and access limitations were not fully understood and were not effectively communicated between the diving liaison and the dive company or crews. Plant personnel and the dive crew treated diving operations as a routine job. No heightened or special awareness was given to the diving operation.

Risk determination - Even though all dives involve an environment 'Immediately Dangerous to Life and Health' according to the Point Beach procedures, general diving was normally classified as ‘medium risk’, not ‘high risk’. The intake structure diving evolution was classified as medium risk by the planner/diving liaison, but the root cause evaluation team classified the same evolution as high risk.

Team communication - The plant concluded that team communication was vague and inconsistent throughout the entire diving evolution leading to the plant personnel, the diving liaison and the dive crew not being aligned on expectations and requirements and consistent understanding of the dive scope and specifically where the divers were located.

Procedure content and use - The procedure for intake structure inspections was vague and not written in accordance with the station writer's guide. In addition, the procedure was not adhered to at all times.

Management and Supervisory Oversight - There was little or no management oversight for the diving operation. Supervisory oversight was not adequate at all times.

Job execution - Although it is understood that boat movement affects line tending, the videotape clearly showed several instances of excessive slack in the diver’s air hose and communication connections and the safety rope.

Use of operating experience - Some elements of involved in this event occurred in a previous diving incident at Point Beach in October 2000. The plant was unable to implement sufficient corrective actions in order to prevent a recurrence.

#### 4.	EAR MOW 02-012; Automatic reactor scram due to a reactor operator's error (Mochovce unit 2, 2 February 2002)

Mochovce unit 2 was operating at 50% power with one of the two main generators connected to the grid. Control personnel received directions to increase power and connect the second generator to the grid. During the reactor power increase, the reactor operator had to adjust periodically the reactor scram set-points on increased neutron flux.

While adjusting the reactor scram set-points at 84% reactor power, the reactor operator erroneously adjusted the set-points in two channels in one of the neutron flux monitorring system (NFMS) sets downwards instead of upwards. This resulted in a 2 out of 3 channels actuation signal from the NFMS system to the reactor protection system (RPS) and the reactor scrammed automatically.

##### Analysis

Improper self-checking - The reactor operator switched the dials on two setting units of the same NFMS below the actual reactor power level (from 98 to 0% and from 98 to 8 %, respectively). He carried out the set-point adjustments quickly, without confirming the correct actions using light signals on the control room panels and without checking the adjusted values on the NFMS monitor. While doing so, the reactor operator did not adhere to requirements in plant operating procedures. The plant concluded that self-checking technique was not properly applied during the sequence.

Concurrent verification technique not used - Adjusting set-points in the neutron flux monitoring system, which provides signal input into the RPS logic, is an activity where an incorrect action would lead to immediate and irreversible harm to the plant. Therefore, RPS logic set-points adjustments is a typical activity were concurrent verification should be required to be applied. This was required by the plant in this case. Subsequently, a reactor scram occurred as a consequence of the manipulation error performed by the staff individual.

#### 5.	EAR MOW 03-010; Breach of plant Technical Specifications during a planned test of protection logic of essential service water pumps (Dukovany unit 1, 23 January 2002)

##### Background

Dukovany NPP consists of four VVER-440 units arranged into two twin units. Each pair of units has its own essential service water system (ESW) consisting of three independent trains with four ESW pumps each. Two of them are powered from the essential power system (including emergency diesel generator) of the first unit and the other two pumps are powered from the second unit. Two pumps are running in each ESW train during normal operation of a unit, while the remaining pumps are normally on standby. Remotely operated equipment in the ESW system is operated either from the main control rooms or from a central pumping station (CPS).

The Technical Specifications require operability of all ESW trains in modes 1 – 4 of each unit, with at least two pumps in each train operable, including powered from different units. One ESW train may be inoperable for 72 hours under a LCO condition.

##### Event

On 23 January 2002, units 1 and 2 were operating at 100% power. During a telephone briefing with shift leading personnel and the shift manager common for all four units at the beginning of the afternoon shift, the unit 1 shift supervisor informed the participants that unit 1 ESW pump protection logic tests (PLT) were scheduled for the afternoon shift according to the plant PLT schedule.

After the briefing, the CPS 1 operator phoned to the unit 1 control room asking if they really were going to perform the protection logic test, since one ESW pump each in two different trains were out of service for maintenance. The unit 1 shift supervisor advised the CPS 1 operator to go ahead with the PLT test.

The control room circuit operator subsequently stopped the one ESW pump in each train upon CPS 1 operator’s request and an electrician deenergized power circuits to the affected ESW pumps.

Three hours later the unit 1 shift supervisor found that in total five ESW pumps were inoperable simultaneously, thus violating Technical Specification requirements. The shift supervisor immediately ordered the protection logic tests to be terminated and to recover operability of three ESW pumps immediately.

##### Analysis

Pre-job briefing not properly performed - The unit 1 shift supervisor did not perform a pre-job briefing before the protection logic test and did not advise the staff involved in the PLT testing to follow the appropriate procedure so that the relevant LCO criteria was met during the test. If the ESW pumps were de-energized consecutively, train by train, it would have resulted in entering the condition A1, which was allowed for 72 hours and the Technical Specifications would not have been violated. The informal pre-job briefing held using telephone was not sufficient to identify the risks with performing the PLT test at this occasion.

Weak team communication - During the discussions between the shift supervisor, the control room operator and the CPS operator, no one questioned whether the logic test was suitable to be executed with two ESW pumps inoperable or proposed alternative ways to perform the test. During the protection logic test, the secondary circuit operator did not inform the shift supervisor that there were two pumps secured in two different ESW trains simultaneously.

Use of procedures - The control room operators did not refer to the written procedure for the logic test, because the protection logic tests (PLT) was always managed by the central pumping station (CPS) operator. No printed copy of the procedure was available in the unit 1 control room, although, it was available on the plant computer LAN.

The first step of the related PLT procedure required informing the shift supervisor, if any essential service water system (ESW) pump was inoperable and postponing the PLT until all pumps were operable. The CPS 1 operator did not consistently perform this step and proceeded with the test. Neither the secondary circuit operator nor the CPS 1 operator referred to the plant Technical Specifications to verify that pertinent LCO criteria would be met during the PLT, with two ESW pumps being out of service.

Work organisation and planning - The two essential service water system (ESW) pumps taken out for maintenance had been inoperable for 5 and 7 days, respectively. Although there was no continuous work on the pumps, they remained secured even during the planned protection logic test (PLT). The maintenance on the pumps was completed within 1-2 days after the event.

The PLT test procedure for the ESW system involves performing the protection logic tests for all pumps belonging to one unit in all three trains during the same shift. According to the procedure, all odd or even pumps are secured simultaneously for the test. Technical Specifications requirements are met as long as all ESW pumps are operable. Although, if any ESW pump is inoperable, the parallel testing of pumps in all ESW trains will result in a Technical Specifications breach. This special condition was not recognised by the staff involved in the evolution.

Management supervision and oversight - The unit 1 shift supervisor authorised the ESW logic tests to be preformed according to the PLT schedule, even though two ESW pumps were secured for maintenance. His reason for this decision was to complete the task during the scheduled time frame so that it did not need to be postponed. Despite the ESW system condition was not appropriate for the protection logic tests and it was inevitable to enter a LCO during the test, the shift supervisor permitted the tests and did not explicitly advise the unit 1 shift supervisor of necessary actions to avoid breach of Technical Specifications.

The unit 1 shift supervisor, who was formally responsible for the PLT performance, was busy with other activities during the test and did not adequately supervise the progress of the test.

#### 6.	EAR PAR 04-002; Removal of two fuel rod bundles around a control rod under annual maintenance (Olkiluoto unit 1, 15 May 2002)

##### Background

During the 2002 annual maintenance and refuelling outage at Olkiluoto unit 1, maintenance on control rod drive mechanisms (CRDM) was planned to be performed in parallel with fuel unloading. The Technical Specifications for the unit allow fuel unloading to be executed in sequence with CRDM maintenance, but not fuel reshuffling or fuel loading. Each CRDM, including the control rod, is withdrawn downwards from the reactor core in order to enable the CRDM to be dismantled for maintenance. Only one control rod at a time is allowed to be withdrawn from the reactor core.

An additional Technical Specifications requirement is that there should be at least two fuel elements in diagonal positions left in the affected ‘supercell’ (a supercell consists of the control rod and four adjacent fuel elements) during CRDM manoeuvring.

Fuel unloading started on 15 May around 11 pm and the first unloading period was scheduled to last until eight o'clock the following morning. The engineering support department had prepared a separate work instruction with a listing of fuel elements to be unloaded. The oncoming fuel handling supervisor on the night shift authorised the fuel unloading to proceed with the unloading of remaining fuel elements in cell U35. The supervisor failed to recognise that the control rod in cell U35 was fully withdrawn. In addition, he did not notice that the fuel removal instruction and fuel listing table clearly stated that latter part of the fuel unloading required the CRDM maintenance to be finished.

The event did not have any safety significance in terms of nuclear criticality. However, the event involved a violation of the Technical Specifications and indicated the vulnerability of the administrative barriers in place.

##### Analysis

Supervision and monitoring - The plant concluded that the on-duty control room shift manager has the overall responsibility of supervising both fuel unloading and control rod drive mechanisms (CRDM) maintenance. In order to do so, there is at Olkiluoto a computerised core mapping system, COROS. In addition, the shift manager had specific work orders with detailed step by step listings for the supervision of both the progress of the CRDM maintenance and the fuel unloading. Although, he failed to supervise these two activities close enough in order to avoid any deviations to occur.

Independent verification not performed - Mixing control rod drive mechanism (CRDM) maintenance with fuel unloading involves different risks related to reactivity control, risk of radioactive releases and equipment damages. Independent verification would have been suitable to be performed to verify that all requirements were fulfilled before the start of fuel unloading and mistakenly continuing with fuel unloading in super cells affected by the CRDM maintenance. The shift manager or the on duty nuclear fuel engineer could have been used as verifier. Although, neither peer-checking, nor independent verification where required by the plant to be used in this situation.

Pre-job briefing not performed - No pre-job briefing was held with the fuel handling team before starting fuel handling during the night shift. The plant is considering to require pre-job briefings with the fuel handling team at the beginning of each shift.

Inter team communication - Weaknesses existed in communication within the fuel handling team and between the fuel handling supervisor, the CRDM maintenance foreman, the control room shift manager and the on duty nuclear fuel engineer.

#### 7.	EAR PAR 04-007; Primary Circuit Leak Rate Exceeds Tech. Spec Limits because of Maintenance on Incorrect V/V (Nogent 1, 17 April 2003)

A maintenance crew consisting of a craftsman and a work supervisor got the task to repair a stuffing box on valve 1 REN 275 VP in the nuclear auxiliary building. When they arrived in the room, the workers made a mistake in locating the relevant valve and started to unscrew the stuffing box on valve 1 RCV 275 VP instead, (a motor operated valve in chemical & volume control system (CVCS)). While unscrewing the stuffing box, a significant leak from the valve occurred.

The workers left the room, convinced they were working on the right equipment. They called the control room to alert them about the leaking valve. After some consideration, the work supervisor felt that pressure was too high for a simple leak. He went back into the room to check the valve identity. He found that they had been working on the worng valve.

While consulting the Technical Specifications the management found that the leak caused the plant to enter into two separate Limiting Conditions for Operations (LCO). One LCO criteria was raised since a charging line in the CVCS system was unavailable. The second LCO criteria related to the fact that valve RCV 275 VP, which is a containment isolation valve, was leaking. These two criteria together required the unit to be shut-down within one hour. The plant was able to repair the leaking valve within the required time frame, thereby avoiding a plant shutdown.

##### Analysis

The maintenance crew made an error and identified the wrong valve, 1 RCV 275 VP instead of 1 REN 275 VP. A couple of factors contributed to the error. Valve 1 REN 275 VP was not properly labelled. While at the work site, the crew first identified valve 1 REN 274 VP, which was locked out in closed position. In close proximity to this valve was located valve 1 RCV 275 VP. By assuming that valves located in close proximity to each other would also belong to the same system and since they knew they were in a room containing equipment in the REN system, both workers read tag 1 R—275 VP and wrongly assumed this valve to be 1 REN 275 VP.

The work area contained radioactive hot spots, a fact that was underscored with the presence of lead shielding on equipment. The plant analysis concluded that this fact was contributing factor to the event, since that put extra pressure on the crew

Peer-checking not performed - The maintenance crew consisted of a craftsman and a work supervisor. This was an ideal situation for using the peer-checking technique during the work, with the craftsman acting as the performer and the work supervisor as the peer verifying that the right actions were taken. By applying proper peer-checking, the crew should have been able to identify the proper valve for the repair work.

#### 8.	EAR PAR 04-010; Human Error during Control Rod Supply Isolation (Saint Alban unit 2, 22 April 2003)

With Saint Alban unit 2 at 100% power, routine replacement of generator brushes on control rod drive mechanisms (CRDM) was underway. The work had been finished on CRDM power supply train 1 and the electrical supply was returned to service for this train. The tagging officer had restored the electrical supply to train 1 and was about to isolate the power supply train 2. This was done in order to replace the brushes on the CRDM in this train in the early afternoon.

The tagging officer was alone when isolating power supply train 2. He followed the sequence described in the procedure. He first racked out the 6.6 kV supply, opened the cabinet for power supply train 2 in order to isolate the instrumentation and excitation breakers. At this point, he realised that he had left the required padlock in the train1 electrical supply cabinet, which was just two meters away.

The tagging officer locked out the coupling breaker in the shared cabinet located between the cabinets for CRDM power supply trains 1 and 2. He then opened the train1 supply cabinet. He was holding the isolation documents and isolation tags in place with his knee, since the documents could otherwise be scattered by the draught of air created by the CRDM power supply unit in operation. When he bent down to pick up the padlock, he unintentionally tripped a circuit breaker in power supply train1. Since he had already opened another breaker in power supply train2, the power supply to the CRDM was lost completely. This caused the control rod to drop into the core and a subsequent reactor trip. The result of the event was a 16 hour production loss.

##### Analysis

Concurrent verification technique not used - While isolating and restoring the CRDM power supply, the tagging officer used a computer-aided procedure and applied an operating instruction. The engineer was familiar with the job, which he had performed twice a year on average. He was familiar with risks and challenges associated the manipulation of CRDM power supply.

Although, the isolation of train 2 of the electrical supply was interrupted when the engineer realised that he had forgotten to remove the padlock from the train1 supply cabinet. Subsequently, a reactor scram occurred caused by the manipulation error performed by the engineer. If concurrent verification would have been applied, the likelihood of this to happen would have been decreased, since this technique emphasize on each step in a procedure or an instruction to be executed before moving to the next step. Plant procedures did not require concurrent verification for this activity.

#### 9.	EAR PAR 04-018; Unmonitored waste gas release (Bugey 4 & 5, 20 March 2003)

The Bugey NPP consists of four PWR units, arranged in pairs with unit 2 and 3 together and unit 4 and 5 together. Unit 1 is an old gas-cooled reactor currently being decommissioned. Equipment common to the whole site are denoted as unit 0 equipment, while equipment common to unit 4 and 5 is denoted as unit 9 equipment.

An equipment operator initiated a release of gaseous waste from waste gas tank 9 TEG 009 BA (a waste tank common for unit 4 & 5). The operator became doubtful that he was operating the right tank, since the tank pressure was 3 bar, while releases from this tank were normally performed at 5 bar.

He therefore made an inquiry to the control room. While checking the release form, the control room operator noticed that the wrong tank was being operated, a unit tank 9 (for unit 4 and 5) instead of a unit 0 tank (for whole site). The control room operator immediately ordered the equipment operator to halt the release, which had lasted 4 minutes.

The actual release of contaminated gas did not reach any authorised statutory limits. Although, any uncontrolled or unauthorised release of radioactivity could impair public confidence in the plant.

##### Analysis

Improper self-checking - The initial error was made by the chemistry supervisor, who mistakenly submitted to the unit 4/5 control room a unit 9 release form containing analysis results for units 4/5. Subsequently, neither the shift manager of units 4/5, nor the two shift supervisors of units 4 and 5, nor the unit 5 control room operator detected the wrong unit identification. None of these six persons involved in the handling of the documents imposed enough rigour self-checking to be able to identify that the release order contained a wrong tank.

Independent verification technique not required - The plant did not require any independent verification to be performed to check whether the release order was correct or not. Such an independent verification could have been set up with the chemistry supervisor as the performer and either of the shift manager or the shift supervisors as the verifier. Had an independent verification been applied in this situation, it is likely that the mistake with choosing the wrong tank would have been disclosed.

There are to risk involved in any release of radioactive waste. One risk is the potential release of waste that exceeds regulatory limits and the second is the fact that any uncontrolled or unauthorised release of radioactivity could impair public confidence in the plant and the industry. Therefore, release of radioactive waste is an activity that involves a significant risk for which independent verification a suitable tool to be used.

#### 10.	EAR PAR 04-053; Rector Trip during Rod Control System Power Supply Replacement (Krško, 10 August 2004)

Two instrument & control (I&C) technicians were performing troubleshooting and corrective actions of the cause of a power supply failure. The troubleshooting revealed that power supply train 1 (PS1) to the rod control system had been lost and that its function was taken over by the redundant power supply train 2 (PS2). Management decided that the malfunctioning power supply should be replaced immediately, since a subsequent loss of the PS2 would cause the plant to trip.

The I&C technicians were using a schematic diagram of the system provided by the vendor, which they had been trained by the vendor to use. However, such schematic diagrams did not provide actual conductor routes in case more wires are connected to one point and are merely suitable for troubleshooting (i.e. measuring voltage, fuses etc). During the pre-job briefing the shift personnel was notified of possible consequences of the power supply replacement (reactor trip in case of redundant supply failure).

While the technicians were removing PS1 power supply, they noticed that the terminal connection actually included two wires, which was in contrast to the schematic diagram. Although, they proceeded dismantling the power supply. When the two terminal lugs were separated, the connection for PS2 to neutral was broken. Therefore, power was lost to the rod control system thus resulting in a reactor trip.

##### Analysis

Lack of questioning attitude (non-conservative decision making) - Although the technicians noticed a strange wiring (they were confused to see additional wire), they did not stop the job to clarify the situation. They relied on the actions and statements of each other, as well as on a misleading instruction manual. A conservative decision making approach would have been to stop the work when facing a confusing situation and report the problem to their supervisor or the control room.

Use of un approved documentation - The I&C technicians followed the power cabinet schematic diagram provided by the vendor instead of using plant wiring diagram. Training at the vendor was based on these schematic diagrams rather than approved wiring diagrams. The difference, although minimal, led to the disconnection of the additional wire, thus causing a reactor trip.

Inadequate use operating experience - Krško received already in 1987 operating experience from the vendor notifying about the problems with the CRDM power supply. The OE information included warnings about possible confusion over differences between the power cabinet schematic and the power cabinet wiring diagram, which could indirectly cause a reactor trip when a plant tries to replace a power supply with the plant at power.

#### 11.	MER PAR 03-028; Target Load Value Incorrectly Set Resulting in Reactor Core Thermal Power Exceeding Operational Limitation (Daya Bay unit 1, 21 August 2003)

Daya Bay unit 1 was operating at 977 MW(e), which was slightly below the maximum electrical output of 978 MW(e). The shift crew decided to raise the electrical output slightly, after they had concluded that there was margin available to raise the thermal power. The turbine operator intended to raise unit power to 978 MW(e), but erroneously set the target load as 988 MW(e).

15 minutes later, during normal control room panel rounds, another operator discovered the error setting. The operator immediately lowered the electrical power to 979 MWe, causing the reactor core thermal power to return to below the operational limitation value of 2905 MW. The centralized data processing system (KIT) records indicated that the thermal power had increased up to 2928 MWth and the nuclear power had reached 101% of full power during the event.

The event caused the reactor core thermal power to exceed allowed limits, thus violating the Technical Specifications.

##### Analysis

Peer-checking or independent verification not performed - Adjusting the electrical output with the thermal power being close to the maximum allowed output limit is an action involving a significant risk for exceeding licensing conditions. Peer-checking is a suitable tool to use to avoid a single personal error during set-point adjustments. Independent verification would be an even stronger tool to use. Neither peer-checking, nor independent verification where required by the plant to be used during this event.

Team communication - The turbine operator did not inform the reactor operator about the electrical output change that he was about to initiate. As a result, the reactor operator failed to discover immediately that the thermal power exceeded the allowed limit.

Two minute rule - Another error prevention tool that would have been suitable to apply in this event is the ‘two minute rule’. Both the turbine operator and the reactor operated should have monitored the appropriate instrumentation and process recorders for a couple of minutes in order to verify the result of the set-point adjustment. Two minutes would have been enough in this case.

#### 12.	MER PAR 04-058; Reactor 1 Trip During Later Stages of Start-up due to Blower Speed Control Switch inadvertently remaining in the Lower position (Dungeness A unit 1, 30 May 2003)

Dungeness A unit 1 was operating at 200 MWth with one of two generators connected to the grid. Preparations were made during the night shift to raise power and to synchronise the second generator.

The shift manager noticed that the speed of one blower for reactor coolant gas had increased beyond the speed limit (1500 rpm). He directed the unit 1 reactor operator to reduce blower speed to maintain blower speed limits. The reactor operator adjusted the blower speed, but did not notice that the blower control switch became stuck in the lower direction after the adjustment. The reactor operator and a reactor operator trainee subsequently left the control room and went to an instrument room in order to adjust a ‘Guard line’ setting (part of the reactor power control logic).

Due to the stuck blower control switch, blower speed continued to decrease causing reactor core temperatures to increase. Control rods automatically inserted to reduce power and core temperatures. At a blower speed of 500 rpm, due to characteristics of the blower speed governor, a rapid increase to 770 rpm suddenly occurred resulting in adding cool gas through the reactor, thereby increasing reactor power. The control rods stopped moving in automatic mode, because the reactor gas outlet temperatures fell below the trip set-point.

At this point, the shift manager returned to the control room, saw that blower speed was at 800 rpm and believed that the blower had tripped. The shift manager also noticed that control rods were in manual with reactor core temperatures lower than normal. He subsequently assumed responsibility for operating the reactor and withdrew control rods to raise power and restore reactor core temperatures.

This action, combined with the blower speed raise, resulted in a rapid reactor power increase (35 MWth in 30 seconds). The unit 2 reactor operator subsequently closed a valve in the reactor coolant gas ductwork, since both he and the shift manager believed that the gas blower had tripped. This action, together with the previous actions, caused the reactor to trip.

##### Analysis

The root cause analysis concluded that the response of the operators to a number of situations during the event did not meet plant expectations outlined in written plant policies. Evidence was found of examples of

- actions being taken without a full understanding of plant conditions (team communication)

- a lack of conservative decision making (questioning attitude)

- a lack of anybody taking an oversight position of the activities (management and supervisory oversight)

Team communication - The unit 1 reactor operator left the control room without handing over proper information to the shift supervisor or the unit 2 reactor operator about the blower speed reduction that he had previously executed. Therefore, no one still present in control room noticed that the blower continued to reduce speed, due the stuck control switch. In addition, when the shift manager returned to the control room he started to take different actions without contacting the absent reactor operator.

Questioning attitude - The unit 1 reactor operator and the operator trainee response to the low margin alarm was to adjust margins rather than question what had caused the alarm. This took them away from the reactor controls and instruments in the control room as the transient was developing.

After arriving back to the control room the shift manager assumed, based on a temperature error indication, that the gas blower had tripped and he started to operate control rods and closing a valve in the gas coolant circuit. It was only after doing this that the shift manager and the unit 2 reactor operator mentally questioned and considered the plant status and wondered why there were no blower emergency stop valve alarms triggered on the alarm panel (such alarms would normally be present in the event of a blower trip).

Two minute rule - The characteristics of the blower speed control are such that an initial reduction in blower speed is followed by a short period in which the blower speed may stabilise or even temporarily increase. This is then followed by a prolonged reduction in blower speed. After initiating a blower speed reduction, the reactor operator did not wait long enough to notice that the blower speed continued to drop after a period of stabilisation.

Management and supervisory oversight - When the shift manager returned to the control room and noticed the low blower speed he resumed the role of the absent reactor operator and started to take different actions. This meant that the shift manager got too involved in the unit 1 reactor desk tasks without having a proper oversight of the plant status. The shift manager had been away from the control room for a while and this aggravated the situation.

##### References

- GL 2002-02, ‘Principles for Excellence in Human Performance’

- WANO Operating Experience Programme Reference Manual

- WANO document ‘Conduct of Pre-job Briefings and Post-job Debriefs’ – March 2004

- WANO document ‘Verification Techniques’ – July 2005

- GL 2001-02, ‘Guidelines for the Conduct of Operations at Nuclear Power Plants’

- GL 2003-01, ‘Guidelines for Operating Experience at Nuclear Power Plants’

##### Event reports

- EAR PAR 03-073; Exceeding the maximum allowed limit for temperature rise for the reactor vessel (Oskarshamn 3, 23 September 2003)

- EAR ATL 03-001: Incorrect Chemicals Added to Steam Generators Results in Dual-Unit Shutdown and Extended Outage (Vogtle unit 1 & 2, November 2002)

- MER ATL 04-044; Endangered Diver Prompts Manual Trip (Point Beach unit 2, 15 May 2004)

- EAR MOW 02-012; Automatic reactor scram due to a reactor operator's error (Mochovce unit 2, 2 February 2002)

- EAR MOW 03-010; Breach of plant Technical Specifications during a planned test of protection logic of essential service water pumps (Dukovany unit 1, 23 January 2002)

- EAR PAR 04-002, Removal of two fuel rod bundles around a control rod under annual maintenance (Olkiluoto unit 1,15 May 2002)

- EAR PAR 04-007; Primary Circuit Leak Rate Exceeds Tech. Spec Limits because of Maintenance on Incorrect V/V (Nogent 1, 17 April 2003)

- EAR PAR 04-010; Human Error during Control Rod Supply Isolation (Saint Alban unit 2, 22 April 2003)

- EAR PAR 04-018; Unmonitored waste gas release (Bugey 4 & 5, 20 March 2003)

- EAR PAR 04-053; Rector Trip during Rod Control System Power Supply Replacement (Krško, 10 August 2004)

- MER PAR 03-028; Target Load Value Incorrectly Set Resulting in Reactor Core Thermal Power Exceeding Operational Limitation (Daya Bay unit 1, 21 August 2003)

- MER PAR 04-058; Reactor 1 Trip During Later Stages of Start-up due to Blower Speed Control Switch inadvertently remaining in the Lower position (Dungeness A, 30 May 2003)