## Лист1
DRAFT_Section 4 ILPM (summary list of activities)
No. | Activity | Problem description | Actions | Justification | Duration, years | Priority | Division | Summary priority factor | Expert estimation of work price | Action implementation schedule. Annual work price . |  |  |  |  | ПРИМЕЧАНИЯ
[10 empty] | 20XY | 20XY+1 | 20XY+2 | 20XY+3 | 20XY+4
1 | Equipment modernization in order to eliminate safety deficiencies, fulfill validity and implementation conditions of the actions for elimination of the root causes for malfunctions in NPP operation
1.1 | NFME modernization. | 1. Impossibility to use NFME SR sensors and RCS sensors outside the reactor at refueling. 2. High difference (2-3 %) in neutron power readings at MCR hardware between NFME and ARM6M. In NFME adjusted neutron power is used, calculation algorithm of which results in difference in neutron power values between NFME and АРМ6М. It is necessary to bring calculation in both systems to a unique algorithm of neutron power calculation. 3. Poor status of cable routes in the containment. | 1.Design modification 2. Equipment delivery 3. Equipment installation 4.Equipment adjustment, testing and commissioning | Safety, reliable and efficient BNPP-1 operation | 3 | 1 | APCSD | [7 empty] | Намерения описаны в протоколе совещания по модернизации АКНП АЭС "Бушер" от 04.03.2018
1.2 | Modernization of automated individual dosimetric monitoring system AIDMS design with replacement of the control, measuring, iodine Whole-Body Counter (WBC), systems of routine and operative monitoring for external exposure, neutron exposure with the more modern ones | Design deficiencies, outdated equipment | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment | Safety, reliable and efficient AIDMS operation./for OSART Mission | 1 | 1 | RSD | [7 empty] | Заявка № 179711
1.3 | Performance of works as per post-Fukushima scenario based on stress-tests recommendations. | BNPP stress-test demonstrated the necessity to take measures for sever beyond-design-basis accidents prevention | 1. Design development 2. Equipping of places for the procured equipment connection to the Unit systems 3. Required equipment procurement (diesel-pumps, motor-pumps and etc.) 4. Installation works 5. Commissioning works | BNPP safety improvement, sever beyond-design-basis accidents prevention./for OSART Mission | 3 | 1 | ETS | [7 empty] | Заявка № 174415
1.4 | FSIV modernization – replacement of valves in FSIV binding | Design deficiencies, outdated equipment. Unreliability of signaling on FSIV binding electromagnetic valves position. Frequent faults in limit switches LS setup and failure occurrence | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Safety, reliable and efficient BNPP-1 operation, reliable SS channels operation | 2 | 1 | RC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.5 | Modernization of local-area-network I&C-TC | Low data transfer rate (10 mb/s at required up to 100 mb/s). In 2012, in the second segment of I&C-TC distant communication bus, changeover to cyclical data recording to archive was implemented. At the network throughput capacity increasing, it is possible to return to the data recording to the archive by delta function (the same as in I&C-RC) | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 1 | APCSD | [7 empty] | Частично заявка № 172777
1.6 | TLSU modernizations. Replacement of LVCD, RC, TC, workstation servers hardware with further SW replacement | Equipment outdating | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 1 | APCSD | [7 empty] | Заявка № 174596, 175833
1.7 | Modernization of SS channels initiating part with replacement of frequency signals transducer unit. | Equipment outdating | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 1 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.8 | PCR (Sapphire) sensors replacement with the sensors equipped with an interface (LCD display). | Impossibility to monitor pressure in-situ upstream and downstream of PCR. (Important parameter at the initial startup of the pump units and at changeovers by Н/а) | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 1 | 1 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании. Есть в планах работ по модернизации у ТО и АСУТП.
1.9 | Modernization of mechanical quantity control system. | MC failure in the measuring transducers . | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 1 | 1 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.10 | Modernization of starting air electrical compressor control console (DGP ACS SAEC CC ) in buildings ZK1, ZK2, ZK3- AKZ MCR (11LXT62, 11LXT63, 12LXT72, 12LXT73, 13LXT82, 13LXT83, 14LXT92, 14LXT93, 10LUQ62, 10LUQ63) | Design deficiencies, outdated equipment, SPTA unavailability | Develop, manufacture and replace standard SAEC CC with the new ones operating under SIEMENS SIMATIC PLC control | Modernization of SAEC CC (DGP ACS) using «Simatic» company equipment. Safety, reliable and efficient BNPP-1 operation | 2 | 1 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.11 | Time synchronization of all events recorders with the common time of BNPP unit No. 1 | Impossible to accurately analyze the events taken place | 1. Design modification 2. Equipment manufacturing, delivery and installation 3. Installation operations 4. Equipment adjustment 5. Programming | Safety, reliable and efficient BNPP-1 operation. | 1 | 2 | EED | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.12 | Modernization of in-core instrumentation system ICIS servers (top level computing complex TL-CC , comprehensive analysis system (CAS) | Outdated equipment, technical failures, unavailability of data monitoring and displaying station at MCR (independent direct formats of ICIS TL-CC) | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 3 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании. Уточнить тематику в РусАС
1.13 | Modernization of BNPP special equipment set КСО.002-51 Operation Manual eF3.049.020-51RE | Outdated equipment, SPTA unavailability | 1. Dismantling and installation works 2. Programming 3. ACS setup | Modernization of КСО.002-51 for BNPP AFPS using “TENZOR” company equipment. Safety, reliable and efficient BNPP-1 operation | 3 | 1 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.14 | Modernization of parameters displaying equipment PDE within EP-PP SCS, ESFIP | Outdated equipment, poor accessibility for the users, high labor-intensity at event archives unloading, small volume of memory for events logging, insufficient time interval for the data recording and analysis | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment, testing, commissioning | Safety, reliable and efficient PDE operation within EP-PP SCS, ESFIP | 3 | 3 | APCSD | [7 empty] | Заявка № 176754
1.15 | Modernization. Improvement of existing headers of boron-containing water tanks TD11,12,13B001 in such a way, that it shall become possible to use one header for inflow to the tank and another header shall be used for discharge from the tank. | Boron-containing water tanks TD11,12,13B001 and distillate tanks TD14,15,16B001 have common inflow and discharge headers, that does not eliminate the possibility of accidental ingress of condensate and liquid coolant solution with concentration less than permitted to the primary coolant. The possibility of simultaneous inflow of boric acid solution with different concentration to different tanks is unavailable . | 1. Flywheels of valves row (TD11S002, TD12S002, TD13S002, TD14S003, TD15S003, TD16S003) are closed with chains and locks, and safety tags are placed «Do not open – danger of accident». 2. Design development and implementation. | Elimination of the possibility for ingress of condensate and liquid coolant solution with concentration less than permitted to the primary coolant as the result of the faulty actions of personnel. | 3 | 1 | CHEM | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.16 | Modernization. Transfer of distillate tank TD14(15,16)B001 to boron-containing water tanks and installation of one (two) TD system distillate tanks outside ZC building. | Difficulties in TD system operation occur in different reactor plant modes: 1. Lack of volume at water exchange without evaporator activation; 2. Lack of volume in tanks at the end of the life cycle; 3. possibility for simultaneous processing of boric acid solution and operation of pumps TD21,22D001 at cool-down is unavailable; | 1. Design correction related to distillate tank TD14(15,16)B001 transfer for coolant receiving. 2. Design development for installation of one (two) tanks outside ZC building for distillate storage and discharge; 3. Designs implementation. 4. Equipment setup. 5. Testing | Sufficiency of volumes at different operation modes of the reactor plant. Provision of conditions for normal operation of the evaporator and TD system as a whole. | 3 | 1 | CHEM | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
1.17 | Work performance as per scenario of UPH flooding at damaging the pipelines inside the structure according to stress-tests recommendations. | UPH structure is designed so that all pumps and motors are below gulf water level. Such equipment layout chart remained from initial German design. The possibility of safety systems (elements) failure at UPH flooding exists. | 1. Carry-out of additional stress-tests regarding UPH with assessment of the plant safety and consequences in case of safety functions loss due to flooding . 2. By stress-tests results, develop design solutions for UPH protection against flooding. 3. Design solutions implementation (CIW and CW). | Safety, reliable and efficient BNPP-1 operation, reliable SS channels operation | 2 | 1 | TC
1.18 | Installation of the device for primary circuit boron-containing water cleaning from colloid ferrum | At SFP operation in refueling mode, colloid ferrum is generated in the coolant. The existing SFP water treatment systems do not remove the colloid ferrum. | 1. Design modification. 2. Equipment procurement and delivery 3. Installation operations 4. Commissioning works | Improvement of BNPP-1 operation safety and efficiency | 2 | 1 | RC
2 | Equipment lifetime management during design and extended lifetime of the Units.
2.1 | Modernization of loose parts detection systems and vibration monitoring system LPDS, VMS (software and equipment) | Defects repetition (application software ASW and equipment), incorrect and unreliable operation of the systems | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation | 1,5 year | 1 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
2.2 | Reconstruction of turbine HPC and LPC1,2,3 steam sealing system SG. | Poor operation pf HPC end seals causing oil watering and end seals wear-out | 1.Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency | 2 | 1 | TC | [7 empty] | Заявка № 180976
2.3 | Pressure gauges installation on the pipelines of inlet and discharge nozzles of pump units RN13,23D001. | Complete unavailability of monitoring for pump units parameters | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
2.4 | Installation of forced ventilation in CPSE-ESFIP cabinets | Modules vigorous heating resulting in modules and units failures. | 1.Equipment development, manufacturing and delivery 2.Temperature mode setup, testing, commissioning | Safety, reliable and efficient CPSE-ESFIP operation | 2 | 2 | APCSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании. Уточнить у Лазбы и Дударя не повторяется ли п. 1.7
2.5 | MA communication system modernization | MZ standby radio communication system, which is being implemented at BNPP as per AEP design, does not ensure required coverage area and radio communication quality over walkdown routes and in the rooms specified in the table of clients No. RPT-1030-01. Perform modernization of common-plant telecommunication system MA equipment relatively MA system further equipping with wireless DECT-standard telecommunication. | 1. Design modification. 2. Equipment procurement and delivery 3. Dismantling, installation activities 4. CW | Safety, reliable and efficient BNPP-1 operation | 2 | 2 | APCSD | [7 empty] | Заявка № 168696
2.6 | Installation of events registers at the auxiliary sections | At present no ample and complete information for events analyses available | 1. Design formation 2. Equipment manufacturing, delivery and installation 3. Installation operations 4. Equipment adjustment 5. Programming | Reliable and efficient BNPP-1 operation | 2 | 2 | EED | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
2.7 | Adding of registration parameters to the generator emergency events recorder | Impossibility to increase the number of registration analog signals | 1. Design modification 2. Equipment delivery, installation 3. Equipment setup 4. Programming | Reliable and efficient BNPP-1 operation | 2 | 2 | EED | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
2.8 | Modernization. Chemicals supply for TR, TD, TG and TC systems filters regeneration. | Ion-exchange charge of TR, TD, TG and TC system filters loose exchanging capacity within shorter (2-3 years) service life than it is established by the design (4-8 years), that causes forced replacement of the ion-exchange charge. Ion-exchange charge replacement in IRI is very complicated and expensive. | 1. 1. Designs correction related to supply of regeneration solutions to the filters. 2. 2. Development of the neutralizing unit design. 3. 3. Development of the design for nitric acid storage and supply unit. 4. Design implementation. 5. Equipment setup. 6. Testing. | Use of ion-exchange charge of the filters within its whole design service life, and within over-design service life at in-service monitoring for its physical-and-chemical characteristics. Reducing of amount of radioactive spent sorbents ingress to tanks ТС31,32В001 and, as the result, generated LRW reducing. Significant reducing of the number of the containers designed for long-term storage or burial of the utilized RW . | 3 | 1 | CHEM | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
2.9 | Surveillance-specimens testing with a view to extend RV lifetime | Additional tasks for SS testing in NRC KI 1) Unavailability of the programme for reactor vessel SS testing; 2) Unavailability of the certificate for RV SS container design and transportation; 3) Unavailability of the testing jig for testing the device for SS removal and transportation | 1. Implementation of protocols on SS transportation and development of the programme for SS testing, transportation routes agreeing 2. Design implementation (SS unloading, transportation to NRC KI, investigation performance, container returning). | Fulfillment of regulatory documentation requirements. Reactor vessel metal state assessment. Preparation for lifetime period extension. | 2 | 2 | TPD
3 | Modernization for equipment operation reliability and resistance improvement (losses prevention).
3.1 | Tank installation for pumps SL11(12,13)D001 suctions cooling at the common manifold of steam-air mixture suck-out from the turbine condensers. | Increased SAM temperature in summer season and at vacuum development. | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 2 | 1 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.2 | Secondary circuit ACM-2 system modernization | Poor system functioning during operation period. Readings deviations from accurate values. | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 2 | 1 | TC | [7 empty] | Заявка № 162968 Предложение Румянцева А.П. удалить тему.
3.3 | Modernization of steam supply system to SSC, replacement of control valves RF82.83S801 | SSC poor operation causing inadequate steam pressure regulation in steam supply line to the seals | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 2 | 1 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.4 | Modernization of turbine control system. Changeover to Diakont TG control system | Unification and possibility to affect the unstable frequency of IRI Grid. The existing control system does not allow the Unit to operate in frequency control maintaining mode in IRI Grid. | 1. Design modification. 2. Equipment procurement and delivery 3. Dismantling and installation works 4. Commissioning works | Reliable IRI grid operation improvement. Improvement of TG operation parameters maintaining accuracy. Improvement of BNPP-1 operation reliability and efficiency. | 3 | 1 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.5 | Elaboration and implementation of air supply circuit to SG for monitoring of SG pipe heater leak tightness. | For inspection of intercircuit leak tightness of the SG pipe heater pneumohydraulic aquarial method is used according to 446.05 RE (part 1, chapter 14). Circuit decision of using this method was not stipulated in the design. | For the possibility of air (nitrogen) supply into the SG housing from the NPP standard systems a design shall be developed and jumper bar between systems ТМ11 (drainage ТМ11S044 or ТМ11S047) and RZ53 (drainage RZ53S016) in room А0507 installed. | The possibility of SG pipe heater leak tightness monitoring during PPM | 1 | 1 | RC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.6 | Check valve installation downstream of RG16S001,801,803 with bypass line. | Liquid back flow prevention | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 2 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.7 | Interconnection of lines RG16 and RM81÷85 (PC supply to deaerator nozzles). | Prevent deaerator RG16 nozzle overloading by separated liquid flow-rate | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 2 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.8 | Control valves RG16,30S801 replacement with the type "butterfly" or another type as per reliability . | Unstable operation in low flow-rate modes | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.9 | Automatic changeover to pumpless discharge RG14B001 at load shedding 30% and less. Optimize CV automatics operation at load shedding up to 50% | At load shedding up to 50%, CV regulator control algorithm does not perform RG14B001 level monitoring and control function, as the result, the control valve on HSC discharge line to the condenser opens completely without monitoring for position of HSC discharge regulator to the deaerator, that drastically affects pump units operation and can cause their trip by level decreasing in RG14B001. | 1. Design modification 2. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.10 | Automatic changeover to pumpless discharge of HSC LPH3 RH13,23B001 at load shedding 30% and less. Optimize CV control automatics at load shedding | Al load shedding up to 30% and less, HSC boiling occurs, as the result quick level increasing takes place (the regulator shall monitor HSC temperature, pressure in LPH steam part). | 1. Design modification 2. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.11 | Modernization of medium water-distribution unit (in respect of beams improvement) of cationite regeneration filter UB94B001 in building ZF. | In the course of ion-exchange material hydraulic reloading process operations from UDP filters to cationite regeneration filter (CRF) UB94B001 drainage elements destruction occurred (detachment of elements casings from the bedplates and connection pipes from the manifold), destruction of weld joint and distribution manifold detachment from regeneration filter casing, and, as a result, manifold displacement and beams detachment. On the advice and technologies of the manufacturer reinforcement of CRF water-distribution unit common manifold has been performed but ion-exchange material partial carryover occurs that causes decrease of UDP filters filtering bed levels . | 1. Inquiry to produce different versions of improved water-distribution unit beams was addressed to JSC “LTVO”. 2. Supply improved water-distribution unit beams. 3. Install and test. | Reliable and efficient operation, ion-exchange material carryover is unavailable. | 1 | 2 | CHEM | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.12 | Installation of exhausters (oil) at RL12,22,32D001; RМ11,12,13D001; VC10-40D001 | Due to numerous defects related to leakages in the bearing units connections, coupling covers and multiplier, mostly owing to oil vapors pressure as well as oil vapors ingress via the air breather to the turbine hall, electric motor and condensed oil flow down on half-couplings covers over the breathers. | 1. Design development 2. Installation works 3.Commissioning works | Removal of oil leakages, oil vapors ingress to electric motor and to the atmosphere. | 2 | 2 | TC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.13 | Elaboration and implementation of DW pump out circuit from tanks RS10-40B001 to CWT for purification | Deterioration of water quality in emergency feed water storage tanks RS10-40B001. A circuit of RS tanks draining to UL sump of its SS channel is implemented as well as pumping over from the sump by pumps UL21,22,23,24D001 to ZX for CWT provided that sump water analysis results are satisfactory. | For the possibility of water purification at CWT plants in building ZG0 DW pump out circuit from tanks RS10-40B001 to CWT bypassing UL sumps shall be implemented . | The possibility of emergency feed water purification | 3 | 1 | RC | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
3.14 | "Robot" implementation for MCC inspection after repair to make sure in unavailability of extraneous items | Impossibility of MCC visual inspection after repair to make sure in unavailability of extraneous items | 1. Design modification. 2. Equipment procurement and delivery 3. Commissioning works | FA operation safety improvement. In case of inspection necessity - personnel dose burdens reducing. Improvement of BNPP-1 operation reliability and efficiency. | 2 | 2 | RC
3.15 | Modernization of 38-СК016М monitoring system | Moral and physical equipment ageing | 1. Design modification. 2. Equipment procurement and delivery 3. Installation works 4. Commissioning works | PPM performance period reducing due to the system failures reducing . Power generation increasing at existing BNPP Unit | 3 | 2 | RC
4 | Modernization for the purposes of power saving, commercial efficiency improvement and power generation increasing at existing NPP Units.
4.1 | Modernization of the current path with SF6 gas insulation (installation of disconnectors and groundings in the side of transformers 10АТ01, 10АТ02, 10AS01,AS02 HV winding as well as to the direction of the current paths | At present it is impossible to provide electric circuit reliability to secure power and the unit transformers all measurements and tests performance | 1. Modification of 400 kV GIS design 2. Elaboration of work performance project 3. Installation operations | Power generation increasing at existing BNPP Unit | 2 | 2 | EED | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
4.2 | BNPP ABH modernization | The existing equipment makes efficient ABH operation at low power levels impossible, thus causing significant overconsumption of fuel. The boiler is purchased: manufacturer – Tehran. Total steam capacity - 8 t/h (1 per Deaerator and 7 per AC). Boiler type: FireTube Full Wet Wake. Fuel: gas or DF. | 1. Design modification 2. Dismantling and installation works 3. Adjustment | BNPP ABH modernization shall result in saving and efficient BNPP-1 operation | 2 | 3 | CPED | [7 empty] | Котел поставлен на площадку, но работы больше не производились.
4.3 | Use of isolating devices in SG headers during PPM | SG HET ECT and ECD performance is possible only at low level in the reactor and coolant unavailability in SG headers. These conditions impose prohibition to FA reloading and as the result cause necessity to perform these works sequentially excluding combining. This shall extend PPM duration. | 1. Design and OI modification 2. Equipment procurement and delivery 3. Equipment adjustment | PPM duration reducing. Power generation increasing at existing BNPP Unit | 1 | 1 | RC
4.4 | Implementation of rapid containment testing method | Long-term containment testing. | 1. Design and OI modification 2. Equipment procurement and delivery 3. Equipment installation 4. Equipment adjustment | PPM duration reducing. Power generation increasing at existing BNPP Unit | 1 | 1 | RC
4.5 | Modernization of SSC chilling machines and cold supply system | Inadequate and inefficient CM operation at low temperatures of outer air and seawater. | 1.Design modification. 2. Equipment procurement and delivery 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and safety. Obtaining additional CM redundancy. | 2 | 2 | V&ACD
5 | Modernization of RW and SF handling equipment
5.1 | Provision of radiation monitoring in ventilation systems TL03,TL13,TL02,TL33 | Unavailability of monitoring for radioactive materials release through these systems | 1.Design development 2. Installation works | Safety NPP operation, monitoring for releases to the vent stack/ for OSART Mission | 1 year | 1 | RSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
5.2 | Provision of monitoring for gas blowers operation | Unavailability of information on gas-blowers operation at RMB for the operative personnel | 1.Design development 2. Installation works | Monitoring for releases to the environment and situation in rooms and equipment /for OSART Mission | 2 | 1 | RSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
5.3 | Modernization. Installation of flow-meters 10TR10F501, 10TR10F503, 10TR10F504, 10TR10F506 at radioactive drains intake pipelines from buildings ZA/ZB, ZC. | Impossibility to monitor and record radioactive drains inflow to radioactive drains tanks TR11,12B001 | 1. 1.) Design correction related to indication of flow-rate measurements readings at MCR-NCA jointly with correction related to flow-meters installation at special sewage drains from buildings ZA/ZB and its implementation. 2. Equipment adjustment. 3. Testing. | Monitoring for radioactive drains inflow and LRW accounting, radioactive wastes minimization /for OSART Mission | 2 | 1 | CHEM | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
5.4 | Installation of the second gas-blower in TV90 system with the common header. Taking into account the walks-down, equipment inspections in ZA, as well as radiation situation monitoring during accident propagation | During withdrawal for repair, monitoring in ZA becomes impossible. Introduce modifications to pulsed lines routing and medium sampling points . | 1.Design development 2. Installation works | Radiation situation monitoring in ZA at NO and during accident propagation | 2 | 1 | RSD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
5.5 | Modernization. Installation of TR system radioactive drains pretreatment unit. | Different insoluble mechanical impurities ingress to the special sewage system via floor drains of the controlled-access area rooms (mainly, these are decontaminating detergents, washouts from the floors, corrosion products). Besides, in compliance with the technology of loosening cleanups of TD, TG, TC, TR, UZ systems filters, ion-exchange sorbents fines are washed to radioactive drains receiving system with further ingress to the vat residue after radioactive drains water treatment at TR system evaporators. And, as a result, non-operability of TT system LRW treatment unit due to the filter and orifices periodic clogging. | 1. Development of waste waters pretreatment unit design in respect of centrifuge installation on the waste waters receiving pipeline. 2. Design implementation. 3. Equipment adjustment. 4. Testing. | Effective and trouble-free waste water pretreatment unit from mechanical coarse particles etc. Operability of TT system LRW treatment system. | 3 | 3 | CHEM | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
5.6 | Refueling machine (RM) modernization, including RM surveillance system | Failures in Tenore NT program operation due to moral and physical ageing of computing complexes Oper 1, Oper 2 (manufacture of 1999). | 1. Send a letter to ZAO ASE. 2. Replacement of computer complexes Oper 1, Oper 2. 3. Adjustment, debugging and testing of Tenore NT program operation. | 1. Enhancement of refueling safety. 2. Prevention of probable shutdowns. | 2 | 2 | TTD | [7 empty] | Работы не охвачены заявками, и не производились на оборудовании.
5.7 | Implementation of individual SFA storage for regular shipment to RF | Unavailability of storage for SFA, except for SFP, causes safety deficiency, in case of SFP failure or damaging. A place in SFP for SFA unloading from the reactor is required. | 1.Design development. 2. Civil works. 3. Equipment procurement and delivery 4. Installation works 5. Commissioning works | SFA shipment to RF without correlating with the Unit PPM. Use of storage for BNPP-2 Units . | 4 | 2 | NS&FS | [7 empty] | Бюджета СК не достаточно для реализации данного проекта.
6 | Renovation and modernization of NPP equipment and facilities of supporting, information-and-process and transportation purpose.
6.1 | Modernization of offshore zone physical protection | Moral and physical ageing of equipment and as the result safety deficiency formation. | 1. Existing equipment inspection 2. Design modification by inspection results 3. Equipment procurement and delivery 4. Dismantling and installation works 5. Commissioning works | Safety improvement as the result of reliable and efficient BNPP-1 operation. | 2 | 1 | PPS

## Лист1 (2)
List of modernization topics
No. | Activity | Problem description | Actions | Justification | Duration | Priority | Division | Итоговый коэффициент приоритетности | Общая стоимость работ | График реализации мероприятия. Годовая стоимость работ.
[10 empty] | 20XY | 20XY+1 | 20XY+2 | 20XY+3 | 20XY+4
1 | МEquipment modernization in order to eliminate safety deficiencies, fulfill validity and implementation conditions of the actions for elimination of the root causes for malfunctions in NPP operation.
2 | Equipment lifetime management during design and extended lifetime of the Units.
3 | Modernization for equipment operation reliability and resistance improvement (losses prevention).
4 | Modernization for the purposes of power saving, commercial efficiency improvement and power generation increasing at existing NPP Units.
5 | Modernization of RW and SF handling equipment
6 | Renovation and modernization of NPP equipment and facilities of supporting, information-and-process and transportation purpose.
1 | Modernization of loose parts detection systems and vibration monitoring system LPDS, VMS (software and equipment) | Defects repetition (application software ASW and equipment), incorrect and unreliable operation of the systems | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation | 1,5 year | 1 | APCSD | [7 empty] | 2
2 | NFME modernization. | 1. Impossibility to use NFME SR sensors and RCS sensors outside the reactor at refueling. 2. High difference (2-3 %) in neutron power readings at MCR hardware between NFME and ARM6M. In NFME adjusted neutron power is used, calculation algorithm of which results in difference in neutron power values between NFME and АРМ6М. It is necessary to bring calculation in both systems to a unique algorithm of neutron power calculation. 3. Poor status of cable routes in the containment. | 1.Design modification 2. Equipment delivery 3. Equipment installation 4.Equipment adjustment, testing and commissioning | Safety, reliable and efficient BNPP-1 operation | 2-3 years | 1 | APCSD | [7 empty] | 1
3 | Provision of radiation monitoring in ventilation systems | Unavailability of monitoring for radioactive materials release through these systems | 1.Design development 2. Installation works | Safety NPP operation, monitoring for releases to the vent stack/ for OSART Mission | 1 year | 1 | RSD | [7 empty] | 5
4 | Modernization of automated individual dosimetric monitoring system AIDMS design with replacement of the control, measuring, iodine Whole-Body Counter (WBC), systems of routine and operative monitoring for external exposure, neutron exposure with the more modern ones | Design deficiencies, outdated equipment | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment | Safety, reliable and efficient AIDMS operation./for OSART Mission | 1 year | 1 | RSD | [7 empty] | 1
5 | Tank installation for pumps SL11(12,13)D001 suctions cooling at the common manifold of steam-air mixture suck-out from the turbine condensers. | Increased SAM temperature in summer season and at vacuum development. | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 2 | 1 | TC | [7 empty] | 3
6 | Secondary circuit ACM-2 system modernization | Poor system functioning during operation period. Readings deviations from accurate values. | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 2 | 1 | ТО | [7 empty] | 3
7 | Reconstruction of turbine HPC and LPC1,2,3 steam sealing system SG. | Poor operation pf HPC end seals causing oil watering and end seals wear-out | 1.Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency | 2 | 1 | TC | [7 empty] | 2
8 | Modernization of steam supply system to SSC, replacement of control valves RF82.83S801 | SSC poor operation causing inadequate steam pressure regulation in steam supply line to the seals | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 2 | 1 | TC | [7 empty] | 3
9 | Modernization of turbine control system. | Unification and possibility to affect the unstable frequency of IRI Grid. | 1. Design modification. 2. Equipment procurement and delivery 3. Dismantling and installation works 4. Commissioning works | Improvement of BNPP-1 operation reliability and efficiency. | 3 | 1 | TC | [7 empty] | 3
10 | Elaboration and implementation of air supply circuit to SG for monitoring of SG pipe heater leak tightness. | For inspection of intercircuit leak tightness of the SG pipe heater pneumohydraulic aquarial method is used according to 446.05 RE (part 1, chapter 14). Circuit decision of using this method was not stipulated in the design. | For the possibility of air (nitrogen) supply into the SG housing from the NPP standard systems a design shall be developed and jumper bar between systems ТМ11 (drainage ТМ11S044 or ТМ11S047) and RZ53 (drainage RZ53S016) in room А0507 installed. | The possibility of SG pipe heater leak tightness monitoring during PPM | 1 | 1 | RC | [7 empty] | 3
11 | Performance of works as per post-Fukushima scenario based on stress-tests recommendations. | BNPP stress-test demonstrated the necessity to take measures for sever beyond-design-basis accidents prevention | 1. Design development 2. Equipping of places for the procured equipment connection to the Unit systems 3. Required equipment procurement (diesel-pumps, motor-pumps and etc.) 4. Installation works 5. Commissioning works | BNPP safety improvement, sever beyond-design-basis accidents prevention./for OSART Mission | 3 | 1 | ETS | [7 empty] | 1
12 | FSIV modernization – replacement of valves in FSIV binding | Design deficiencies, outdated equipment. Unreliability of signaling on FSIV binding electromagnetic valves position. Frequent faults in limit switches LS setup and failure occurrence | 1. Design modification. 2. Equipment modernization 3. Dismantling and installation works 4. Commissioning works | Safety, reliable and efficient BNPP-1 operation, reliable SS channels operation | 2 | 1 | RC | [7 empty] | 1
13 | Check valve installation downstream of RG16S001,801,803 with bypass line. | Liquid back flow prevention | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 2 | 2 | TC | [7 empty] | 3
14 | Interconnection of lines RG16 and RM81÷85 (PC supply to deaerator nozzles). | Prevent deaerator RG16 nozzle overloading by separated liquid flow-rate | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 2 | 2 | TC | [7 empty] | 3
15 | Control valves RG16,30S801 replacement with the type "butterfly" or another type as per reliability . | Unstable operation in low flow-rate modes | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | 3
16 | Automatic changeover to pumpless discharge RG14B001 at load shedding 30% and less. Optimize CV automatics operation at load shedding up to 50% | At load shedding up to 50%, CV regulator control algorithm does not perform RG14B001 level monitoring and control function, as the result, the control valve on HSC discharge line to the condenser opens completely without monitoring for position of HSC discharge regulator to the deaerator, that drastically affects pump units operation and can cause their trip by level decreasing in RG14B001. | 1. Design modification 2. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | 3
17 | Automatic changeover to pumpless discharge of HSC LPH3 RH13,23B001 at load shedding 30% and less. Optimize CV control automatics at load shedding | Al load shedding up to 30% and less, HSC boiling occurs, as the result quick level increasing takes place (the regulator shall monitor HSC temperature, pressure in LPH steam part). | 1. Design modification 2. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | 3
18 | Pressure gauges installation on the pipelines of inlet and discharge nozzles of pump units RN13,23D001. | Complete unavailability of monitoring for pump units parameters | 1. Design modification 2. Equipment delivery 3. Installation works 4. Equipment adjustment | Reliable and efficient system operation. | 1 | 2 | TC | [7 empty] | 2
19 | Modernization of local-area-network I&C-TC | Low data transfer rate (10 mb/s at required up to 100 mb/s). In 2012, in the second segment of I&C-TC distant communication bus, changeover to cyclical data recording to archive was implemented. At the network throughput capacity increasing, it is possible to return to the data recording to the archive by delta function (the same as in I&C-RC) | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 1 | APCSD | [7 empty] | 1
20 | TLSU modernizations. Replacement of LVCD, RC, TC, workstation servers hardware with further SW replacement | Equipment outdating | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 1 | APCSD | [7 empty] | 1
21 | Modernization of SS channels initiating part with replacement of frequency signals transducer unit. | Equipment outdating | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 1 | APCSD | [7 empty] | 1
22 | PCR (Sapphire) sensors replacement with the sensors equipped with an interface (LCD display). | Impossibility to monitor pressure in-situ upstream and downstream of PCR. (Important parameter at the initial startup of the pump units and at changeovers by Н/а) | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 1 | 1 | APCSD | [7 empty] | 1
23 | Modernization of mechanical quantity control system. | MC failure in the measuring transducers . | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 1 | 1 | APCSD | [7 empty] | 1
24 | Modernization of starting air electrical compressor control console (DGP ACS SAEC CC ) in buildings ZK1, ZK2, ZK3- AKZ MCR (11LXT62, 11LXT63, 12LXT72, 12LXT73, 13LXT82, 13LXT83, 14LXT92, 14LXT93, 10LUQ62, 10LUQ63) | Design deficiencies, outdated equipment, SPTA unavailability | Develop, manufacture and replace standard SAEC CC with the new ones operating under SIEMENS SIMATIC PLC control | Modernization of SAEC CC (DGP ACS) using «Simatic» company equipment. Safety, reliable and efficient BNPP-1 operation | 2 | 1 | APCSD | [7 empty] | 1
25 | Installation of forced ventilation in CPSE-ESFIP cabinets | Modules vigorous heating resulting in modules and units failures. | 1.Equipment development, manufacturing and delivery 2.Temperature mode setup, testing, commissioning | Safety, reliable and efficient CPSE-ESFIP operation | 2 | 2 | APCSD | [7 empty] | 2
26 | Provision of monitoring for gas blowers operation | Unavailability of information on gas-blowers operation at RMB for the operative personnel | 1.Design development 2. Installation works | Monitoring for releases to the environment and situation in rooms and equipment /for OSART Mission | 2 | 2 | RSD | [7 empty] | 5
27 | Modernization. Installation of flow-meters 10TR10F501, 10TR10F503, 10TR10F504, 10TR10F506 at radioactive drains intake pipelines from buildings ZA/ZB, ZC. | Impossibility to monitor and record radioactive drains inflow to radioactive drains tanks TR11,12B001 | 1. 1.) Design correction related to indication of flow-rate measurements readings at MCR-NCA jointly with correction related to flow-meters installation at special sewage drains from buildings ZA/ZB and its implementation. 2. Equipment adjustment. 3. Testing. | Monitoring for radioactive drains inflow and LRW accounting, radioactive wastes minimization /for OSART Mission | 2 | 1 | CHEM | [7 empty] | 5
28 | BNPP secondary circuit water chemistry implementation and pilot operation with corrective treatment of the operating medium with monoethanolamin | Increased content of Fe oxides in the secondary circuit at ammonia-and-hydrazine mode causes frequent regenerations of AWT filters and increased chemicals flow-rate | 1. BNPP design correction 2. Works project development 3. Installation works | Safety, reliable and efficient BNPP operation. Reducing of chemicals consumption | 2 | 2 | CHEM | [7 empty] | 2
29 | Modernization of medium water-distribution unit (in respect of beams improvement) of cationite regeneration filter UB94B001 in building ZF. | In the course of ion-exchange material hydraulic reloading process operations from UDP filters to cationite regeneration filter (CRF) UB94B001 drainage elements destruction occurred (detachment of elements casings from the bedplates and connection pipes from the manifold), destruction of weld joint and distribution manifold detachment from regeneration filter casing, and, as a result, manifold displacement and beams detachment. On the advice and technologies of the manufacturer reinforcement of CRF water-distribution unit common manifold has been performed but ion-exchange material partial carryover occurs that causes decrease of UDP filters filtering bed levels . | 1. Inquiry to produce different versions of improved water-distribution unit beams was addressed to JSC “LTVO”. 2. Supply improved water-distribution unit beams. 3. Install and test. | Reliable and efficient operation, ion-exchange material carryover is unavailable. | 1 | 2 | CHEM | [7 empty] | 3
30 | Modernization of the current path with SF6 gas insulation (installation of disconnectors and groundings in the side of transformers 10АТ01, 10АТ02, 10AS01,AS02 HV winding as well as to the direction of the current paths | At present it is impossible to provide electric circuit reliability to secure power and the unit transformers all measurements and tests performance | 1. Modification of 400 kV GIS design 2. Elaboration of work performance project 3. Installation operations | Power generation increasing at existing BNPP Unit | 2 | 2 | EED | [7 empty] | 4
31 | Installation of events registers at the auxiliary sections | At present no ample and complete information for events analyses available | 1. Design formation 2. Equipment manufacturing, delivery and installation 3. Installation operations 4. Equipment adjustment 5. Programming | Reliable and efficient BNPP-1 operation | 2 | 2 | EED | [7 empty] | 2
32 | Adding of registration parameters to the generator emergency events recorder | Impossibility to increase the number of registration analog signals | 1. Design modification 2. Equipment delivery, installation 3. Equipment setup 4. Programming | Reliable and efficient BNPP-1 operation | 2 | 2 | EED | [7 empty] | 2
33 | Time synchronization of all events recorders with the common time of BNPP unit No. 1 | Impossible to analyze accurately the events taken place | 1. Design modification 2. Equipment manufacturing, delivery and installation 3. Installation operations 4. Equipment adjustment 5. Programming | Safety, reliable and efficient BNPP-1 operation. | 1 | 2 | EED | [7 empty] | 1
34 | Installation of exhausters (oil) at RL12,22,32D001; RМ11,12,13D001; VC10-40D001 | Due to numerous defects related to leakages in the bearing units connections, coupling covers and multiplier, mostly owing to oil vapors pressure as well as oil vapors ingress via the air breather to the turbine hall, electric motor and condensed oil flow down on half-couplings covers over the breathers. | 1. Design development 2. Installation works 3.Commissioning works | Removal of oil leakages, oil vapors ingress to electric motor and to the atmosphere. | 2 | 2 | TC | [7 empty] | 3
35 | Elaboration and implementation of DW pump out circuit from tanks RS10-40B001 to CWT for purification | Deterioration of water quality in emergency feed water storage tanks RS10-40B001. A circuit of RS tanks draining to UL sump of its SS channel is implemented as well as pumping over from the sump by pumps UL21,22,23,24D001 to ZX for CWT provided that sump water analysis results are satisfactory. | For the possibility of water purification at CWT plants in building ZG0 DW pump out circuit from tanks RS10-40B001 to CWT bypassing UL sumps shall be implemented . | The possibility of emergency feed water purification | 3 | 1 | RC | [7 empty] | 3
36 | BNPP ABH modernization | The existing equipment makes efficient ABH operation at low power levels impossible, thus causing significant overconsumption of fuel. T | 1. Design modification 2. Dismantling and installation works 3. Adjustment | BNPP ABH modernization shall result in saving and efficient BNPP-1 operation | 2 | 3 | CPED | [7 empty] | 4
37 | Modernization of in-core instrumentation system ICIS servers (top level computing complex TL-CC , comprehensive analysis system (CAS) | Outdated equipment, technical failures, unavailability of data monitoring and displaying station at MCR (independent direct formats of ICIS TL-CC) | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment 4. Programming | Safety, reliable and efficient BNPP-1 operation. | 2 | 3 | APCSD | [7 empty] | 1
38 | Modernization of BNPP special equipment set КСО.002-51 Operation Manual eF3.049.020-51RE | Outdated equipment, SPTA unavailability | 1. Dismantling and installation works 2. Programming 3. ACS setup | Modernization of КСО.002-51 for BNPP AFPS using “TENZOR” company equipment. Safety, reliable and efficient BNPP-1 operation | 3 | 1 | APCSD | [7 empty] | 1
39 | Modernization of parameters displaying equipment PDE within EP-PP SCS, ESFIP | Outdated equipment, poor accessibility for the users, high labor-intensity at event archives unloading, small volume of memory for events logging, insufficient time interval for the data recording and analysis | 1. Design modification. 2. Equipment manufacturing, delivery and installation 3. Equipment adjustment, testing, commissioning | Safety, reliable and efficient PDE operation within EP-PP SCS, ESFIP | 3 | 3 | APCSD | [7 empty] | 1
40 | Installation of the second gas-blower in TV90 system with the common header. Taking into account the walks-down, equipment inspections in ZA, as well as radiation situation monitoring during accident propagation | During withdrawal for repair, monitoring in ZA becomes impossible. Introduce modifications to pulsed lines routing and medium sampling points . | 1.Design development 2. Installation works | Radiation situation monitoring in ZA at NO and during accident propagation | 2 | 1 | RSD | [7 empty] | 5
41 | Modernization. Improvement of existing headers of boron-containing water tanks TD11,12,13B001 in such a way, that it shall become possible to use one header for inflow to the tank and another header shall be used for discharge from the tank. | Boron-containing water tanks TD11,12,13B001 and distillate tanks TD14,15,16B001 have common inflow and discharge headers, that does not eliminate the possibility of accidental ingress of condensate and liquid coolant solution with concentration less than permitted to the primary coolant. The possibility of simultaneous inflow of boric acid solution with different concentration to different tanks is unavailable . | 1. Flywheels of valves row (TD11S002, TD12S002, TD13S002, TD14S003, TD15S003, TD16S003) are closed with chains and locks, and safety tags are placed «Do not open – danger of accident». 2. Design development and implementation. | Elimination of the possibility for ingress of condensate and liquid coolant solution with concentration less than permitted to the primary coolant as the result of the faulty actions of personnel. | 3 | 1 | CHEM | [7 empty] | 1
42 | Modernization. Transfer of distillate tank TD14(15,16)B001 to boron-containing water tanks and installation of one (two) TD system distillate tanks outside ZC building. | Difficulties in TD system operation occur in different reactor plant modes: 1. Lack of volume at water exchange without evaporator activation; 2. Lack of volume in tanks at the end of the life cycle; 3. possibility for simultaneous processing of boric acid solution and operation of pumps TD21,22D001 at cool-down is unavailable; | 1. Design correction related to distillate tank TD14(15,16)B001 transfer for coolant receiving. 2. Design development for installation of one (two) tanks outside ZC building for distillate storage and discharge; 3. Designs implementation. 4. Equipment setup. 5. Testing | Sufficiency of volumes at different operation modes of the reactor plant. Provision of conditions for normal operation of the evaporator and TD system as a whole. | 3 | 1 | CHEM | [7 empty] | 1
43 | Modernization. Chemicals supply for TR, TD, TG and TC systems filters regeneration. | Ion-exchange charge of TR, TD, TG and TC system filters loose exchanging capacity within shorter (2-3 years) service life than it is established by the design (4-8 years), that causes forced replacement of the ion-exchange charge. Ion-exchange charge replacement in IRI is very complicated and expensive. | 1. 1. Designs correction related to supply of regeneration solutions to the filters. 2. 2. Development of the neutralizing unit design. 3. 3. Development of the design for nitric acid storage and supply unit. 4. Design implementation. 5. Equipment setup. 6. Testing. | Use of ion-exchange charge of the filters within its whole design service life, and within over-design service life at in-service monitoring for its physical-and-chemical characteristics. Reducing of amount of radioactive spent sorbents ingress to tanks ТС31,32В001 and, as the result, generated LRW reducing. Significant reducing of the number of the containers designed for long-term storage or burial of the utilized RW . | 3 | 1 | CHEM | [7 empty] | 2
44 | Modernization. Installation of TR system radioactive drains pretreatment unit. | Different insoluble mechanical impurities ingress to the special sewage system via floor drains of the controlled-access area rooms (mainly, these are decontaminating detergents, washouts from the floors, corrosion products). Besides, in compliance with the technology of loosening cleanups of TD, TG, TC, TR, UZ systems filters, ion-exchange sorbents fines are washed to radioactive drains receiving system with further ingress to the vat residue after radioactive drains water treatment at TR system evaporators. And, as a result, non-operability of TT system LRW treatment unit due to the filter and orifices periodic clogging. | 1. Development of waste waters pretreatment unit design in respect of centrifuge installation on the waste waters receiving pipeline. 2. Design implementation. 3. Equipment adjustment. 4. Testing. | Effective and trouble-free waste water pretreatment unit from mechanical coarse particles etc. Operability of TT system LRW treatment system. | 3 | 3 | CHEM | [7 empty] | 5
45 | Implementation of RM and railways video surveillance system. | At present no possibility of RM and railways overall visual inspection from the control room is available. | МInstallation and adjustment of cameras in RC CH and a display with control panel in the control room. | 1. Enhancement of refueling safety. 2. Prevention of probable shutdowns . | 2 | 1 | TPD | [7 empty] | 6
46 | Modernization of computer complexes Oper 1, Oper 2 as part of RM control system and located in the control room. | Malfunctions in Tenore NT program operation due to moral and physical ageing of computer complexes Oper 1, Oper 2 (manufacture of 1999). | 1. Send a letter to ZAO ASE. 2. Replacement of computer complexes Oper 1, Oper 2. 3. Adjustment, debugging and testing of Tenore NT program operation . | 1. Enhancement of refueling safety. 2. Prevention of probable shutdowns. | 2 | 2 | TPD | [7 empty] | 5