## Noteworthy
OE Reports
Event Summary Monthly by Significance (2018 April)
Report Status: Published
User(s): admin, N/A, WMMOS42
Centre(s): Atlanta, Moscow, Paris, Tokyo
Member(s): Multiple members selected
Date Range (Published Date): 01.04.2018 To 30.04.2018
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER PAR 18-0148 | 2018-04-12 07:28 | Cofrentes 1 | 2017-10-06 |  | Electric arc flash accident resulting in minor hand burns | 00 | 2018-04-12 07:28 | Noteworthy | During a refuelling outage, electrical maintenance work was programmed on the 6.3 kV bus bar. An arc flash occurred on the worker's gloves and hands and he was treated for minor hand burns at the first aid station. The event is Noteworthy because of potential for severe injury. | The direct cause was the failure to correctly check for voltage measurement at the front and rear of the cabin. A contributing cause was the inadequacy of the risk assessment as it was carried out without knowing the plant status at the time of the work.&nbsp; | SER 2002-4 | 1 - For information only, electric shock, human error, industrial safety, injury, procedure inadequacy, risk assessment | IS.1 , MA.1
WER PAR 17-0781 | 2017-11-09 06:11 | Belleville 2 | 2017-10-10 |  | Deviation affecting the seismic resistance of fire-fighting water production pipes in the pump house | 02 | 2018-04-17 08:33 | Noteworthy | Thickness measurements taken on fire-fighting water and essential service-water system pipework showed that these pipes would be unable to withstand an earthquake. The essential service-water motors could be submerged, potentially resulting in the loss of heat sink on both units in case of seismic events. This situation affected 25 EDF units. The event is Noteworthy because the potential loss of ultimate heat sink on multiple units. Nine units of the fleet were shut down. INES level 2 events were recorded at 20 units. | The direct cause was corrosion. #The root causes were deficiencies in the preventive maintenance programme, inadequate risk assessment and weaknesses in the management, corporate support and oversight process.# |  | 1 - For information only, essential service water, fire suppression, management oversight, preventive maintenance, reactor shutdown, risk assessment, seismic qualification, shutdown cooling | CO.5 , EN.1 , ER.2 , ER.4
WER ATL 18-0240 | 2018-04-09 12:57 | Pilgrim 1 | 2017-04-29 18:00 |  | Loss of Control Power to Emergency Diesel Generator | 00 | 2018-04-09 12:57 | Noteworthy | During a refuelling outage, a ground fault on the 125V dc bus concurrent with a loss of control power to an emergency diesel generator (EDG) occurred. This resulted in the EDG being declared inoperable and entry into a limiting condition of operation. The other EDG was already out of service, so fuel movement was suspended. The event is Noteworthy because of loss of a safety function due to unavailability of both EDGs. | The cause was a blown control power fuse due to current surges caused by intermittent ground faults in the past. Another cause was failure to appropriately use the corrective action programme to evaluate and resolve the problem after a similar event in 2012. |  | 1 - For information only, dc bus, diesel generator, fuse, limiting condition of operation, power supply | ER.1 , PI.2

## Trending
OE Reports
Event Summary Monthly by Significance (2018 April)
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 18-0144 | 2018-04-20 00:49 | Kuosheng 2 | 2017-11-17 |  | Emergency Diesel Generator Failed to Trip during Overspeed Test | 00 | 2018-04-20 00:49 | Trending | During an outage, while a post-maintenance test on an emergency diesel generator (EDG) was being performed, the EDG failed to trip by the engine overspeed signal and was tripped manually. As a result of over speed operation, six thermal detectors and several bearings were damaged. The event resulted in an extension of the outage for four days. | The direct cause was internal air leak of two governor valves ensuring the EDG over speed function. The root cause was an inadequate preventive maintenance of the governor valves. Contributing factor was lack of human performance to initiate manual EDG trip at over speed operation. | SOER 2002-2, rec.2 | 1 - For information only, diesel generator, governor valve, human error, outage extension , preventive maintenance | ER.2 , OP.1
WER TYO 18-0143 | 2018-04-20 00:32 | Kuosheng 2 | 2018-03-28 |  | Automatic Reactor Scram During the Performance of Power Ascension Testing | 01 | 2018-04-20 01:01 | Trending | During start-up operation, with reactor at 29% power, the reactor protection system actuated and scrammed the reactor due to signal oscillations from the steam by-pass and pressure regulator system. | The event causes are to be clarified. |  | 1 - For information only, automatic scram, turbine control, turbine trip | ER.1
WER TYO 18-0140 | 2018-04-12 22:30 | Hamaoka 4 | 2017-04-20 |  | Continuation of an operation state not satisfying an operational limit in the emergency gas processing system | 00 | 2018-04-12 22:30 | Trending | During an outage and while performing pressure resistance test of a filter vent, a valve of the emergency gas processing system at the boundary of the system being tested was removed without following the procedures. The mistake was identified after eight months and it was found that during this period an irradiated fuel was handled for four hours with the emergency gas processing system in a state not satisfying an operational limit. | The direct causes were lack of procedure adherence and not providing drawings explaining an accurate system configuration to the workers implementing the procedure. The root cause was lack of management oversight to ensure information sharing about the roles and responsibilities as well as compliance items in the overall isolation management. |  | 1 - For information only, configuration control, drawing, human error, management oversight, procedure adherence | CM.2 , LF.1 , MA.1 , MA.2
WER TYO 18-0136 | 2018-04-03 21:55 | Hamaoka 4 | 2017-10-29 |  | Infiltration of Rainwater into the Reactor Equipment Cooling Water System Trench Room | 00 | 2018-04-03 21:55 | Trending | During unit shutdown and on-going periodic inspection, rainwater leaked into the reactor equipment cooling water system piping duct outside of the radiologically controlled area. The water entered through a wall penetration part due to an untight manhole cover. There was no impact on cables or pipes located in the duct. | The event cause was rainwater leak through an untight manhole cover during a typhoon. The other cause was failure to extract the penetration part as an investigation target to verify station resistance against external events. | SER 2016-02 | 1 - For information only, leak, risk assessment, water intrusion | ER.1
WER PAR 18-0188 | 2018-04-24 05:56 | Ringhals 2 | 2018-03-10 |  | Isolation valves for the containment not ready for operation due to a failed processor module. | 00 | 2018-04-24 05:56 | Trending | During normal operations, following the receipt of containment isolation valves status alarms the operator concluded that the valves remained operable when they were not. Operations failed to enter the required limited condition of operation. | The direct cause was a processor fault . A further cause was that the operators mistakenly considered that the processor logic for component actuation was redundant. The contributing causes were the quality of information available to the operator and the operator's knowledge of the impact on the reactor protection system following receipt of alarms and equipment failures. | SER 2005-2 SOER 2013-1 Rec 3 | 1 - For information only, containment isolation, limiting condition of operation | ER.1 , OP.1 , OP.2
WER PAR 18-0187 | 2018-04-23 09:35 | Ringhals 4 | 2018-01-22 |  | Instrumentation for containment ventilation isolation not operable caused by missing automatic initiation. | 00 | 2018-04-23 09:35 | Trending | During normal operations, the automatic containment ventilation isolation was found inoperable on high radiation initiation from the radiation monitoring system. | The cause was a fault in the circuit board in one of the monitoring channels which in turn failed to trigger the containment ventilation isolation function. The cause of the circuit board failure was a leak from a cadmium nickel battery. |  | 1 - For information only, battery, circuit board, containment isolation, solid state protection system | ER.1 , ER.2
WER PAR 18-0185 | 2018-04-23 09:29 | Ringhals 2 | 2017-11-21 |  | Emergency diesel generator not operable due to water leakage in a cooling water pump. | 00 | 2018-04-23 09:29 | Trending | During normal operations and whilst carrying out a routine surveillance test, a leak on an emergency diesel generator's (EDG) cooling water pump's gland was found unacceptable for further operation. The pump and associated EDG were made unavailable for the replacement. | The direct cause was that the cooling pump's internal components had become loose allowing the shaft to float and to damage the gland seal affecting its ability to retain water. The root cause was that the pump had not been refurbished within the manufacturers's time recommendations. | SOER 2002 Rec 2 | 1 - For information only, ageing, diesel generator, leak, limiting condition of operation, loose part, preventive maintenance, pump seal, pump shaft, seal water | EN.1 , ER.2
WER PAR 18-0184 | 2018-04-23 09:25 | Atucha 1 | 2017-12-13 |  | Unnecessary unavailability of the Diesel of the Emergency Feedwater System. | 00 | 2018-04-23 09:25 | Trending | During normal operations, whilst performing a monthly surveillance test a leak was observed on an emergency diesel for the emergency feed system, the system was made unavailable and a limited condition of operation entered for 14 hours. The leak had been initially observed at the previous month's test when it had been decided that the repair could wait until the refuelling shutdown in March 2018. After repairs it was realised that the unavailability was not necessary. | The direct cause was the lack of communication between maintenance and operations on the availability of the system. The direct cause was a broken seal due to ageing. |  | 1 - For information only, ageing, diesel engine, emergency feedwater, leak, limiting condition of operation, seal | ER.1 , ER.3 , MA.1 , OP.1 , WM.1
WER PAR 18-0181 | 2018-04-23 09:18 | Doel 3 | 2018-02-02 |  | Technical specifications surveillance requirement not integrally recorded in the reactor-operator parameter recording documents. | 00 | 2018-04-23 09:18 | Trending | During a compliance review of technical surveillance requirements it was discovered that the requirement to check the reactor coolant flow indication was not covered in the operating procedures. | The direct cause was the historical procedural inadequacy. The root cause was that the compliance programme did not cover all the reactor statuses so compliance was only checked for steady power and hot shutdown operations. |  | 1 - For information only, procedure inadequacy, surveillance, technical specification | CM.2 , EN.1 , OP.2
WER PAR 18-0179 | 2018-04-23 09:16 | Torness 2 | 2018-01-29 |  | Unit trip due to incorrect switching of essential supplies | 00 | 2018-04-23 09:16 | Trending | During normal operations and following the return to service of one train of uninterruptible power supply train from testing, the electrical supply to an essential supply board was lost resulting in a trip of a quadrant and subsequent reactor automatic scram on high channel gas outlet temperature. | The direct cause was the UPS inverter was configured outside the procedural sequence. The root cause was the failure to operate to procedural requirements. | SER 2003-5 SOER 2013-1 Rec 3 | 1 - For information only, automatic scram, human error, power supply, procedure adherence, risk assessment, switch | ER.1 , OP.1
WER PAR 18-0177 | 2018-04-23 09:15 | Hunterston B 1 | 2018-01-05 |  | Reactor 3 / Turbine Generator 7 Automatic trip – Bulk Group 1 control Rod earth fault causing rod drop | 00 | 2018-04-23 09:15 | Trending | During normal operations, a control rod unexpectedly fell into the reactor activating the reactor protection and resulting in an automatic scram and a three day outage. | The direct cause was an earth fault within the control rod actuator. The root cause was a failure to exclude foreign material. Contributing causes include inadequate component monitoring and inadequate operating experience feedback implementation following the same event at the sister station. |  | 1 - For information only, actuator, automatic scram, control rod drive, FME, insulation electrical, preventive maintenance | ER.2 , MA.1 , OE.1
WER PAR 18-0176 | 2018-04-23 09:15 | Hinkley Point B2 | 2017-03-21 |  | A total of five shutdowns were carried out during reactor 4 start up and return to full load following Reactor 4 Graphite Outage | 00 | 2018-04-23 09:15 | Trending | During reactor start up operations, five separate manual shutdowns of reactor four were carried out following problems with the boiler feed start up system and dump condenser. | The direct cause was equipment defects associated with the start up vessel system. The root cause was a reliance on manual operation and intervention due to organisational tolerance to long standing conditions and workarounds. Contributing causes include inadequate plant preventative maintenance and inadequate design. | SOER 2015-2, rec.3 | 1 - For information only, leak, preventive maintenance, reactor shutdown, steam supply, throttle valve, water hammer | ER.2 , LF.1 , OF.1
WER PAR 18-0175 | 2018-04-23 09:10 | Heysham B1 | 2017-12-18 |  | Secondary shutdown liquid nitrogen storage vessel discovered to be empty | 00 | 2018-04-23 09:10 | Trending | During normal operation, it was identified that secondary shutdown liquid nitrogen storage vessel (SSD) was empty for three months. Two low power refuelling operations were carried out inadvertently on both units during that time. This condition would have required entry into limiting condition of operation during low power refuelling. In addition, the event caused that low power refuelling on unit two was delayed by one week. | The direct cause was stuck level measurement gauge in SSD, failing to respond to a falling level. The root cause were inadequate operational personnel work practices resulting in failing to identify level gauge failure. Contributing factor was missing procedure for extracting trends from plant tour data. | SOER 2013-1 rec. 3 | 1 - For information only, fuelling machine, human error, level instrument, procedure inadequacy, reactor protection system, technical specification | OP.1 , OP.2
WER PAR 18-0174 | 2018-04-23 09:09 | Hartlepool 2 | 2018-01-11 |  | 2A Boiler Trip due to main boiler steam stop valve 2A/SS/8 Spuriously Closing | 00 | 2018-04-23 09:09 | Trending | During normal operation, one out of four boilers was manually isolated and reactor power was reduced to 75%, when an emergency close solenoid failed and spuriously shut the main boiler steam stop valve. The reactor had to be shutdown to reconnect the boiler. | The direct cause was as a short circuit and overheating of the main boiler steam stop valve solenoid as a result of inadequate vendor quality. The root cause was an inadequate operating experience feedback process following numerous events at the sister station, failing to ensure timely and proper implementation of corrective actions. Contributing factor was inadequate frequency and thermography data monitoring. |  | 1 - For information only, main steam isolation valve, power reduction, preventive maintenance, reactor shutdown, solenoid, steam generator / boiler, vendor | ER.2 , ER.3 , PI.3
WER PAR 18-0173 | 2018-04-23 09:09 | Hartlepool 2 | 2017-12-31 |  | Automatic Trip of R2 during Routine Turbine Over Speed Testing | 00 | 2018-04-23 09:09 | Trending | During normal operation, the turbine tripped followed by a reactor scram during standard turbine overspeed protection testing due to a failure of control fluid supply system. The reactor was shutdown for five days. | The direct cause was a break of swaged pipe connection supplying oil to the turbine front trip ring. The root cause was an inadequate quality of swaged pipe connection maintenance. Contributing factor was an inadequate operating procedure. |  | 1 - For information only, automatic scram, oil, procedure inadequacy, surveillance, turbine control, turbine trip | MA.1 , OP.2
WER PAR 18-0172 | 2018-04-23 09:08 | Hartlepool 1 | 2017-12-11 |  | 4 Hour Shutdown Condition Following a Level Abnormal Alarm on Gas Turbine 5 Day Tank | 00 | 2018-04-23 09:08 | Trending | During normal operation, a frozen level transmitter triggered a standing trip signal of low level in the gas turbine fuel oil tank. Limiting condition of operation (LCO) were entered as all three fuel oil centrifuges were declared unavailable. | The direct cause was a blockage of the impulse line of the fuel oil day tank level measurement due to freezing of the condensate build up. The root cause was a missing requirement to perform a routing drainage of condensation collected in the base of gas turbine fuel oil day tank. Contributing factors were isolation of the fuel oil day tank trace heating for a maintenance, lack of observation of operating procedures and inadequate availability of heating equipment. | SOER 2002-1 rev.1 rec. 4 | 1 - For information only, hydraulic fluid, limiting condition of operation, power supply, preventive maintenance, procedure adherence, procedure inadequacy, risk assessment | MA.1 , OF.2 , OP.2 , WM.1
WER PAR 18-0159 | 2018-04-17 08:47 | Ningde 3 | 2017-08-26 |  | Oil Leakage in an Emergency Diesel Generator Heat Exchanger Resulted in Diesel Generator being Unavailable | 00 | 2018-04-17 08:47 | Trending | During normal operations and a low power surveillance test on an emergency diesel generator, an oil leak was observed from the oil cooler so the test was terminated. The EDG was shut down and made unavailable pending repairs. | The cause was heat exchanger inter-plate leakage as the sealing tape had been squeezed out. The apparent cause was inadequate vendor quality control. |  | 1 - For information only, diesel generator, limiting condition of operation, lube oil, vendor | ER.3
WER PAR 18-0155 | 2018-04-17 08:45 | Ningde 3 | 2017-07-12 |  | Parameters Were Found Improper Setting during Inspection of a Temperature Measurement Instrument in Electrical Building Main Ventilation System | 00 | 2018-04-17 08:45 | Trending | During normal operations, a surveillance inspection of the temperature measurement instrumentation for the electrical building main ventilation was carried out and adjustments made. During the post maintenance test a failure alarm was received in the control room and the operator entered a limited condition of operation. | The direct cause was improper settings of the ventilation system valve limit switches during commissioning. A contributing factor was that valve settings in the local programmable logic computer were inconsistent with those in the backup files. |  | 1 - For information only, heating ventilating and air conditioning, human error, limit switch, limiting condition of operation, procedure inadequacy, switch | CM.2 , MA.2 , WM.1
WER PAR 18-0152 | 2018-04-16 08:25 | Chooz B 1 | 2017-12-06 |  | Unauthorised unavailability of the Control Rod Drive Mechanism Ventilation System further to inadvertent isolation of the Component Cooling System | 00 | 2018-04-16 08:25 | Trending | During normal operation, common equipment section of the component cooling system (CCS) was isolated due to a human error further to a CCS train changeover, triggering a spurious high level alarm on the CCS expansion tank. This lead to an unavailability of the control rod drive mechanism ventilation system and entry into limiting condition of operation. | The direct cause was a human mistake. The root causes were inadequate use of operating experience, insufficient training of field operators, lack of procedure and lack of independent verification use by the operation staff. |  | 1 - For information only, control rod drive, heating ventilating and air conditioning, human error, limiting condition of operation, procedure inadequacy | OE.1 , OP.1 , OP.2 , TR.1
WER PAR 18-0151 | 2018-04-13 04:14 | Civaux 1 | 2017-12-28 |  | Inoperability of the door and louver of the building housing the combustion turbine in the event of loss of off-site power | 00 | 2018-04-13 04:14 | Trending | During a station black out (SBO) test to test the availability of the combustion turbine (essential electrical system supplies) and supporting systems it was found that the electrical actuation for the building's doors and louvres which are required to open to provide adequate air flow and cooling for the combustion turbine did not work. The station failed to enter the required limiting condition of operation. Actions to restore the SBO safety case were not carried out until six months later. A fully engineered system was not installed until a further three months later. | The direct cause of the door and louvre failures was due to the original design of providing the electrical supplies from a non essential electrical supply system. Manual opening of the door was not possible because of deformation of the hangar due to lack of maintenance. A contributing cause was that manual testing was not specified as a surveillance routine. | SOER 2002-2 Rec 5 | 1 - For information only, design criteria / design basis, heating ventilating and air conditioning, limiting condition of operation, power supply, preventive maintenance, station blackout | CM.1 , EN.1 , ER.2 , OF.1
WER PAR 18-0150 | 2018-04-12 07:30 | Cruas 4 | 2018-01-08 |  | Cleaning work in the turbine hall resulted in loss of a turbine-driven feedwater pump and automatic load reduction | 00 | 2018-04-12 07:30 | Trending | During normal operations, alarms from several insulation faults on the 48 V switchboard on train A were received coincident with the loss of the turbine-driven feed water pump and an automatic load reduction to 60%. A group 1 limiting condition of operation was also entered. | The direct cause was a worker cleaning the pressure sensor support on turbine-driven feed water pump 1 with a spray and cloths causing a breakdown in insulation resistance of the control equipment and a change in its status. The root cause was an inadequate risk assessment and procedure for the cleaning work. |  | 1 - For information only, control circuit, human error, insulation electrical, limiting condition of operation, power reduction, procedure inadequacy, risk assessment | MA.1 , MA.2 , WM.1
WER PAR 18-0149 | 2018-04-12 07:29 | Cofrentes 1 | 2017-07-12 |  | Failure to request regulatory approval to use methodology for examinations on nozzle-vessel welds | 00 | 2018-04-12 07:29 | Trending | During normal operations, a review of pressure vessel to nozzle weld inspection results revealed that of the two methods of weld inspection (perpendicular and parallel) only one had been carried out. This omission was completed at the next refuelling outage and all welds were found to be satisfactory. | The root cause was that the design change proposal from using the existing approved CSN (Consejo de Segurided Nuclear) non destructive testing (NDT) standard requiring two methods of NDT to the Swedish NDT standard which only requires one method of NDT had been carried out without regulator approval. |  | 1 - For information only, configuration control, design change, nondestructive examination, procedure adherence, reactor vessel, surveillance, weld | CM.3 , EN.1
WER PAR 18-0147 | 2018-04-12 07:28 | Cofrentes 1 | 2017-10-13 |  | A diesel generator started unexpectedly due to human error during testing another one | 00 | 2018-04-12 07:28 | Trending | During a refuelling outage, an automatic start up test was carried out on a division II diesel generator. The testing resulted in the start-up of division 1 systems including the low pressure core spray system, the low pressure coolant injection system and the diesel generator. | The direct cause was human error in starting up the wrong diesel generator. The root cause was that self-checking was not used. Contributing causes were the lack of protection for the push button and a lack of supervision. | SOER 2013 Rec 3 | 1 - For information only, diesel generator, human error, management oversight | OP.1
WER PAR 18-0146 | 2018-04-12 07:26 | Borssele 1 | 2017-10-17 |  | SCRAM during full load due to the erroneous activation of the YZ068 signal for Steam Generator 1 | 00 | 2018-04-12 07:26 | Trending | During normal operations, the unexpected activation of the steam generator (SG) protection resulted in the loss of feed water to SG1 and a reactor scram. This was a repeat of an event three months earlier. | The direct cause was short-circuiting as a result of a micro metal shavings on the cabinet connector of the SG protection module. The contributing cause was the failure to eliminate the foreign material following the same event three months earlier. |  | 1 - For information only, automatic scram, feedwater control system, FME, reactor protection system | MA.2 , OE.1 , PI.2
WER PAR 18-0145 | 2018-04-12 07:25 | Atucha 2 | 2017-11-07 |  | Unavailability of one out of four loops of the intermediate residual heat removal system | 00 | 2018-04-12 07:25 | Trending | During normal operations, a loop of the intermediate residual heat removal system was made unavailable due to inability to correct a low pressure condition. This resulted into entry in a limiting condition of operation. | The apparent cause of the loss in pressure was due to the pressurised water tank being emptied as a result of successive draining. This in turn was due to the erroneous indication of the level sensor due to leakage through the seal of the bypass valve on the reference column. |  | 1 - For information only, leak, level instrument, limiting condition of operation, residual heat removal | ER.1
WER PAR 18-0144 | 2018-04-12 07:25 | Atucha 2 | 2017-11-16 |  | Corrosion of a radial bearing in a startup/shutdown pump of the feedwater system | 00 | 2018-04-12 07:25 | Trending | During normal operations, whilst performing a monthly surveillance test, one of the four start-up /shutdown feed water system pumps failed and an entry into a limited condition of operation was made for six days during the repairs. | The cause of the failure was a failed bearing due to gland cooling water ingress which caused corrosion of the bearing. Contributing causes were the operating and testing regime and control of gland coolant. |  | 1 - For information only, bearing, erosion/corrosion, feedwater pump, limiting condition of operation, procedure inadequacy, pump seal, seal, water intrusion | ER.1 , MA.1
WER PAR 18-0053 | 2018-02-09 08:11 | Chooz B 1 | 2017-11-02 |  | Violation of an LCO action statement on both units | 01 | 2018-04-26 04:25 | Trending | During normal operation of Unit 1 and intermediate shutdown of Unit 2, the combustion turbine tripped during a surveillance test. This resulted in entry into a group-2 limiting condition of operation (LCO) on both units. The combustion turbine could not be repaired in time and the LCO action time was exceeded by three days. A portable generator was brought in as a temporary substitute for the combustion turbine. | The causes include numerous equipment failures and organisational shortfalls. These include spurious switchover of the control system in no-load conditions; issues with the excitation system; breaker retransmission malfunction; problem with reduction gear coupling; inadequate relationship with contractors and suppliers; lack of preventive maintenance and inadequate coordination between mechanical and electrical technicians. |  | 1 - For information only, contractor, limiting condition of operation, preventive maintenance, technical specification, work control | ER.1 , ER.2 , WM.1
WER PAR 17-0837 | 2017-11-20 09:01 | Cofrentes 1 | 2017-10-30 |  | Unscheduled shutdown to resolve discrepancies identified in the feedwater flow rate indication | 01 | 2018-04-12 07:21 | Trending | During startup after an outage, the feedwater flow distribution between lines A and B was not as expected, larger through line B and than through line A. The plant was taken to cold shutdown to inspect the feedwater loop A. The event resulted in a 35-day outage. | The direct cause was that the valve flap inside a feedwater system containment isolation valve became detached and entered the line A. The root causes were incorrect set up of the actuator during maintenance which caused the valve flap experiencing high turbulence inside the valve and failure of the set screws fastening the counterweight. The other causes were inadequate maintenance procedure and risk assessment. |  | 1 - For information only, check valve, feedwater control system, human error, loose part, procedure inadequacy, reactor shutdown, risk assessment, valve actuator | CM.2 , MA.1 , MA.2
WER PAR 17-0817 | 2017-11-16 09:56 | Fangchenggang 1 | 2017-03-08 |  | Rupture of the Pipe Where Safety Injection System Safety Valve was Located | 01 | 2018-04-26 04:53 | Trending | During shutdown and after starting a safety injection system pump for performing a test, a leak occurred on the pipe where a safety valve was located. The safety injection pump was shut down and isolated. This resulted in an entry into a limiting condition of operation and outage extension for four days. | The direct cause was that a water hammer caused weld fatigue cracking. The root cause was gas intrusion in a dead zone of the safety injection system pipes due to a construction deficiency. Contributing cause was a lack of verification of gas content control requirements in existing venting processes. | SER 2005-1 | 1 - For information only, fatigue cracking, gas intrusion, leak, limiting condition of operation, outage extension , safety injection, safety injection pump, water hammer | EN.1 , ER.1
WER PAR 17-0482 | 2017-08-29 08:29 | Grohnde 1 | 2016-07-30 |  | Leakage at a measuring line of the reactor coolant system | 01 | 2018-04-26 04:43 | Trending | During normal operation, a signal indicating leakage in the reactor coolant system was received in the control room. The reactor was shut down to locate the leakage. A small leakage (0.002 kg/sec) was spotted at a weld seam of an instrumentation line. The event resulted in a 16-day outage. | The cause was a wall penetrating crack due to vibration, which had grown in stages over a longer period of time. |  | 1 - For information only, leak, nozzle, reactor coolant, reactor shutdown, vibration, weld | ER.1 , ER.2
WER PAR 17-0277 | 2017-05-18 06:16 | Atucha 2 | 2016-12-22 |  | Manual shutdown due to a minor leakage through rupture disk of Safety Injection System (JND40AA008 | 01 | 2018-04-26 04:17 | Trending | During normal operation, a water leak exceeding the set limit of the primary system was found through a rupture disk of the safety injection system. The reactor was shut down for about 12 days for troubleshooting. | The cause was unexpected variations in temperatures for the rupture disk. At the bottom of the disk is the pipe corresponding to the outlet of the heat exchanger of the moderator, radiating significant heat. |  | 1 - For information only, design criteria / design basis, leak, reactor coolant, reactor shutdown, rupture disc, safety injection | CM.1 , EN.1
WER MOW 18-0085 | 2018-04-27 14:57 | Smolensk 2 | 2018-04-27 |  | #PRELIMINARY# Leak of the feed water pressure header followed by unit 2 an unplanned repairing. | 00 | 2018-04-27 14:57 | Trending | During operation at 70% power, a leak was found on the feed water pressure header. The reactor was manually scrammed. During investigation, a through wall leak of an air vent tube nozzle on the pressure header and a metal crack downstream of the welded seam were found. | The event is being investigated. |  | 1 - For information only, feedwater control system, leak, manual scram, nozzle, weld | ER.1
WER MOW 18-0084 | 2018-04-26 03:43 | Kola 4 | 2018-03-12 |  | Through wall crack of the drainage valve of the second extraction steam separator led to manual trip of TG-7. | 00 | 2018-04-26 03:43 | Trending | During normal operation, a steam leak was found from the drain valve of an extraction steam separator of one of the two turbine generators. The turbine generator was tripped for repair. | The direct cause was flow accelerated corrosion on the valve&rsquo;s body and cracks on the welded seam of the valve&rsquo;s outlet nozzle. The root cause was erosion defects on the valve surface due to heat treatment violation during the valve manufacturing. |  | 1 - For information only, drain valve, erosion/corrosion, leak, power reduction, steam, turbine trip, vendor, weld | ER.2 , ER.3
WER MOW 18-0083 | 2018-04-25 16:22 | Zaporozhye 2 | 2018-03-07 |  | Safety System Train Actuation on the Loss of Power to a 6 kV Vital Bus During Refueling | 00 | 2018-04-25 16:22 | Trending | During a refuelling outage, a 6kV vital bus lost power after tripping of a standby feeder breaker. A diesel generator automatically started to energize the vital bus. | The direct cause was control cable conductor shorting during installation due to degraded insulation. The root causes were inadequate installation procedure and deficient cable installation. The contributors were lack of work permit and inadequate supervision of contractor performance. |  | 1 - For information only, contractor, insulation electrical, management oversight, power supply, procedure inadequacy | MA.1 , MA.2 , WM.1
WER MOW 18-0079 | 2018-04-23 14:46 | Smolensk 2 | 2018-04-22 |  | #PRELIMINARY# Unit 2 was manually shutdown for an unplanned maintenance. | 00 | 2018-04-23 14:46 | Trending | During normal operation, the reactor was conservatively shut down to ensure the veracity of primary circuit leak detection system. After cooling of the primary circuit, a leak was found on a valve flange of the distributing group header's dead-end zone flushing pipe. | The cause of the leakage is being investigated. |  | 1 - For information only, leak, reactor coolant, reactor shutdown, valve | ER.1
WER MOW 18-0078 | 2018-04-23 14:37 | Dukovany 3 | 2018-04-22 |  | #PRELIMINARY# Unit 3 of Dukovany NPP was conservatively shutdown to check heterogeneous welds | 00 | 2018-04-23 14:37 | Trending | During normal operation, Unit 3 was shut down conservatively to check six heterogeneous weld joints on emergency feed water inlet pipelines to steam generators. The decision was based on the investigation and analysis of findings on cracks on weld joints of several emergency feedwater inlet pipelines of Unit 2 (WER MOW 15-0218, WER MOW 15-0078). | The causes of the cracks on the weld joints in Unit 2 are being investigated. |  | 1 - For information only, emergency feedwater, reactor shutdown, weld | ER.1 , PI.2
WER MOW 18-0076 | 2018-04-18 00:56 | Tianwan 3 | 2017-10-31 |  | Low level of Unit 3 pressurizer triggered a shutdown protection signal | 00 | 2018-04-18 00:56 | Trending | During start up after a maintenance, with reactor subcritical and temperature of primary coolant circuit of 225 deg. C, reactor protection signal was triggered due to pressurizer (PRZ) level drop to the setpoint due to a coolant leak through the fractured PRZ spray bypass preheating line. | The direct cause was a fracture of the PRZ spray preheating pipeline bypass line. The root cause was that an alternating load generated by pipeline vibration caused its fracture. Contributing factor was the machined cutting mark on the surface of the headjoint and the thinner thickness of the pipe wall lead to the fracture of the pipe. |  | 1 - For information only, leak, pressuriser level, pressuriser spray valve, reactor coolant, vibration | CM.1 , ER.1
WER MOW 18-0075 | 2018-04-18 00:47 | Tianwan 2 | 2018-01-16 |  | Most positive terminal posts of the accumulator battery 2BTD53 of Unit 2 are badly corroded. | 00 | 2018-04-18 00:47 | Trending | During normal operation and when performing preventive maintenance, most of the unit accumulator battery positive terminal posts were found significantly corroded. In addition, they caused break of the terminal post cover. The corroded batteries had to be prematurely replaced during normal operation with a standby group of batteries used to ensure the safety function. | The direct cause was that the accumulator battery has been close to the end of its lifetime with an observed slowly accumulating corrosion. The root cause was an inadequate design of the sealing ring cover, easy to fail and causing acid leakage and corrosion of positive terminal posts. The contributing factor was inadequate procedure of routine maintenance, not taking into account specifics of the close the end of the life phenomena. |  | 1 - For information only, ageing, battery, erosion/corrosion, procedure inadequacy | ER.2 , ER.3
WER MOW 18-0074 | 2018-04-18 00:35 | Tianwan 3 | 2018-01-13 |  | Lubricant leaked from the cracked electric actuator of atmospheric release valve 30LBU10AA201. | 00 | 2018-04-18 00:35 | Trending | During commissioning and when performing load dump test at 50% power, electric actuator of steam generator atmospheric relieve valve cracked and the whole shell ruptured into two parts. This resulted in its inoperability and entry into limiting condition of operation. | The direct cause was excessive vibration of the pipeline and valve during steam discharge from the atmospheric relieve valve. The root cause was that the sub-contractor failed in providing a correct installation and assembling of the pipework associated with the steam relieve valve following a corrective action. |  | 1 - For information only, actuator, contractor, leak, limiting condition of operation, steam dump valve, vibration | ER.1 , MA.1 , MA.2 , PI.3
WER MOW 18-0072 | 2018-04-12 09:09 | Dukovany 4 | 2018-04-12 |  | #PRELIMINARY# Planned Shutdown of Unit 4 to Carry out Check of Emergency Feedwater Pipeline Heterogeneous Welds | 00 | 2018-04-12 09:09 | Trending | During normal operation, Unit 4 was shut down conservatively to check six heterogeneous weld joints on emergency feed water inlet pipelines to steam generators. The decision was based on the investigation and analysis of findings on weld joints of several emergency feedwater inlet pipelines of Unit 2 (WER MOW 15-0218, WER MOW 15-0078). The expected duration of the outage was 10 days. | The causes of the cracks on the weld joints in Unit 2 are being investigated. |  | 1 - For information only, emergency feedwater, reactor shutdown, weld | ER.1 , PI.2
WER MOW 18-0071 | 2018-04-10 23:42 | Kola 3 | 2018-02-02 |  | Generator’s brushgear sparking due to eroded surface of the “+” rocker. | 00 | 2018-04-10 23:42 | Trending | During normal operation, sparking on one of the two turbine generator's brushgear was found. The turbine generator was downloaded and put in the standby mode. | The direct cause was erosion of the brushgear slipping contacts due to micro cracks on the contact positive surface. Micro cracks were developed due to the generator rotor overvoltage caused by the exciting system thyristor device fault. The root cause was inadequate brushgear rockers maintenance procedure. |  | 1 - For information only, erosion/corrosion, exciter, power reduction, preventive maintenance, procedure inadequacy, turbine generator, turbine trip | ER.2 , MA.2
WER MOW 18-0070 | 2018-04-10 07:38 | Dukovany 3 | 2017-12-04 |  | Broken venting pipe on Essential Service Water (ESW) due to his corrosion | 00 | 2018-04-10 07:38 | Trending | During normal operation and while performing inspection of the venting sumps on the essential service water (ESW) system, a fallen rusted venting pipe was found in the sump. The affected ESW pipeline was drained for repair. This resulted in inoperability of one of the three ESW trains and entry into a limiting condition of operation. | The direct cause was corrosion of the vent pipe located in the sump. The root cause was inadequate monitoring of the pipe. | SER 2006-2 | 1 - For information only, erosion/corrosion, essential service water, leak, limiting condition of operation, preventive maintenance | ER.2 , ER.4
WER MOW 18-0069 | 2018-04-10 07:30 | Dukovany 3 | 2017-11-28 |  | Leak from Essential Service Water (ESW) pipeline due to corrosion his venting pipe | 01 | 2018-04-24 03:25 | Trending | During normal operation, a leak was found from a vent pipe on the essential service water (ESW) pipeline. The pipeline was isolated and drained for repair, making one of the three ESW trains inoperable. This resulted in an entry into a limiting condition of operation. | The direct cause was corrosion of the vent pipe located in the sump. The root cause was inadequate monitoring of the pipe. | SER 2006-2 | 1 - For information only, erosion/corrosion, essential service water, leak, limiting condition of operation, preventive maintenance | ER.2 , ER.4
WER MOW 18-0067 | 2018-04-08 13:55 | Zaporozhye 6 | 2018-04-08 |  | Unit 6 reactor automatically scrammed by protection actuation. | 01 | 2018-04-28 22:56 | Trending | During operation at 92% power, the reactor scrammed automatically on trip of both turbine driven feed water pumps (TDFPs). | #The direct cause was a stuck push button on the manual control assembly on the main condensate line, which resulted in low suction pressure of the TDFPs. The root cause was structural deficiency of the manual control pushbutton. The contributors were inadequate main condensate configuration reliability and inadequate operator training.# |  | 1 - For information only, automatic scram, design criteria / design basis, feedwater pump | ER.1 , TR.1
WER MOW 18-0066 | 2018-04-06 14:06 | Smolensk 3 | 2018-01-26 |  | A Turbine Generator was tripped off line due to excitation circuit insulation resistance dropping | 00 | 2018-04-06 14:06 | Trending | During normal operation, one of the two turbine generators (TG) ground fault alarm was received. Insulation resistance of the TG excitation circuitry was checked and found low. The TG was tripped and the reactor power was reduced to 50% for troubleshooting. | The direct cause was a damaged glass fibre regulation gasket on the brushgear minus yoke and loss of gasket insulating properties. The root cause was deficient vendor specification for the brushgear maintenance. |  | 1 - For information only, exciter, gasket, insulation electrical, power reduction, procedure inadequacy, turbine trip, vendor | ER.2 , MA.2
WER MOW 18-0065 | 2018-04-06 08:34 | Balakovo 1 | 2017-08-11 |  | Traces of a Water Leak into the Diesel Generator Oil | 00 | 2018-04-06 08:34 | Trending | During normal operation, regular emergency diesel generator (EDG) oil sampling test identified water traces in the lube oil. The water content was below the limit value. The EDG was taken out of service for maintenance to identify the causes of water intrusion into the oil, entailing entry into limiting condition of operation. | The direct cause was a damaged bottom ring in the seal assembly between the sleeve and EDG exhaust header section. The root cause was lack of requirements to check for alignment during barrel bushing installation in the maintenance documentation. Contributing factor was incorrect maintenance work practices. | SOER 2002-2, rec.2 | 1 - For information only, contractor, diesel generator, leak, limiting condition of operation, lube oil, preventive maintenance, procedure inadequacy | MA.1 , MA.2
WER MOW 18-0063 | 2018-04-03 14:50 | Khmelnitsky 1 | 2018-04-03 |  | #PRELIMINARY# A ground fault of the generator stator winding followed by the unit disconnection from the grid | 00 | 2018-04-03 14:50 | Trending | During normal operation, the unit was disconnected from the grid due to a generator stator winding ground fault. The reactor power was stabilized at 0.5% thermal power. | Causes of the event are being investigated. |  | 1 - For information only, stator, turbine trip | ER.1
WER MOW 18-0057 | 2018-03-29 00:48 | Rostov 1 | 2018-03-28 |  | Personnel Error during scheduled work at switchyard led to the unit disconnection from the grid. | 01 | 2018-04-26 09:23 | Trending | During normal operation and while working at switchyard to test a grid stability and protective relaying system, an input was generated to trip the main turbine generator and two circuit breakers. | The direct cause was human error as a turbine trip signal was generated due to inadequate scheme analysis completed by a protective relaying group supervisor when developing / testing the work package. The root cause was inadequate training/qualification. |  | 1 - For information only, human error, surveillance, turbine trip | MA.1 , TR.1
WER MOW 18-0039 | 2018-03-07 14:16 | Rostov 4 | 2018-03-07 |  | Unit 4 disconnected from the grid | 01 | 2018-04-19 07:59 | Trending | During unit commissioning, with steady operation at 50% power, main turbine tripped on loss of a generator oil sealing pumps due to a loss of related 0.4 kV power supply bus. The reactor power was reduced to 0.5%. The 0.4 kV bus bar lost power following a short circuit induced by a foreign material intrusion and due to a degraded insulation resistance of a control cable in an associated electric power supply system. | The direct cause was a of low insulation resistance of the control cable and a foreign material drop onto the standby feeder breaker cubicle. The root cause was a mechanical damage of the control cable insulation during cable laying work by electrical contractors and failure to meet post-installation requirements on ensuring absence of foreign materials. |  | 1 - For information only, bus bar, contractor, insulation electrical, power reduction, power supply, turbine trip | CM.1 , MA.1
WER MOW 18-0032 | 2018-03-06 00:43 | Leningrad 2 | 2018-03-03 |  | The second 330kV bus system switched off by the bus differential protection actuation. | 01 | 2018-04-24 02:44 | Trending | During normal operation, the 330kV busbar system switched off by differential protection actuation. An automatic load reduction system actuated to trip one of the two turbine generators on high current. The reactor power automatically reduced to 50%. | The direct cause was a short circuit of the cable connector on the 330kV bus due to poor oil quality. The root cause was deficient vendor documentation having no requirements to check oil quality prior to filling out the connector and following the final assembly. |  | 1 - For information only, bus bar, debris / crud, documentation, oil, power reduction, procedure inadequacy, turbine trip, vendor | ER.2 , MA.2
WER MOW 18-0006 | 2018-01-12 04:51 | South Ukraine 3 | 2018-01-11 |  | The Unit was down powered due to loss of the reactor coolant pump (RCP). | 01 | 2018-04-23 23:57 | Trending | During normal operation, a reactor coolant pump (RCP) tripped on low pressure differential between seal ring water and the first stage of sealing device. The reactor power automatically reduced to 67%. | The direct cause of the RCP trip was closing of its seal water discharge valve due to spurious actuation of sealing water pressure interlock as a result of a fluid leak from one of the sensor blowdown valves. The root cause was inadequate analysis of engineering solutions available in the industry. The contributor was inadequate inspection programme. |  | 1 - For information only, leak, power reduction, reactor coolant pump, reactor coolant pump seal, sensor | ER.1 , ER.2 , PI.2
WER MOW 17-0219 | 2017-10-24 23:25 | Armenia 2 | 2017-10-19 |  | Turbine Generator No.4 Tripped Off on the Loss of Excitation | 01 | 2018-04-12 23:58 | Trending | While operating at 92% reactor power, a grid load swing occurred. The generator pulled out of synchronization and disconnected from the grid followed by an automatic reactor power reduction to 54%. Five fuses and 12 diodes in a turbine generator cooling rectifier were found burnt due to the disturbance. | The direct cause was overheating of the diodes and fuses due to overvoltage. The root cause was that engineering review process failed to specify requirements on the diode service life which resulted in component degradation and failure. |  | 1 - For information only, diode, exciter, fuse, power reduction, transmission line, turbine generator | ER.2
WER MOW 17-0167 | 2017-07-27 08:00 | Armenia 2 | 2017-07-27 |  | TG-4 disconnection from the grid by protection actuation | 01 | 2018-04-12 08:16 | Trending | While operating at 92% power, a running stator cooling pump was mistakenly de-energised, resulted in tripping of one of the two turbine generators due to stator flow protection actuation. | The direct cause was human error. While de-energising the generator stator cooling pump B, an electrician by mistake turned off power switch of the pump A. The root cause was inadequate peer check and training on use of peer check and on-line communication. |  | 1 - For information only, configuration control, human error, stator, turbine trip | OP.1
WER ATL 18-0271 | 2018-04-27 13:41 | Bruce A 2 | 2018-01-31 |  | Automatic Turbine Trip, Due to Governing System Control Module Failure (SCRAM) | 00 | 2018-04-27 13:41 | Trending | During normal operation, one of the turbine governor valves (GV) was closed due to GV oscillations requiring servo valve replacement. When disconnecting the cannon connector to pursue servo valve replacement, an automatic turbine trip occurred due to valve discrepancy. The reactor was shut down for 10 days for troubleshooting. | The cause of the turbine trip was failure of a redundant position control module in the turbine governor control system. |  | 1 - For information only, governor valve, reactor shutdown, turbine control, turbine trip | ER.1
WER ATL 18-0270 | 2018-04-27 12:27 | Darlington 3 | 2018-03-08 |  | Failure of Safety Related System Test for Low Pressure Service Water System Results in Reduction of Redundancy | 00 | 2018-04-27 12:27 | Trending | During normal operation and while performing a low pressure service water (LPSW) system preventive maintenance test, the LPSW tank level control valve for the LPSW main pump did not open at its set point. This resulted in reduction in the LPSW system redundancy. | The apparent cause was that the carbon steel components and configuration of the piping resulted in accumulation of corrosion products in the tank standpipe and level switch bodies. The contributing factor was inadequate preventive maintenance frequency. |  | 1 - For information only, debris / crud, erosion/corrosion, essential service water, level instrument, preventive maintenance, switch | ER.2 , ER.4
WER ATL 18-0269 | 2018-04-27 12:25 | Bruce B 8 | 2018-02-13 |  | Unit 8 Forced outage due to Reactor Area Bridge Brake Failure | 00 | 2018-04-27 12:25 | Trending | During normal operation and while performing a reactor area bridge (RAB) brake test prior to fuelling, the RAB brakes were found failed. The unit was shut down for 54 hours to replace the brakes. | The cause was cracking of all friction discs in the RAB brake. The other cause was inadequate design of the brake hub, producing stress concentrations on the corners of the hub which caused the friction discs to fracture. |  | 1 - For information only, design criteria / design basis, fatigue cracking, fuelling machine, reactor shutdown | CM.1 , FA.1
WER ATL 18-0267 | 2018-04-25 13:13 | Fermi 2 | 2017-11-26 15:37 |  | Reactor Recirculation Motor Generator Set Field Ground Results in Required Downpower | 00 | 2018-04-25 13:13 | Trending | During normal operations, an earth fault alarm was received from a reactor recirculation motor generator (RRMG). The RRMG was made unavailable, a limited condition of operation entered, the unit load reduced to 37% and operation continued on a single loop only. An equivalent loss of 7 days operation was incurred during the repair. | The direct cause was a build up of carbon deposits resulting in a loss of contact between brush and slip ring and a subsequent earth fault. The root cause was inadequate operations instructions and guidance. Contributing causes were inadequate preventive maintenance strategies, inadequate event reporting and unrecognised reduction of operational margin. | SER 2005-3 | 1 - For information only, design change, limiting condition of operation, power reduction, preventive maintenance, reactor recirculation, risk assessment | CM.3 , ER.2 , OP.2 , PI.1
WER ATL 18-0266 | 2018-04-25 13:08 | Turkey Point 3 | 2014-07-01 14:50 |  | Unit Load Increase During Linear Variable Differential Transformers Signal Conditioner Card Replacement | 00 | 2018-04-25 13:08 | Trending | During operation at 48.7% power and while replacing a linear variable differential transformer signal conditioner card of a turbine control valve, a step change in a control valve position occurred. This resulted in a transient load increase of 1.3%. | The cause was a fault in the turbine control system software logic, which opened a control valve based on a signal that indicated it had moved closed. |  | 1 - For information only, design criteria / design basis, digital control system / digital components, power surge, reactivity management, risk assessment, turbine control, turbine control valve | CM.1 , ER.1 , OF.2
WER ATL 18-0264 | 2018-04-25 13:01 | Vogtle 1 | 2016-10-25 |  | Falsification of Plant Records | 00 | 2018-04-25 13:01 | Trending | System operators created false logs which are required by the Operating Licence. Operators did not perform some surveillance rounds and recorded inaccurate information in some cases. | The root cause was that the operators wilfully falsified operator rounds logs. The contributing causes include inadequate leadership, supervision, and follow up of events relating to nuclear professionalism. |  | 1 - For information only, counterfeit / fraudulent , management oversight, technical specification | LF.1 , NP.1 , OR.1 , SC.1
WER ATL 18-0263 | 2018-04-25 12:56 | Browns Ferry 3 | 2016-04-06 15:00 |  | Unusual Event Due to Main Steamline High High Radiation Condition | 00 | 2018-04-25 12:56 | Trending | While increasing power after an outage and at 99% power, main steam line high radiation alarm was received, resulting in declaration of an unusual event. Unit power was reduced to 90.6% and main steam line radiation lowered accordingly. | The direct cause was oil intrusion into the condensate system via a reactor feedwater (RFW) pump outboard bearing seal water leak-off drain due to the incorrect installation of the RFW pump outboard bearing oil return flow indicating sight glass. The root cause was a vendor design vulnerability associated with the bearing housing. The contributing causes were inadequate documentation and inadequate RFW outboard bearing oil breather cap configuration. |  | 1 - For information only, design criteria / design basis, documentation, feedwater pump, FME, human error, main steam line, oil, power reduction, seal, vendor | ER.3 , MA.1 , MA.2
WER ATL 18-0262 | 2018-04-25 12:49 | Oyster Creek 1 | 2017-08-31 13:00 |  | Test Equipment Does Not Meet Technical Specification Surveillance Requirements | 00 | 2018-04-25 12:49 | Trending | During a review of industry operating experience, it was identified that a reactor protective system test device routinely used during anticipatory scram testing bypasses more input signals than is permitted by technical specification and the action to verify that sufficient channels remain operable or tripped was not completed in one hour time limit. With this test device installed, a full scram would not occur in the test channel based on closure of 3 of 4 turbine stop valves. | The cause was inadequate rigor applied when reviewing the suitability of this equipment during the procedure revision carried out in 2013. | SER 2005-3 | 2 - Important lessons, design change, human error, procedure inadequacy, reactor protection system, surveillance, technical specification | CM.3 , EN.1
WER ATL 18-0261 | 2018-04-25 12:46 | Grand Gulf 1 | 2018-01-08 12:35 |  | Forced Outage Due to Un-Isolatable Steam Leak on Main Steam Equalizer Line | 00 | 2018-04-25 12:46 | Trending | During normal operation, an un-isolatable steam leak from a steam line in the condenser bay was identified. The reactor was shut down for repair. | The direct cause was cyclic fatigue. The other causes were not including the main and reheat steam in the trip critical systems list and non implementation of the relevant management standard. |  | 1 - For information only, ageing, fatigue cracking, leak, preventive maintenance, reactor shutdown, single point vulnerability, steam | ER.2 , ER.3
WER ATL 18-0259 | 2018-04-24 14:26 | Surry 1 | 2017-08-09 13:38 |  | Unit Shutdown Due to Reactor Coolant System Pressure Boundary Leakage | 00 | 2018-04-24 14:26 | Trending | During normal operation, a reactor coolant system leakage was identified in the sampling system line. The leakage resulted in unit shutdown for two days. | The direct cause was a thermal fatigue of an instrumentation tube in a weld area. The apparent cause was inadequate installation of seismic tubing and supports during the equipment installation. |  | 1 - For information only, fatigue cracking, leak, reactor coolant, reactor shutdown | ER.2 , MA.1
WER ATL 18-0258 | 2018-04-24 13:36 | Grand Gulf 1 | 2016-11-17 09:00 |  | Organizational Issues Result in Inoperable Oscillation Power Range Monitors | 00 | 2018-04-24 13:36 | Trending | During normal operation, it was identified that oscillation power range monitor period setpoints were outside of the allowed license basis range, making the oscillation power range monitors inoperable. This resulted in an entry into limiting conditions of operation. | The direct cause was a failure to ensure the required procedure changes were incorporated and performed prior to the unit entering the mode of applicability. The apparent cause were improper personnel work practices in the modification process, failing to ensure technical information was incorporated into the appropriate procedures. Contributing cause was inadequate oversight of the modification over an extended implementation time period. | SER 2005-3 | 1 - For information only, design change, human error, limiting condition of operation, management oversight, nuclear instrumentation, reactor protection system | CM.2 , CM.3
WER ATL 18-0257 | 2018-04-24 13:33 | Cook 1 | 2017-12-21 00:01 |  | Turbine Driven Auxilary Feedpump Failed to Reach Rated Speed During Surveillance | 00 | 2018-04-24 13:33 | Trending | During normal operation and while performing a surveillance test, the turbine driven auxiliary feedwater pump (TDAFP) did not come up to speed as required. This resulted in an entry into a limiting condition of operation and the reactor power was reduced to 96% to repair the TDAFP. | The cause was incorrect set up of the TDAFP governor valve linkage, which prevented the governor valve from having full travel capability. A contributing cause was minor binding of the governor valve linkage. |  | 1 - For information only, auxiliary feedwater pump, governor valve, limiting condition of operation, power reduction | MA.1 , MA.2
WER ATL 18-0253 | 2018-04-19 15:13 | Peach Bottom 3 | 2018-01-14 05:55 |  | Trash Racks and Outer Screens Clogged by River Ice | 00 | 2018-04-19 15:13 | Trending | During normal operation, ice was building-up at the intake water structures due to a cold weather and rapidly changing river flow. Power had to be reduced to 88% to maintain main condenser vacuum. | The direct cause was an ice build-up at the cooling water intake structures due to a cold weather. The root cause was an inadequacy of operating procedures for response to river ice blockage to address rapidly changing river flow and ice movement conditions. The contributing factor was inadequate availability of staged equipment to mitigate the consequences of the event. | SOER 2007-2, rec.5 | 1 - For information only, condenser vacuum, intake, power reduction, procedure inadequacy, strainer, travelling screen | CM.1 , OP.2
WER ATL 18-0252 | 2018-04-19 15:08 | Quad Cities 2 | 2018-01-14 23:43 |  | Adjustable Speed Drive Tripped | 00 | 2018-04-19 15:08 | Trending | During normal operation, an adjustable speed drive (ASD) tripped causing a trip of the associated reactor recirculation pump. This resulted in entry into limiting conditions of operation and power decrease to 30%. | The cause was an incorrect signal sent from degraded circuit card in the ASD. The root cause was that the vendor revised the circuit card without sharing the information with the station, resulting in an improper operation of the system. |  | 1 - For information only, circuit card, limiting condition of operation, power reduction, reactor recirculation pump, vendor | ER.3
WER ATL 18-0250 | 2018-04-19 14:39 | Callaway 1 | 2018-01-11 09:00 |  | Service Air Containment Isolation Valve Found Open | 00 | 2018-04-19 14:39 | Trending | During normal operation, a service air containment isolation valve was found unlocked and open. The valve was inadvertently left open during the refueling outage when the plant entered mode 4. This resulted in a condition prohibited by technical specifications and an entry into a limiting condition of operation. | The root cause was lack of direction in the plant startup procedure to close the service air containment isolation valve. The contributing causes were inadequate plant startup and containment isolation verification procedures and inadequate validation of the out of service equipment log by the shift supervisor. | SOER 2010-1 Rec 6 | 1 - For information only, configuration control, containment isolation, human error, isolation valve, procedure inadequacy, technical specification | CM.2 , OP.2
WER ATL 18-0249 | 2018-04-19 14:35 | Grand Gulf 1 | 2018-01-13 15:30 |  | Steam Leak in Auxiliary Steam Tunnel Results in Extension to Forced Outage | 00 | 2018-04-19 14:35 | Trending | The unit was being started after an outage, with reactor at 3% power when the reactor had to be shut down and cooled down to repair main steam leakage control isolation valve leak. The outage was extended by approximately two days. | The cause was a packing leak on the main steam isolation valve leakage control isolation valve due to ageing. |  | 1 - For information only, ageing, leak, main steam line, outage extension , reactor shutdown, steam | ER.3
WER ATL 18-0248 | 2018-04-19 14:32 | Mcguire 1 | 2018-01-18 12:00 |  | Parking Lot Slip on Icy Surface Later Deemed an Occupational Safety and Health Administration Recordable Injury | 00 | 2018-04-19 14:32 | Trending | An employee slipped on an icy surface without falling, after exiting a personal vehicle inside the company parking lot. The knee pain was later determined as occupational injury requiring surgery. | The cause of the knee injury was a slip on an icy parking lot surface. |  | 1 - For information only, industrial safety, injury | IS.1
WER ATL 18-0247 | 2018-04-17 10:20 | Pickering B7 | 2017-11-20 |  | Incorrect Coupling Hub Found Installed in Unit 7 East Fueling Machine Bridge Y-Drive Coupling Resulted in 31-Day Outage | 00 | 2018-04-17 10:20 | Trending | During normal operation and while performing fuelling, the east fuelling machine (FM) could not clamp onto a channel. Visual inspection revealed a FM bridge tilt in the north/south direction of approximately three inches, resulting in the FM not being able to move in the south direction. The reactor was shut down for troubleshooting. The event resulted in a 31-day outage. | The cause was installation of an incorrect hub into the FM bridge coupling. The root cause was substandard work instructions and not stopping the work after discovering it due to increased production pressure. The contributing cause was confusing work order wording. |  | 1 - For information only, fuelling machine, human error, procedure inadequacy, reactor shutdown | FA.1 , MA.1
WER ATL 18-0245 | 2018-04-17 10:18 | Pickering B5 | 2018-02-23 |  | High Boiler Pressure Caused Large Steam Release Valves to Open and Resulted in Forced Outage | 00 | 2018-04-17 10:18 | Trending | During normal operation, high boiler pressure caused the large steam release valves to open and the reactor setback to less than 2% power. The reactor was shut down for three days for troubleshooting. | The apparent cause was failure of the turbine electro hydraulic governor due to failure of its interface module relays as a result of ageing. The corrective action after a similar event in Unit 7 had not been implemented. |  | 1 - For information only, ageing, electro hydraulic control, governor valve, power reduction, reactor shutdown, relay | ER.3 , PI.3
WER ATL 18-0244 | 2018-04-17 10:17 | Pickering B7 | 2018-02-26 |  | Safety Relief Valve Isolation Led to Unexpected Unavailability of a Pair of Safety Relief Valves, Resulting in Unavailability of Steam Discharge Capacity | 00 | 2018-04-17 10:17 | Trending | During normal operation and when performing preventive maintenance of a steam generator safety relief valve (SRV), another SRV inadvertently opened and subsequently had to be put out of service. This resulted in an entry into limiting condition of operation as both SRVs were inoperable. The maintenance of the SRV had to be stopped. | The direct cause was an excess voltage present in the SRV control loop. The apparent cause was a gap in the SRV alignment procedure which was not adequately updated following equipment modification. Contributing factor was lack of understanding of the SRV configuration and operation during maintenance. | SER 2005-3 | 1 - For information only, design change, limiting condition of operation, procedure inadequacy, relief valve, risk assessment | CM.2 , CM.3
WER ATL 18-0241 | 2018-04-10 15:50 | Koeberg 1 | 2018-03-10 |  | Misalignment of In-Service Inspection Programme Requirement Monitoring activities linked to a Maintenance Intervention resulting in a statutory non-compliance. | 00 | 2018-04-10 15:50 | Trending | During an outage and while performing magnetic particle inspection of welds on a main steam isolation valve, one weld was not inspected as required by the inspection schedule. The weld exceeded its 10-yearly inspection frequency, resulting in a statutory non-compliance. | The cause was that maintenance task list could not be uploaded into the computer in time for the refuelling outage task download. A stand-alone notification was raised but an error in the in-service inspection database resulted in one weld instead of two having notifications raised for inspection during the outage. |  | 1 - For information only, human error, nondestructive examination, surveillance, weld, work control | EN.1 , WM.1
WER ATL 18-0239 | 2018-04-09 12:51 | Palisades 1 | 2017-12-09 11:30 |  | Employee Sustained Injury While Traversing Stairs | 00 | 2018-04-09 12:51 | Trending | While traversing snow covered stairs, an employee slipped and fell, resulting in a lost time injury. He was transported to the hospital for treatment. | The causes were overconfidence and lack of clear expectations to site personnel in regards to removing snow and ice before traversing over stairway. |  | 1 - For information only, human error, industrial safety, injury | IS.1
WER ATL 18-0238 | 2018-04-09 12:47 | Turkey Point 3 | 2017-05-04 03:20 |  | Power Reduction to Correct Unarmed Turbine Medium Runback | 00 | 2018-04-09 12:47 | Trending | During normal operation, a condensate pump breaker position input to the turbine control system (TCS) was found indicating the breaker was open while the pump was running. This defeated the TCS medium runback feature and the condensate pump recirculation control valve auto-control capability. The unit was down powered to 82% to allow for repairs and adjustments. | The cause was mechanism-operated cell (MOC) switch actuating fork having a larger than design gap which allowed the MOC switch pin to travel and give a wrong indication. The contributing cause was the slightly bowed plastic guide which holds the MOC actuating fork outward toward the MOC switch pin. The other cause was inadequate preventive maintenance procedure. |  | 1 - For information only, breaker, condensate pump, digital control system / digital components, power reduction, preventive maintenance, procedure inadequacy, switch, turbine control | ER.2 , MA.2
WER ATL 18-0236 | 2018-04-09 12:21 | Point Lepreau 1 | 2017-10-03 |  | Manual Reactor Shutdown due to Governor Valve Failure | 00 | 2018-04-09 12:21 | Trending | During normal operation, a turbine governor valve was found cycling open and close. An attempt to close the valve after reducing reactor power to 93% was unsuccessful. A reactor setback on high boiler pressure occurred and at 35% power the reactor was manually scrammed. | The cause was failure of a servo valve, which controls the governor valve operation. Investigation of a previous event (WER ATL 17-1172) revealed that contaminates in the turbine hydraulic fluid due to inadequate chemistry control were causing governor valves sticking and erratic operation. |  | 2 - Important lessons, chemistry, debris / crud, electro hydraulic control, governor valve, hydraulic fluid, manual scram | CY.2 , ER.2 , PI.2
WER ATL 18-0231 | 2018-04-04 13:43 | Waterford 3 | 2017-09-17 06:21 |  | Emergency Feedwater to Steam Generator Backup Isolation Valve Opened Unexpectedly | 00 | 2018-04-04 13:43 | Trending | During normal operation, a backup isolation valve of the emergency feedwater to a steam generator unexpectedly failed open . The valve could not perform its required containment isolation closure functions in the event of steam or feed line loss. This resulted in an entry into a limiting condition of operation. | The apparent cause was a solenoid valve coil failure. |  | 1 - For information only, containment isolation, emergency feedwater, isolation valve, limiting condition of operation, solenoid valve | ER.1
WER ATL 18-0230 | 2018-04-04 13:27 | Indian Point 2 | 2018-01-03 14:16 |  | Nuclear Plant Operator Injures Finger While Moving Boron Barrels | 00 | 2018-04-04 13:27 | Trending | While an operator was moving barrels containing boron from a pallet to a staging location, one of his fingers was caught in a pinch point between the barrel top and a cross beam on a nearby wall. The operator was transported to a hospital for medical treatment. | The cause was failure to sufficiently recognize and communicate hazards associated with work and a lack of overall oversight of the activity. |  | 1 - For information only, human error, industrial safety, injury, management oversight, risk assessment | IS.1 , MA.2
WER ATL 18-0229 | 2018-04-04 13:09 | Prairie Island 2 | 2017-09-18 01:06 |  | Unit Downpower due to Turbine Oil Leak | 00 | 2018-04-04 13:09 | Trending | During normal operation, a leak was identified on the main lube oil pump discharge piping. The main turbine was taken offline for two days for repair. The reactor was stabilised at 7% power. | The cause was inadequate weld quality in a pipe interconnection which led to a crack in the weld. The weld was from original plant construction. A loose pipe hanger for this area was a potential contributor. |  | 1 - For information only, leak, lube oil, power reduction, turbine trip, weld | ER.2 , ER.3 , MA.1
WER ATL 18-0228 | 2018-04-04 13:04 | Quad Cities 1 | 2017-11-16 18:13 |  | Control valve Taken Out of Service Prior to Failing | 00 | 2018-04-04 13:04 | Trending | During operation at reduced power of 87% for generation load following, power was lowered to 68% to perform corrective maintenance on a main turbine control valve due to a loosen servo valve cable connector. | The direct cause was loosening of the servo valve cable due to high vibrations. The root cause was inadequate risk assessment and analysis during implementation of associated design modification. The other root cause was inadequate operating experience feedback process with delayed implementation of corrective actions. | SER 2005-03 | 1 - For information only, control cable, design change, power reduction, risk assessment, turbine control valve, vibration | CM.3 , PI.3
WER ATL 18-0227 | 2018-04-04 13:01 | Grand Gulf 1 | 2017-12-05 05:35 |  | Reactor Shutdown Due to Loss of Drywell Cooling Fan Cooler | 00 | 2018-04-04 13:01 | Trending | During startup, a drywell cooling fan tripped while another cooling fan was already unavailable and scheduled for replacement in next refuelling outage. The reactor was shut down for five additional days to carry out repair or replacement of the drywell cooling fans. | The cause of failure of both fans was short circuits. |  | 1 - For information only, drywell, fan, heating ventilating and air conditioning, outage extension , reactor shutdown | ER.1 , OF.1
WER ATL 18-0226 | 2018-04-04 12:57 | Callaway 1 | 2017-11-13 04:00 |  | Main Generator Stator Rewind High Potential Test Failure | 00 | 2018-04-04 12:57 | Trending | During a refuelling outage and following the main generator stator rewind, electrical high potential testing of the main generator phase connection insulation failed to meet the standard post-change testing specifications. This resulted in a 14-day outage extension. | The cause was that the new generator stator winding configuration made application of insulation difficult due to close proximity to the phase connectors. The contributing cause was over-confidence and untimely recognition of first of a kind design by the contractor. The other cause was acquisition of the generator rewind contractor by the manufacturer, which impacted insulation application because the contractor procedure were very generic in nature and the manufacturer oversight personnel were not knowledgeable with the design developed by the contractor. |  | 1 - For information only, contractor, insulation electrical, management oversight, outage extension , risk assessment, stator, turbine generator, vendor | MA.1 , MA.2 , OR.2 , PM.1
WER ATL 18-0224 | 2018-04-04 12:43 | Browns Ferry 1 | 2017-04-06 01:00 |  | Power Reduction to Support Condenser Waterbox Cleaning | 00 | 2018-04-04 12:43 | Trending | During normal operation, condenser vacuum was found decreased. The unit was down powered to 83% to isolate and clean condenser waterboxes to improve condenser vacuum. | The cause was fouling of the condenser tubes. |  | 1 - For information only, condenser tube, condenser vacuum, power reduction | ER.1
WER ATL 18-0223 | 2018-04-04 12:39 | Monticello 1 | 2017-11-14 |  | Loss of Reactor Protection System Scram Function During Main Steam Isolation Valve and Turbine Stop Valve Testing | 00 | 2018-04-04 12:39 | Trending | During normal operation, it was determined that the use of a test fixture in two reactor protection system (RPS) surveillance procedures bypass a reactor scram initiation signal following a closure of some combinations of three main steam lines or turbine stop valves. This resulted in the loss of RPS function during the quarterly surveillance tests and conditions not allowed by technical specifications. | The apparent cause was that the RPS surveillance procedures were inappropriately revised eight years ago, not recognising that the test fixtures disable two reactor scram functions. | SER 2005-03 | 2 - Important lessons, design change, human error, procedure inadequacy, reactor protection system, risk assessment, surveillance, technical specification | CM.3 , EN.2
WER ATL 18-0222 | 2018-04-03 15:55 | Prairie Island 1 | 2017-09-26 23:42 |  | Indicated Quadrant Power Tilt Ratio Exceeded the Tech Spec Limits | 00 | 2018-04-03 15:55 | Trending | While reducing power for condenser tube cleaning and leakage repair and at 60% power, the quadrant power tilt ratio alarm came in due to excore channel upper detector indicating a tilt greater than the technical specification limit. This resulted in entry into a limiting condition of operation. | The cause was change in the power distribution within the core as power was reduced, resulting in increase in tilt which was not anticipated. | SOER 2013-1 Rec 3 | 1 - For information only, flux tilt, limiting condition of operation, reactivity management | OP.1
WER ATL 18-0221 | 2018-04-03 15:26 | Grand Gulf 1 | 2017-12-12 09:22 |  | Reactor Core Isolation Cooling Trip After Transformer Lockout | 00 | 2018-04-03 15:26 | Trending | During normal operation, an engineered safety feature transformer lockout caused isolation of reactor core isolation cooling (RCIC) system. This resulted in an entry into a limiting condition of operation. | The direct cause was a temperature switch design flaw. The leak detection temperature switches actuated and de-actuated instantaneously upon loss and restoration of power and since the condition persisted for a time period greater than the existing logic time delay, RCIC isolation occurred. The other cause was lack of a rigorous post modification test plan. |  | 1 - For information only, design change, design criteria / design basis, limiting condition of operation, reactor core isolation cooling , switch, vendor | CM.3 , ER.1
WER ATL 18-0220 | 2018-04-03 15:20 | North Anna 2 | 2017-12-10 05:47 |  | Unit Shut Down as a Result of Reactor Vessel Level Indication System Bellows Flange Leakage. | 00 | 2018-04-03 15:20 | Trending | During normal operation, a reactor coolant system leak was identified from the reactor vessel level indication system (RVLIS) bellows. This resulted in an entry into a limiting condition of operation. The reactor was shut down to carry out repair. | The cause was degradation of O-rings and nickel gasket due to ageing. |  | 1 - For information only, ageing, gasket, leak, level instrument, limiting condition of operation, o-ring , reactor coolant, reactor shutdown | ER.3
WER ATL 18-0219 | 2018-04-03 15:17 | Mcguire 1 | 2017-12-14 13:00 |  | Employee Fell from Scaffold Ladder Resulting in OSHA Recordable Injury | 00 | 2018-04-03 15:17 | Trending | While climbing a scaffold ladder, a technician lost his balance and fell to the ground. He suffered a hip fracture. | The apparent causes were an inadequate procedure, which did not guide scaffold builders to erect scaffold by using swing gates and false assumptions that the work required a scaffold. Contributing causes were differences between nuclear and non-nuclear scaffold programmes and differences in expectations. |  | 1 - For information only, industrial safety, injury, procedure inadequacy, scaffold | IS.1 , MA.2
WER ATL 18-0218 | 2018-04-03 15:12 | Oyster Creek 1 | 2018-01-06 05:24 |  | Declaration of Unusual Event Due to Abnormally Low-Tide | 00 | 2018-04-03 15:12 | Trending | During normal operation, an abnormally low-tide caused the intake level to drop to the threshold for declaring an unusual event. The unit power was reduced to 70% and one circulating water pump was removed from service. | The cause of the abnormally low tide was a combination of the tidal cycle, wind speed and direction and low atmospheric pressure. | SOER 2002-1 Rec 1 | 1 - For information only, intake, power reduction | ER.1
WER ATL 18-0217 | 2018-04-03 10:30 | Bruce B 8 | 2018-01-08 |  | Worker pinched finger on Turbine Lube Oil access hatch | 00 | 2018-04-03 10:30 | Trending | While opening the turbine lube oil tank hatch cover to perform the tank level reading, a worker's right hand finger was pinched between the hatch cover and the turbine lube oil return header pipework located directly adjacent to the hatch. He was sent to a local hospital, where the tip of the smallest finger was found fractured. | The cause was lack of focus and situational awareness of the task and ineffective pre-job briefing. |  | 1 - For information only, human error, industrial safety, injury | IS.1
WER ATL 18-0216 | 2018-04-03 10:30 | Bruce B 5 | 2018-01-19 |  | Firewater check valve found installed in the wrong direction during inspection | 00 | 2018-04-03 10:30 | Trending | During normal operation and while performing preventive maintenance, a firewater check valve was found installed in the wrong direction. The check valve provides firewater to 11 firewater hose connections in Unit 0 stairwells. The event resulted in a firewater system impairment since firewater would not have been available at this location had it been required. | The cause was human error as the check valve was incorrectly installed during last overhaul in 2013 or previously. |  | 1 - For information only, check valve, configuration control, fire suppression, human error | CM.2 , FP.1 , MA.1
WER ATL 18-0214 | 2018-04-02 12:11 | Bruce B 6 | 2018-01-02 |  | Fueling Machine Head unable to unclamp from Unit 6 | 00 | 2018-04-02 12:11 | Trending | During normal operation and after performing fuelling, a fuelling machine head was unable to unclamp from a reactor channel. The reactor was shut down for 53 hours for troubleshooting. | The cause was failure of the torque limiter in the disengaged position. The other cause was legacy engineering change requirements. The failure modes of the torque limiter were not fully analysed at the time of its installation in 2009 as they are at present in the engineering change control process. Inadequate preventive maintenance was a contributor. |  | 1 - For information only, fuelling machine, reactor shutdown, torque | EN.1 , ER.2 , FA.1
WER ATL 18-0213 | 2018-04-02 12:04 | Darlington 1 | 2018-01-20 |  | Passing Check Valve resulted in a Loss of Heatsink to Steam Generator # 1 | 00 | 2018-04-02 12:04 | Trending | The unit was in a planned outage, when a loss of backup heatsink on one steam generator (SG) was declared as temperature in SG emergency cooling flow path reached 170 degree C, exceeding the allowed value of 146.8 degree C. This was caused by two passing check valves of SG emergency cooling system. As a result, the unit outage configuration had to be modified to lower the temperature. | The direct cause was internal leak of two check valves. The apparent cause was that previous actions taken to address similar problem of these valves were not effective. The contributing factor was a potential manufacturer parts issue. |  | 1 - For information only, check valve, decay heat removal, emergency feedwater, leak, spare part, steam generator / boiler, vendor | ER.3 , PI.2

## Other
OE Reports
Event Summary Monthly by Significance (2018 April)
Report Identifier (click to view report) | Original Published Date | Reference Unit | Event Date |  | Event Title | Revision Number | Revision Published Date | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 18-0147 | 2018-04-27 01:16 | Qinshan 2 4 | 2018-02-15 |  | Leakage at Non-drive End of Main Motor-driven Feedwater Pump | 00 | 2018-04-27 01:16 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0146 | 2018-04-27 00:39 | Qinshan 3 2 | 2018-01-25 |  | Jam of Air Distributor Valve Caused the Failure of Automatic Opening of Hatch | 00 | 2018-04-27 00:39 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0145 | 2018-04-26 23:44 | Qinshan 3 1 | 2018-02-18 |  | Isolation Valve Failed to Open Normally due to Internal Fault | 00 | 2018-04-26 23:44 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0142 | 2018-04-12 23:03 | Fuqing 3 | 2018-01-24 |  | Post-weld Penetrant Testing was not Performed for Weld After Modification | 00 | 2018-04-12 23:03 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0141 | 2018-04-12 22:50 | Fangjiashan 2 | 2018-01-12 |  | Level High High High Alarm Caused Isolation of High Pressure Heater | 00 | 2018-04-12 22:50 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0139 | 2018-04-11 21:16 | Higashidori (TOHOKU) 1 | 2018-02-02 |  | Water leak during water filling work after completing the inspection of the fuel pool cooling and cleanup system | 00 | 2018-04-11 21:16 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0138 | 2018-04-11 20:48 | Onagawa 1 | 2018-03-16 |  | Some errors in meteorological data on precipitation | 00 | 2018-04-11 20:48 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 18-0137 | 2018-04-05 22:10 | Sanmen 2 | 2017-12-05 |  | Low Pressure of Auxiliary Steam Led to Breaking of Condenser Vacuum | 00 | 2018-04-05 22:10 | Other | See summary below | See causes below |  | 1 - For information only
WER PAR 18-0186 | 2018-04-23 09:32 | Ringhals 4 | 2018-01-11 |  | Deficiency in organisation concerning handling of demounted Wide Range detector. | 00 | 2018-04-23 09:32 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0183 | 2018-04-23 09:24 | Atucha 2 | 2017-11-27 |  | A spray valve of the Pressurizer is much more actuated than its other 3 redundancies. | 00 | 2018-04-23 09:24 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0182 | 2018-04-23 09:19 | Cofrentes 1 | 2017-10-24 |  | Incomplete testing associated with electrical surveillance requirements. | 00 | 2018-04-23 09:19 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0180 | 2018-04-23 09:17 | Torness 1 | 2018-02-02 |  | Excitation of the turbine generator failed to initiate during return to service | 00 | 2018-04-23 09:17 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0178 | 2018-04-23 09:16 | Torness 1 | 2018-01-28 |  | Turbine Generator 1 Main Lubricating Oil Pressure Transient | 00 | 2018-04-23 09:16 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0171 | 2018-04-23 09:08 | Hartlepool 2 | 2017-12-01 |  | Gas Circulator Motor Winding Temp Trip Amp Lifters set Incorrectly | 00 | 2018-04-23 09:08 | Other | See summary below | See causes below |  | 1 - For information only
WER PAR 18-0170 | 2018-04-19 05:34 | Krsko 1 | 2018-01-11 |  | Feedwater chemical addition pump motor replacement difficulties | 00 | 2018-04-19 05:34 | Other | See summary below | See causes below |  | 1 - For information only
WER PAR 18-0169 | 2018-04-17 09:00 | Sellafield - Magnox East River 1 | 2017-11-20 |  | Unauthorised modification to working at height Risk Assessment | 00 | 2018-04-17 09:00 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0168 | 2018-04-17 09:00 | Sellafield - Infrastructure 1 | 2017-08-31 |  | Incorrect Installation of Isolation Test Certificate | 00 | 2018-04-17 09:00 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0167 | 2018-04-17 08:59 | Emsland 1 | 2017-10-25 |  | Damage to diaphragm valves caused by throttling mode | 00 | 2018-04-17 08:59 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0166 | 2018-04-17 08:53 | Atucha 2 | 2017-11-28 |  | Repeated Trips and switchovers of pumps of the Volume Control System). | 00 | 2018-04-17 08:53 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0165 | 2018-04-17 08:52 | Torness 1 | 2018-02-04 |  | Failure of contaminated air extract fan | 00 | 2018-04-17 08:52 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0164 | 2018-04-17 08:51 | Torness 2 | 2018-01-09 |  | Incorrect wiring to 250V dc emergency lighting | 00 | 2018-04-17 08:51 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0163 | 2018-04-17 08:51 | Torness 2 | 2017-12-01 |  | Sodium hypochlorite pipework leak in cooling water forebay | 00 | 2018-04-17 08:51 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0162 | 2018-04-17 08:50 | Heysham B1 | 2017-11-15 |  | High total residual oxidant reading at reactor sea water discharge | 00 | 2018-04-17 08:50 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0161 | 2018-04-17 08:49 | Bugey 2 | 2017-12-21 |  | Trace amounts of tritium found in groundwater | 00 | 2018-04-17 08:49 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0160 | 2018-04-17 08:49 | Ningde 3 | 2017-10-16 |  | Oil Leakage Caused by Weld Fracture in Seal Oil Inlet Pipe of the No.7 Bearing Shell in the Turbine Generator | 00 | 2018-04-17 08:49 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0158 | 2018-04-17 08:47 | Ningde 3 | 2017-08-12 |  | High Bearing Temperature Tripped a Drain Pump of Feedwater Heaters Drain Recovery System | 00 | 2018-04-17 08:47 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0157 | 2018-04-17 08:46 | Ningde 1 | 2017-08-05 |  | Oil Leakage of the Hose of a Turbine Governing Valve | 00 | 2018-04-17 08:46 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0156 | 2018-04-17 08:45 | Ningde 1 | 2017-07-20 |  | The Level of Volume Control Tank in Chemical and Volume Control System Unexpectedly Decreased | 00 | 2018-04-17 08:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0154 | 2018-04-17 08:45 | Ningde 2 | 2017-06-07 |  | Grid Synchronization and Connection System Fan Failure and Burnout | 00 | 2018-04-17 08:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 18-0153 | 2018-04-17 08:43 | Ningde 1 | 2017-05-23 |  | Containment Sweeping Ventilation System Spurious Shutdown by a Radioactivity Detector’s Processor Overflow | 00 | 2018-04-17 08:43 | Other | See summary below | See causes below |  | 1 - For information only
WER PAR 18-0143 | 2018-04-12 07:25 | Almaraz 1 | 2018-02-09 |  | Spent fuel container movements using the fuel building cask crane without previously performing Surveillance Requirements. | 00 | 2018-04-12 07:25 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 18-0086 | 2018-04-30 16:45 | Mochovce 1 | 2018-04-25 |  | A foreign material was found in the absorber part of the control rod. | 00 | 2018-04-30 16:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 18-0082 | 2018-04-25 14:47 | Tianwan 2 | 2018-01-23 |  | Air release pre-isolating valve of turbine in Unit 2 is unable to reseat after opening | 00 | 2018-04-25 14:47 | Other | See summary below | See causes below. |  | 1 - For information only
WER MOW 18-0081 | 2018-04-25 14:23 | Tianwan 2 | 2018-01-20 |  | The bypass valve of Unit 2 turbine was not removed from the closure limit during the activity test. | 00 | 2018-04-25 14:23 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 18-0080 | 2018-04-25 13:45 | Kola 1 | 2018-01-17 |  | Incorrect Low Pressure Heater Level Meter Indications Due to Cold Air Ingress into the Turbine Hall | 00 | 2018-04-25 13:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 18-0073 | 2018-04-18 00:20 | Tianwan 3 | 2018-01-21 |  | The blade of cooling fan 30BAT13AN012 of main transformer ruptured. | 00 | 2018-04-18 00:20 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 18-0068 | 2018-04-09 13:31 | Balakovo 3 | 2018-01-05 |  | A Limit Switch Failure to Actuate Resulted in Containment Bridge Crane Load Trolley Damage | 00 | 2018-04-09 13:31 | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 18-0064 | 2018-04-05 14:44 | Temelin 1 | 2018-01-11 |  | Foreign material in cold header of steam generator | 00 | 2018-04-05 14:44 | Other | See summary below | See causes below |  | 1 - For information only
WER MOW 18-0019 | 2018-02-13 23:47 | South Ukraine 1 | 2018-02-08 |  | High Pressure Heaters HPH 6A and HPH6B removed from service for unplanned repairing | 01 | 2018-04-25 13:54 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0277 | 2018-04-30 12:31 | Pickering A4 | 2018-04-10 |  | Solenoid Valve Found Charred | 00 | 2018-04-30 12:31 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0276 | 2018-04-30 07:57 | Laguna Verde 1 | 2018-03-03 |  | Auto-Transformer oxygen concentration increasing trend | 00 | 2018-04-30 07:57 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0275 | 2018-04-30 07:56 | Laguna Verde 1 | 2017-12-03 |  | Forced variable of Reactor Recirculation Control System Programmable Logic Controller causes blockage of Reactor Recirculation Control Valve | 00 | 2018-04-30 07:56 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0274 | 2018-04-27 13:45 | Bruce A 4 | 2018-03-30 |  | High Pressure Recirculation Water Leak | 00 | 2018-04-27 13:45 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0273 | 2018-04-27 13:43 | Bruce A 1 | 2018-02-20 |  | Foreign Material Found on Tube Side of Heat Exchanger | 00 | 2018-04-27 13:43 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0272 | 2018-04-27 13:42 | Bruce A 1 | 2018-02-20 |  | Worker Electrical Contact with Light Fixture | 00 | 2018-04-27 13:42 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0268 | 2018-04-27 12:24 | Bruce B 5 | 2018-02-10 |  | Tank draining to Active Drainage incident | 00 | 2018-04-27 12:24 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0265 | 2018-04-25 13:04 | Browns Ferry 1 | 2017-09-25 01:00 |  | Temporary Downpower to Return Reactor Feedwater Pump Turbine to Service | 00 | 2018-04-25 13:04 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0260 | 2018-04-25 12:30 | Koeberg 2 | 2018-03-05 |  | The Unit 2 Boron Recycle System pump was damaged due to lack of cooling flow through it. | 00 | 2018-04-25 12:30 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0256 | 2018-04-24 12:32 | Koeberg 1 | 2018-03-18 |  | Damage to the railing of the Reactor Building Fuel Handling and Storage crane. | 00 | 2018-04-24 12:32 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0255 | 2018-04-24 12:17 | Darlington 2 | 2018-02-28 |  | Common Cause Review Darlington Refurbishment Material Handling Equipment Events Resulting in an Increased Risk to Personnel Safety | 00 | 2018-04-24 12:17 | Other | See summary below | See causes below |  | 1 - For information only
WER ATL 18-0254 | 2018-04-24 12:16 | Darlington 1 | 2018-02-16 |  | Increased Trend of Fuelling Machine Input Drives Failures | 00 | 2018-04-24 12:16 | Other | See summary below | See causes below |  | 1 - For information only
WER ATL 18-0251 | 2018-04-19 14:43 | Oyster Creek 1 | 2017-11-29 19:35 |  | Plant Down-Power to Investigate Feedwater Heater Low Pressure Signal | 00 | 2018-04-19 14:43 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0246 | 2018-04-17 10:19 | Pickering B6 | 2018-02-02 |  | Spurious Shutdown System Channel Trip during Guaranteed Shutdown State | 00 | 2018-04-17 10:19 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0243 | 2018-04-16 09:54 | Point Lepreau 1 | 2017-11-14 |  | Leak of FRF Fluid from 4119-GV-7 during Maintenance | 00 | 2018-04-16 09:54 | Other | See summary below | See causes below |  | 1 - For information only
WER ATL 18-0242 | 2018-04-12 12:00 | Cernavoda 2 | 2018-02-22 |  | Service Building Lighting Panel for Safeguards 2-5622-LP23 remained unpowered after maintenance activities | 00 | 2018-04-12 12:00 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0237 | 2018-04-09 12:44 | Oyster Creek 1 | 2018-01-18 21:28 |  | Plant Downpower Due to Reactor Recirculation Pump Trip | 00 | 2018-04-09 12:44 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0235 | 2018-04-06 08:34 | Koeberg 1 | 2018-02-05 |  | Potential adverse trend of Instrumentation and Control failures over the period 01 January 2017 to 31 January 2018 was identified by the Station Corrective Action Review committee on 05 February 2018 | 00 | 2018-04-06 08:34 | Other | See summary below | See causes below |  | 1 - For information only
WER ATL 18-0234 | 2018-04-06 08:33 | Koeberg 2 | 2018-02-26 |  | Contamination was found on Chemistry individual | 00 | 2018-04-06 08:33 | Other | See summary below | See causes below |  | 1 - For information only
WER ATL 18-0233 | 2018-04-06 08:31 | Koeberg 1 | 2018-03-24 |  | A break in barriers led to a Permit to Work being issued while the plant was still energised. | 00 | 2018-04-06 08:31 | Other | See summary below | See causes below |  | 1 - For information only
WER ATL 18-0232 | 2018-04-04 14:52 | Point Lepreau 1 | 2018-01-09 |  | 120V Electrical Shock at Off Site Fresh Water Pumphouse | 00 | 2018-04-04 14:52 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0225 | 2018-04-04 12:48 | Browns Ferry 1 | 2017-07-07 |  | Downpower to Address Leaking Reactor Feedwater Valve | 00 | 2018-04-04 12:48 | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 18-0215 | 2018-04-03 10:27 | Darlington 3 | 2018-01-18 |  | Replacement of Main Steam Condenser Tube Plugs Resulted in a Unit Transient | 00 | 2018-04-03 10:27 | Other | See summary below. | See causes below. |  | 1 - For information only