## Information
***Information Regarding the OE Monthly Summary Report*** The OE monthly summary provides a monthly update of all of the events submitted to WANO in that month. The Operating Experience Central Team in London reviews and summarises all of the operating experience reports submitted, and creates a summary report that is separated into the following three categories: • Significant events • Noteworthy events • Events for Trending • Other events The four different categories are sorted onto individual spreadsheets within this file. The summary includes a short description of the event, the event causes, and a short list of keywords in a spreadsheet. The monthly summaries are combined into annual summaries for general use. The OE monthly summary is available on the website under the ‘monthly OE information’ link. To begin reviewing the OE Monthly Summary Report, simply select one of the worksheet tabs at the bottom of the screen. A few helpful hints: To search a single worksheet, simply use the 'Ctrl-F' search tool To search the entire work book, use 'Ctrl-F', then select 'options' and change the search from 'Within: Sheet' to 'Within: Workbook' To print the entire work book, use file, print - then select 'entire workbook' under the 'print what' selection box Please forward any questions or comments you may have to oect@WANO.org

## Significant
Reference Posted in 2015 | Event Date (DD/MM/YY) | Reference Unit | Title | Short Description (what happened and the consequences) | Causes | Keywords | OECT Reference | PO&Cs
The following events are considered significant
WER ATL 15-0465 | 2015-02-02 | LaSalle 2 | Reactor Recirculation Pump Discharge Isolation Valve Failed to Close | During an outage, a reactor recirculation (RR) discharge isolation valve failed to be closed on demand. This resulted in a dose accumulation of 250 mSv and a 13 hour impact on outage critical path. This is significant because the high level and unplanned&nbsp;accumulated dose. | The direct cause was the valve disc fretting into the valve body integral guides, creating a ledge in the guides which allowed the disc to become mechanical bound. The apparent cause was that the flow induced vibration as a result of being located immediately downstream of the throttled flow control valve. 2h | disk,flow induced vibration,isolation valve,recirculation |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3);

## Noteworthy
Reference Posted in 2015 | Event Date (DD/MM/YY) | Reference Unit | Title | Short Description (what happened and the consequences) | Causes | Keywords | OECT Reference | PO&Cs
The following events are noteworthy based on their consequences, causes, or on-going areas of interest to the industry.
WER PAR 15-0274 | 2015-03-20 | Gravelines 5 | Isolated case of worker contamination resulting in his skin being exposed to more than one quarter of the statutory annual individual dose limit. | During an outage, a contractor head was found contaminated in the radiological controlled area exit monitor. The skin equivalent dose was calculated to be 401.5mSv which is greater than 50% of the annual individual dose limit (500mSv) making this event Noteworthy. | The most probable cause of the event was a likely transfer of contamination during the dress-out process at the exit of contaminated areas. Immediate contamination control was not performed after undressing the additional protective cloth. | ALARA,contamination control,contractor,decontamination |  | RADIOACTIVE CONTAMINATION CONTROL (RP.3); RADIOLOGICAL SAFETY (RS.1);
WER MOW 15-0079 | 2015-04-30 | Paks 1 | #PRELIMINARY# Detecting of foreign objects in the annular cavity of the steam generator header during the scheduled maintenance outage | During an outage and when purging of a steam generator hot header annular cavity to perform ultrasonic testing, two lead shielding parts for radiation protection were found in the collector pocket of the blowdown pipeline. In addition, significant amount of magnetite needed to be removed out of the collector pocket. The event is classified as noteworthy because of its widespread interest. | Lead shielding blankets were left in the steam generator during work performed in 2011. | FME,lead,shielding,steam generator |  | CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0442 | 2015-05-09 | Indian Point 3 | #PRELIMINARY# Unusual Event Declared and Automatic Scram due to Main Transformer Fire | During normal operation, a fire occurred on the main transformer resulting in an automatic reactor scram. An unusual event was declared and offsite fire fighting assistance was requested. The fire was extinguished after 14 minutes. Subsequently, the transformer oil mixed with fire water overflowed the berm into the discharge canal and made its way into the river. This event is classified as noteworthy because of the widespread interest. | The cause is under investigation. | environment,fire,leak,oil,automatic scram,transformer |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0411 | 2013-07-01 | Koeberg 1 | The Emergency Diesel Generator spare parts supplied to Koeberg by contractor not meeting the design specification/classification. | The air starter motors for emergency diesel generators (EDGs) procured from a vendor were found not qualified to meet the design requirements. This resulted in all 5 EDGs being declared 'operable but degraded' for the non-conforming air starter motors installed on the EDGs. This event is classified as Noteworthy because it is a common mode failure that affected all EDG and the widespread interest to other stations. | The direct cause was that the vendor no longer manufactured, qualified and supplied nuclear-grade starter motors to the nuclear industry. They currently supply only commercial grade motors. The root cause was that customer requirements were not properly considered by the vendor's project manager. Engineering was not sufficiently involved in the procurement process. | air start,diesel generator,motor,spare part,vendor | SOER 2002-2 Rec 6 | ENGINEERING FUNDAMENTALS (EN.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3);

## Trending
Reference Posted in 2015 | Event Date (DD/MM/YY) | Reference Unit | Title | Short Description (what happened and the consequences) | Causes | Keywords | OECT Reference | PO&Cs
The following events are identified for trending purposes and may be of interest to the industry
WER PAR 15-0278 | 2014-09-14 | Forsmark 3 | Non-operational activity measurement in active workshop | During testing of switching and automatic start sequence on one electrical rail, activity measurement in active workshop chimney stopped while the washing of heat exchanger plates was in progress. The event resulted in violation of technical specification. | The direct cause was power interruption during the test. The contributing factor was deficiency in operational instructions. | procedure deficiency,radiation monitor,technical specification,voltage |  | CONDUCT OF OPERATIONS (OP.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER PAR 15-0277 | 2014-09-03 | Forsmark 3 | EDG not ready for operation | During a regular load test of the emergency diesel generator (EDG) during an outage, abnormal voltage and current values were observed. The EDG was stopped and declared inoperable causing deviation from the technical specification with respect to the number of operational subsystems may not be less than two. | The direct cause was short circuit in all the diodes on the negative side of the exciter rectifier. Inadequate preventive maintenance and component ageing were contributors. Similar event had occurred twice in the past. | ageing,diesel generator,diode,preventive maintenance,rectifier,short circuit,technical specification |  | EQUIPMENT FAILURE PREVENTION (ER.2); LONG-TERM EQUIPMENT RELIABILITY (ER.3); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
WER TYO 15-0065 | 2015-04-06 | Shin-Wolsong 2 | TBN-GEN tripped by integrated differential relay malfunction | During full power commissioning and while performing power ascension test, integrated differential relay malfunction resulted in turbine generator trip. The reactor power was decreased to 50% immediately and stabilised at 37% by control system. | The cause of the generator trip was input module failure for switchyard circuit breaker current signal. The root cause was differential current by input current waveform distortion that induced integrated differential relay malfunction. The distortion was caused by bad current input module or possibility of analog/digital conversion error. | circuit breaker,differential relay,power reduction,switchyard,turbine trip |  | EQUIPMENT PERFORMANCE (ER.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER PAR 15-0275 | 2015-03-12 | Chinon B1 | Presence of a drum containing waste with a hot spot greater than 50 mSv/h on contact without orange area marking off in the room | A waste drum caused high dose of 95 mSv/h on contact without control of access. | The direct cause was removing a screen of lead blankets from the drum to install for another high dose drum due to lack of communication and lack of questioning attitude. | human performance,radiation protection | SOER 2001-1 Rec 8 | RADIATION DOSE CONTROLS (RP.2); RADIOLOGICAL SAFETY (RS.1);
WER MOW 15-0097 | 2015-05-16 | Tianwan 2 | #PRELIMINARY# Negative pressure loss in Unit 2 containment | During cooling down for refuelling outage and while transporting equipment to the containment building through the equipment air lock, the outer door was still open by approximately 10 cm when the inner door was opened. This resulted in loss of negative pressure in the containment. | The cause was combination of wrong operation mode of the air lock and mistakes of the operators. Under this operating mode, there is no interlock for forbidding simultaneous opening of inner and outer door. The operator did not follow the procedure. The inner door operator opened the door due to wrong assumption. | air lock,communication,containment integrity,human error,misposition |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1);
WER MOW 15-0098 | 2015-05-16 | Tianwan 2 | #PRELIMINARY# Action of Unit 2 CE11 (System isolation in case of earthquake) | While the unit was cooling down for refuelling outage, reactor scram and seismic isolation system triggered due to earthquake signal actuation. | The direct cause of an earthquake signal actuation was falling down of a heavy concrete plate due to cracking of crosstie. Lack of requirements for inspection, maintenance and management of crossties was a contributor. | earthquake,plate,procedure deficiency,automatic scram |  | EQUIPMENT FAILURE PREVENTION (ER.2);
WER PAR 15-0271 | 2015-03-10 | Dampierre 1 | Near miss further to the fall of biological shielding from a height of 3 meters | A shell and its biological shielding on the filter deck at level 13.5 m were lifted to transfer through the hatch at level 0 m. After the first movement, the biological shielding came away from the shell and fell by approximately 3m from the filter deck. | The mounting system of the biological shielding on the shell was defective. | industrial safety,lifting device | SOER 2008-1 Rec 3 and 5 | INDUSTRIAL SAFETY (IS.1);
WER ATL 15-0495 | 2015-03-02 | Chalk River NRU 1 | Incorrect Safety System Equipment Installed and Subsequent Failure | During shutdown, two control rod module relays were received from the manufacturer, placed into service, and subsequently failed. | The required relays were designed to break the current from a DC inductive load, whereas the received relays were not. The apparent cause was that the incorrect part number was not noticed by appropriate personnel, and that the relays were not tested with the same current during maintenance. | control rod drive,procurement,relay,spare part,test |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0169 | 2014-10-08 | Perry 1 | Individual Received Multiple Dose Rate Alarms in a Locked High Radiation Area (LHRA) | While working in a locked high radiation area, a worker received multiple dose rate alarms that were not acknowledged and work continued. No planned dose limits were exceeded. | The apparent cause was the worker did not apply the proper human performance error detection techniques when the unexpected dosimeter alarm vibrations were felt. Also, the worker did not communicate the unexpected alarms to the radiation protection technician who was monitoring the work. | dose rate,human error,radiation area,radiation work permit |  | RADIOLOGICAL SAFETY (RS.1);
WER PAR 15-0267 | 2014-11-19 | Heysham A2 | Fitting Failure Resulting in oil leak in 6FL1/CUB20 Hydraulic Cubicle | High pressure hydraulic fluid and pipe fitting components were ejected when a fitting failed following maintenance. This resulted in a near miss for the people working on the cubicle at the time. | The direct cause was that the fitting degraded due to o-ring failure. The orientation of the parts within the fitting was not correct. | circuit breaker,degradation,fitting,hydraulic fluid,industrial safety,maintenance error |  | INDUSTRIAL SAFETY (IS.1); MAINTENANCE FUNDAMENTALS (MA.1);
WER PAR 15-0266 | 2015-03-10 | Sizewell B 1 | Multi-Gas Meter found inside Essential Diesel Generator Engine Crankcase during Planned Maintenance | During planned maintenance on essential diesel generator a multi-gas meter was found hanging inside the engine crankcase, having been left there during a previous maintenance activity. The foreign object could have caused significant damage and lead to unplanned inoperability of safety related equipment. | This was an infrequently performed work activity and the work scope walk through was not performed. Work package did not address all administrative requirements. Failure to exclude foreign material during work was a contrbutor. | diesel generator,FME,foreign material,human error,work control |  | CONDUCT OF MAINTENANCE (MA.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER PAR 15-0264 | 2015-03-19 | Sizewell B 1 | Steam Generator Level Excursion due to loss of Main Feedwater Regulating Valve / Main Feed Pump Scoop Control | During normal operation and while repairing a defect on a high integrity control system (HICS) panel a technician switched off both dual redundant power supplies to the HICS panel. This resulted in loss of control for the main feedwater regulating valve and the main feed pump scoop. Neither manual or automatic control was available and steam generator levels began to oscillate. Power to the panel was restored in three minutes and the affected computer was restarted. | The technician used written work instructions that did not contain sufficient detail to work on the HICS panel. He was not clear on the required isolation and isolated the panel, instead of just the one half of the dual redundant supply. The impact assessment documentation for the HICS panel was inadequate and was not updated. | feedwater pump,feedwater valve,human error,power supply,regulating valve,steam generator |  | CONDUCT OF MAINTENANCE (MA.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER ATL 15-0492 | 2014-12-26 | Hope Creek 1 | Waterbox Reversing Chamber Leak Identified | During normal operation, a 15gpm leak from a condenser waterbox manway was observed. The leak could not be isolated because the outlet valve was stuck in the open position. This resulted in the plant reducing power to 80% to lower dose rates for repairs. | The leak was caused by failure of the vulcanised rubber coating on the manway. An area of the coating on the manway was missing which created a void in the sealing surface between the manway and the cover and provided a leak path out of the waterbox. | coating,condenser,leak,manway,power reduction,rubber |  | EQUIPMENT PERFORMANCE (ER.1); CONDUCT OF MAINTENANCE (MA.2);
WER PAR 15-0263 | 2015-03-06 | Ringhals 4 | Leaking hand hole on steam generator 2 at unit 4 | During plant startup, leakage was identified on the hand hole of a steam generator. The unit was shut down to address the problem. This was the second leakage since steam generator replacement in 2011. This resulted in loss of production equal of approximately 7 days. | The direct cause was that the specified residual pre-tension of the stud was too low. The vendor could not determine the cause for the stud relaxation. | leak,modification,reactor shutdown,steam generator,stud |  | DESIGN CHANGE PROCESSES (CM.3); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
WER PAR 15-0262 | 2015-01-19 | Asco 2 | Foaming in the Emergency Diesel Generator alternator oil | During the operability verification of the emergency diesel generator (EDG), the presence of a 10-12 centimetre thick layer of foam was detected inside the alternator oil tank. Several oil samples were taken and contaminant presence such as calcium was observed in the oil analysis. The EDG was declared inoperable. | The cause was the contamination of the oil by calcium particles stemmed from cement or concrete dust generated by the different civil works taking place on site. The air suction grilles in the ventilation units for the EDGs' rooms had no filters and during maintenance on the EDGs, the building's roller doors were lifted up, enabling the entry of dust into the rooms. | cement,concrete,diesel generator,FME,lubrication,oil,sample | SOER 2002-2 Rec 6 | CONDUCT OF MAINTENANCE (MA.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER PAR 15-0260 | 2014-12-11 | Dungeness B 2 | Water Spray Fire Pump 24 Claimed for Duty with Maintenance Schedule Work Outstanding | The water spray fire pump was inadvertently claimed for duty with a maintenance schedule work still outstanding causing non-compliance with the technical specification. | The direct cause was human error as the control room supervisor misunderstood the requirements of the interim hand over certificate (HOC) and reclaimed the pump with a maintenance schedule work that had not been signed off as completed. Wording in the HOC was ambiguous. | fire pump,human error,technical specification |  | MAINTENANCE FUNDAMENTALS (MA.1); OPERATIONS FUNDAMENTALS (OP.1); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER ATL 15-0115 | 2015-02-06 | Dresden 2 | Automatic Reactor Scram due to Loss of Feedwater | During normal operation and while connecting a test recorder to 5V DC power supply bus of the feed water level control (FWLC) to troubleshoot an event that occurred on 01/13/2015, power supply was interrupted, which caused the FWLC multi-function processors to lock up. This resulted in a reactor recirculation pump ran back and reactor pressure vessel (RPV) level increase. Finally, the reactor automatically scrammed on RPV level low. | The cause was a spurious power interruption on an improperly landed power supply ribbon cable connection for the FWLC system. The root cause was errors made during troubleshooting. | cable,feedwater control system,power supply,automatic scram,troubleshooting |  | EQUIPMENT PERFORMANCE (ER.1); MAINTENANCE FUNDAMENTALS (MA.1);
WER ATL 15-0491 | 2015-01-14 | Vogtle 2 | Engineering Safety Feature Chiller Cycling on Low Evaporator Water Temperature | During normal operation and when an engineering safety feature (ESF) chiller was started to support a monthly surveillance, the ESF chiller shut down and restarted roughly every 30 minutes. Operations declared the ESF chiller inoperable and entered a 72 hour shutdown limiting condition of operation (LCO). | The direct cause was failure of a relay for the hot gas bypass valve due to sticking contacts. Calibration and replacement frequency on preventive maintenance was not adjusted based on previous reliability issues. | chiller,contact,limiting condition of operation,preventive maintenance,relay |  | EQUIPMENT FAILURE PREVENTION (ER.2); LONG-TERM EQUIPMENT RELIABILITY (ER.3); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
WER ATL 15-0489 | 2015-03-23 | Susquehanna 2 | Motor Operated Butterfly Valve Failed to Close Due to Loss of Actuator to Valve Coupling Engagement | During normal operation and while attempting to shut down a reactor heat removal service water (RHRSW) pump, the RHRSW heat exchanger inlet isolation valve failed to close on demand. This resulted in RHRSW loop inoperability and the unit entered a 72 hour shutdown limiting condition for operation (LCO). | The direct cause was that the actuator output shaft became disengaged from the coupling connecting it to the valve shaft. The apparent cause was no preventive maintenance to address this failure mode and less than adequate procedure. | disconnect,limiting condition of operation,preventive maintenance,procedure inadequacy,residual heat removal,valve stem |  | EQUIPMENT FAILURE PREVENTION (ER.2); CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0486 | 2014-12-11 | Limerick 2 | Momentary Simultaneous Opening of Secondary Containment Airlock Doors | During normal operation, workers entered the refuel floor causing both secondary containment airlock doors to be opened at the same time. The containment breach lasted ten seconds and technical specification was entered. | The workers failed to verify that the inboard door was closed and latched prior to opening the outboard door. Lack of situational awareness and inattention to detail were contributors. | airlock,containment integrity,door,human error,technical specification |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1);
WER ATL 15-0484 | 2015-04-07 | Koeberg 1 | Reactor Coolant System pump motor potential common cause on low oil level after alarms sustained twice at full power within a period of five months | During normal operation, the motor bearing low oil level alarm of reactor coolant system pump sustained on oil tank. The power was reduced to below 50% to enter containment, top up the oil tank and clear the alarm. The reactor coolant pump motor low oil level alarm&nbsp;occurred twice at full power within a period of five months. The plant has modified its&nbsp;<span style="color: black; letter-spacing: 0.05pt; font-family: 'Arial','sans-serif'; font-size: 10pt;">procedure&nbsp;for&nbsp;topping up the lower motor oil level reservoir.</span> | The most probable cause&nbsp;is hot oil vapour and escape of the oil vapour between the labyrinth seal and the motor shaft. Technically incomplete documentation for topping up the oil reservoir was a contributor. | alarm,bearing,common mode failure,oil level,power reduction,procedure deficiency,reactor coolant pump motor |  | CONDUCT OF MAINTENANCE (MA.2);
WER TYO 15-0062 | 2014-10-23 | Kashiwazaki Kariwa 1 | Injury by being caught associated with boring operation at Kashiwazaki-Kariwa Nuclear Power Plant | During the geological survey, using the boring machine, a worker's hand was mistakenly caught in the equipment.The hand was njured when the boring rod was lowered. The worker was taken to the hospital for the assistance. | The cause was touching the moving parts with hands. Inadequate communication and lack of specific instructions were contributors. | human error,industrial safety,injury,procedure deficiency |  | INDUSTRIAL SAFETY (IS.1);
WER TYO 15-0060 | 2015-01-13 | Fukushima Daiichi 2 | Injury of a worker during decontamination operations on the 1st floor of Unit2 nuclear reactor building at Fukushima-Daiichi Nuclear Power Plant | During decontamination operations in the reactor building a worker was injured when hand rails of an elevating workbench came down to his head when manipulating a lever of the workbench. | Work instructions were not clear and not understood by the workers. No operating guidance for the elevating workbench was given to the workers. | human error,industrial safety,injury |  | INDUSTRIAL SAFETY (IS.1);
WER TYO 15-0059 | 2014-11-28 | Kashiwazaki Kariwa 1 | Injury by getting right hand caught between the small access door of the double-entry door and the door frame | While performing a test on the double-entry door, a worker got his hand caught between the small door for inspection and its frame. This resulted in his thumb being fractured. | The cause was that there was no safety measures described in the test instruction manual and no specific instructions for prevention. | contractor,fracture,industrial safety,injury,procedure inadequacy |  | INDUSTRIAL SAFETY (IS.1);
WER ATL 15-0483 | 2015-01-15 | Comanche Peak 2 | Atmospheric Relief Valve Could Not Be Opened At the Manual / Automatic Station | During normal operation and while performing a surveillance test, an atmospheric relief valve on the main steam line could not be opened at the manual/automatic (M/A) station in the main control board. | The direct cause was a random failure of the controller driver printed circuit board. Card output did not change with simulated inputs. | circuit board,controller,main steam safety valve |  | EQUIPMENT PERFORMANCE (ER.1); EQUIPMENT FAILURE PREVENTION (ER.2);
WER ATL 15-0481 | 2014-12-21 | Point Beach 2 | Rod Position Indication Showing Unexpected Alarms | During normal operation, a rod position indication was noted jumping steps and then returned to normal twice. The associated control rod was declared out of service since correct rod bottom light indication could not be provided. | Further investigation into the equipment failure will be available during the next outage. | rod position indicator |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0410 | 2015-02-09 | Hatch 2 | Main Steam Isolation Valve Had Excessive Stroke Time To Close | During normal operation and while performing surveillance testing, two main steam isolation valves were found having excessive stroke time to close, resulting in entry into a limiting condition of operation. | The apparent cause was excessive lubrication of the 2-way and 4-way valves of the pneumatic manifold causing them to stick and delay the opening of air supply and exhaust paths of the air operator cylinder. | actuator,limiting condition of operation,lubrication,main steam isolation valve,surveillance |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0480 | 2014-11-26 | Three Mile Island 1 | Erroneous Vibration Indication on a Reactor Coolant Pump Leads to Reduction to 74% Power | During normal operation, steadily rising trend of vibration indication for the reactor coolant pump (RCP) was observed. After reduction to 74% power, the problem was determined to be a faulty vibration indication. The alternate vibration indication had failed 22 days prior to the event and was not available to validate the pump performance. | The direct cause was degradation of vibration indication. Actions were not implemented when the vibration indication was identified as degraded and the condition was not repaired in a timely manner. The alarm response procedure for RCP high vibration did not contain guidance on other pump parameters to validate actual high vibrations. | power reduction,procedure deficiency,reactor coolant pump,vibration |  | EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
WER ATL 15-0479 | 2015-01-21 | Prairie Island 2 | De-clutching Lever Bumped Resulting in an Unplanned LCO and Misposition | During normal operation, an auxiliary feedwater train became inoperable due to misposition of an associated motor valve. The unit entered a limiting condition of operation (LCO) of 72 hours. | A worker unknowingly bumped the declutch lever for the motor operated valve while performing a welding activity, which resulted in the valve being mispositioned. Workers did not effectively use the two minute drill and walkdown to identify the need to protect bump sensitive equipment. | clutch,human error,limiting condition of operation,mispositioned valve,motor operated valve |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER ATL 15-0477 | 2015-01-08 | Indian Point 3 | Refueling Water Storage Tank Level Indication Sensing Lines Frozen | During normal operation, the unit entered technical specification for unit shutdown due to two inoperable level indication channels for the refuelling water storage tank (RWST). When reactor power was reduced to 43% for shutdown, the level indication was restored and the unit was returned to normal operation. | The direct cause was a frozen sensing line for the transmitters due to a failed strip heater. The apparent cause was thermal cycling and ageing of the electrical connection at the strip heater wire lug, which most likely led to the degradation of the mechanical connection with the crimp. | ageing,freezing,heat tracing,level transmitter,power reduction,technical specification |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0475 | 2015-01-07 | Waterford 3 | 72 Hour Unplanned Limiting Condition of Operation entered due to “A” Steam Generator Main Feedwater Isolation Valve Actuator Air Leak | During normal operation and while performing a planned maintenance, a steam generator main feedwater isolation valve became inoperable. This resulted in entry into a 72 hour limiting condition of operation (LCO). | The direct cause was air leakage from the pressure gauge due to a manufacturer defect, which caused a low pressure condition in the main feedwater isolation valve's air reservoir. A crack formed in the solder plug, creating a small leak in the bourdon tube pressure boundary. | ageing,crack,feedwater valve,leak,limiting condition of operation,pressure instrumentation,solder |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0474 | 2015-02-08 | Palo Verde 1 | An Unexplained Loss of a Reactor Makeup Water Pump was due to the unique Breaker Control Circuit | During normal operation, electricians racked out the breaker for the B reactor makeup pump which caused the A pump to trip. Operators noticed that the A pump was not running but no audible alarm was received. An attempt was made to restart the pump with no success. | The cause for the loss of the pump was a lack of understanding by the electricians the unique features of the breaker control circuit for the reactor makeup pump. Electricians were not aware of the connection of the two pumps control curcuits. | breaker,control circuit,human error,pump |  | MAINTENANCE FUNDAMENTALS (MA.1); OPERATIONAL RISK (OF.2);
WER ATL 15-0473 | 2015-03-07 | Virgil C. Summer 1 | Emergency Diesel Generator Attached Fuel Oil Pump Damaged Due To Unclear Procedure Feedback | During post-maintenance testing, an emergency diesel generator (EDG) engine driven fuel oil pump did not&nbsp;develop adequate discharge pressure. The pump shaft bearing had significant wear. The problem increased EDG unavailability. | The cause was inadequate fuel oil flow through the engine driven pump due to higher discharge pressure from the&nbsp;DC fuel oil pump. The probable cause was that the maintenance procedure did not include a procedure feedback submitted during a previous diesel generator overhaul. The DC fuel oil pump had been recently replaced without verifying the correct discharge pressure. | diesel generator,fuel pump,limiting condition of operation,procedure deficiency |  | CONDUCT OF MAINTENANCE (MA.2); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER ATL 15-0472 | 2015-03-15 | Watts Bar 1 | Emergency Diesel Cooling Water Valve Failed to Stay Open During Start | During the fast start surveillance for the emergency diesel generator (EDG), the cooling water valve fully opened as designed and immediately began to close. The loss of cooling flow required an emergency stop of the EDG, unplanned unavailability of the safety function and entry into 14-day shutdown limiting condition of operation. | The cause was a defective stop pushbutton handswitch for the valve which stuck in closed position preventing the valve from remaining open. The apparent cause was design vulnerability. Handswitch has a bump guard made of plastic material susceptible to ageing. | ageing,design,diesel cooling water,diesel generator,limiting condition of operation,switch,valve | SOER 2002-2 Rec 1 | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0470 | 2015-03-26 | Brunswick 1 | Incidental Contact Made Between Overhead Turbine Building Cranes | During an outage and while working two cranes in close proximity, the Unit 2 turbine crane rail rubber bumpers came in contact with the Unit 1 turbine crane rail trucks rubber bumpers resulting in a minor collision. Both cranes were placed in a safe condition and all crane activities stopped. | Two cranes made contact due to an inadequate risk assessment of the proximity of the cranes and a failure to validate the assumption of the position of the other crane. A spotter was not established for turbine crew lifts. | crane,human error,lifting device | SOER 2008-1 Rec 2 | INDUSTRIAL SAFETY (IS.1); CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0469 | 2015-03-31 | Cook 2 | Loss of Indication during Diesel Generator Surveillance | During an outage and while performing a load rejection test, a diesel generator was removed from service due to loss of indication and was declared inoperable. | The direct cause was failure of the master load shedding relay. The apparent cause was oxidized contacts as a result of inadequate adjustments of closing contact gap potentially related to lack of the procedural requirements to document measured values of as-found/as-left gap settings. | contact,corrosion,diesel generator,indication,procedure inadequacy,relay |  | CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0467 | 2015-01-05 | Robinson 2 | Security Officer Knee Injury | A security officer was injured while performing an annually required physical agility qualification. He was transported to an offsite medical provider due to severe pain, and required surgery. | The apparent cause was that layout of the physical agility course was not evaluated for modifications to lessen likelihood of an injury. The contributing cause was that security training failed to give adequate guidance related to stretching/warm up. | industrial safety,injury |  | INDUSTRIAL SAFETY (IS.1);
WER ATL 15-0466 | 2015-02-14 | LaSalle 2 | Core Shroud Inspection Resulted in Scope Expansion | During a refuelling outage, ultrasonic inspections of the reactor core shroud identified flaws that exceeded a threshold established by the reactor vessel internals program. The identified flaws did not challenge structural integrity or affect leakage calculations. The inspection scope was expanded to inspect additional welds. The refuelling outage critical path was delayed by 88 hours. | The flaws were most likely due to intergranular stress corrosion cracking and/or irradiation-assisted stress corrosion cracking. | corrosion,intergranular stress corrosion cracking,reactor core,ultrasonic testing |  | MATERIALS RELIABILITY (ER.4);
WER MOW 15-0002 | 2015-01-07 | Kozloduy 6 | #PRELIMINARY# A Turbine Feedwater Pump tripped due to feed water pump condenser high pressure protection actuation | During normal operation, a turbine driven feedwater pump tripped due to high pressure of its condenser. Reactor power decreased to 50% as per design. In 50 minutes, the condenser pressure was recovered. | The direct cause was low circulating water flow to the turbine driven pump condenser. Vacuum degradation was attributed to air accumulation in the cooling water system. Required surveilance test was not scheduled. | circulating water,condenser vacuum,feedwater pump,power reduction,turbine |  | EQUIPMENT FAILURE PREVENTION (ER.2); CONDUCT OF MAINTENANCE (MA.2);
WER MOW 15-0096 | 2015-05-12 | Tianwan 2 | #PRELIMINARY# The Unit 2 unplanned power decreasing | During normal operation, intermittent water leak from&nbsp;a cooling water pipe of the air cooler of a main pump motor was observed. The unit power was reduced to 67%. | The cause investigation is in progress. | cooler,leak,motor,power reduction,recirculation pump |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0464 | 2015-02-07 | Grand Gulf 1 | Reactor Scram Due to Generator Lockout with Main Transformer Differential Relay Overcurrent Flag | During normal operation, the reactor was automatically scrammed due to main generator lockout, caused by the main transformer differential overcurrent relay being activated. | The cause of the transformer differential relay actuation was degraded wiring on the high voltage current transformer. Inadequate oversight performed by the vendor during manufacture of the transformer and inadequate oversight during implementation of major projects were contributors. | differential relay,automatic scram,transformer,vendor,wiring | SOER 2011-1, Rec 5 | LONG-TERM EQUIPMENT RELIABILITY (ER.3); PROJECT MANAGEMENT (PM.1);
WER ATL 15-0199 | 2014-12-26 | Browns Ferry 2 | Feedwater Heater Isolation Results in Unplanned Downpower | During normal operation, a reactor feedwater heater level control processor module failed, causing an influx of cold water into the reactor and a reactor power rise. Operators manually reduced reactor power to 86% to prevent a power excursion. | The cause was ageing of the control processor module. | ageing,feedwater control system,power reduction,power surge,reactivity management,reactor water level | SOER 2007-1 Rec 5 | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0463 | 2015-01-31 | Oconee 3 | Manual Reactor Trip Due to Oscillations in the Feedwater System | During normal operation, feedwater flow oscillations occurred. The reactor was manually scrammed, and the unit was shut down for approximately 3 days. | The root cause was a manufacturing defect in the electro-pneumatic converter (E/P) for a main feedwater control valve, which resulted in intermittent electrical fault within the E/P. | control valve,converter,feedwater,manual scram,oscillation |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0462 | 2014-12-04 | Oconee 1 | Unplanned Outage Delay Due to High Pressure Feedwater Heater Tube Failure | While preparing for startup from a refuelling outage, a tube leak of the high pressure feedwater heater was observed. The feedwater heater was bypassed leading to reduced production capability during operation, and a 3-day outage extension for repairs. | The apparent cause was inadequate preventive maintenace and life cycle management. Inadequate system monitoring resulted in operating with a heater tube leak for an extended period of time. Methods for early identification of a tube leak (heater level and heater drain valve position) were not documented on a frequent basis to be trended. | erosion/corrosion,feedwater heater,preventive maintenance,tube leak |  | EQUIPMENT FAILURE PREVENTION (ER.2); LONG-TERM EQUIPMENT RELIABILITY (ER.3); MATERIALS RELIABILITY (ER.4);
WER ATL 15-0461 | 2015-03-31 | Darlington 2 | Ground Fault on Main Output Transformer White Phase Gas Relay | During normal operation, an intermittent ground fault had been observed on a 125V DC negative rail for several months. A solid ground then occurred during a heavy rain. | The direct cause was failure of cabling and conductors of the gas relay on the main output transformer (MOT), which increased risk of a turbine trip. A contributing factor was that preventive maintenance inspections were not comprehensive. | ageing,dc bus,ground fault,relay,transformer |  | EQUIPMENT FAILURE PREVENTION (ER.2); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER MOW 15-0095 | 2015-01-19 | Temelin 2 | Drop in water level in containment spray system tank below the limit after calibration of the sensor | During normal operation, oscillations occurred from the level sensor for the potassium borate tank in the containment spray system. After calibration, the tank level was found as 229.9 cm, which was below the low level limit of 230 cm required by technical specification. | The direct cause was false response of the sensor and the presence of air bubbles in the impulse line. The root cause was inadequately performed maintenance. | calibration drift,containment spray,level transmitter,tank,technical specification |  | EQUIPMENT FAILURE PREVENTION (ER.2); MAINTENANCE FUNDAMENTALS (MA.1);
WER MOW 15-0094 | 2015-03-15 | Temelin 2 | Loss of neutron flux measurement in one train | During normal operation, the loss of neutron flux measurement occurred in one train of primary reactor protection system. Failure disappeared spontaneously after one minute. The remaining two trains were fully functional and the continuity of neutron flux measurement was maintained. | The loss of measurement was caused by the short-term failure of the power supply for ionisation chambers. | excore neutron monitor,neutron flux,power supply,reactor protection system |  | EQUIPMENT PERFORMANCE (ER.1);
WER MOW 15-0093 | 2014-12-29 | Dukovany 3 | Failure to perform a functional test resulting in the breach of the Limiting Condition of Operation (LCO) | During startup after repair of leakage, a functional test on the primary circuit was not performed as required in the lines of the loop isolating valve and the pressurizer. This resulted in violation of technical specifications. | Completion of the test was not monitored or checked. Human error prevention tools such as independent checking were not used. Procedures were incorrect and incomplete. | post-maintenance test,technical specification |  | CONDUCT OF OPERATIONS (OP.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER ATL 15-0458 | 2015-01-19 | Wolf Creek 1 | Missile Door Misalignment and Binding Results in a Reduction in Accident Mitigation | During normal operation, the missile door for entrance to engineered safety features (ESF) switchgear and emergency diesel generator (EDG) rooms stuck open and could not be closed. This resulted in entry into a limiting condition of operation. | The direct cause was wear of hinge pin which caused binding with the height adjusting screw. The height adjusting screw unthreaded due to door movement. | diesel generator,door,engineered safety feature,limiting condition of operation,pin,screw |  | EQUIPMENT FAILURE PREVENTION (ER.2);
WER ATL 15-0457 | 2015-02-25 | Hope Creek 1 | Drywell Leak Detection Secured due to Human Error | During normal operation, the drywell leak detection system was inadvertently secured, which resulted in an inadvertent shutdown of the sample pump of the system. The unit entered a technical specification action. | The direct cause was that an operator selected the incorrect pushbutton due to human error. The cause was less than effective use of human performance and error prevention tools prior to manipulating the component pushbuttons to obtain required readings. | containment,detector,human error,leak,misposition,technical specification |  | OPERATION CONFIGURATION CONTROL (CM.2); OPERATIONS FUNDAMENTALS (OP.1);
WER ATL 15-0456 | 2015-04-14 | Darlington 2 | #PRELIMINARY# Forced Outage due to Primary Heat Transport Leak Outside Containment | During normal operation, approximately 7000 litre of heavy water (D2O) spilled from a D2O transfer system valve that was being overhauled. The unit was manually shutdown. The event resulted in a 4-day forced outage. | The likely cause was leak from an isolation valve, which was found one turn open. The root cause analysis is being conducted. | configuration control,heavy water,isolation valve,leak,reactor shutdown |  | OPERATION CONFIGURATION CONTROL (CM.2);
WER MOW 15-0022 | 2015-02-10 | Novovoronezh 5 | #PRELIMINARY# The Unit 5’s Turbo Generator 13 was disconnected from the grid to address a hydrogen leakage. | During normal operation, the hydrogen analyser on a turbine generator stator showed hydrogen concentration increased to 11%. The reactor power was reduced to 50% to shutdown the turbine generator and repair the hydrogen leak. | The cause was a failed soldered connection due to increased vibration on the rod winding ends caused by the lack of sealing material. The root cause was deficient fabrication of the turbine generator stator. | hydrogen,leak,power reduction,solder,stator,turbine trip,vibration |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER MOW 15-0091 | 2015-05-10 | Kursk 2 | #PRELIMINARY# The reactor was shutdown from the automatic reactor setback key when testing the primary safety valves | During startup at 17% power and while performing functional tests for the pilot operated relief valves (PORV) of the primary safety valves, a pullback spring failed to initiate to close the PORV. The reactor was manually scrammed. | The cause is under investigation. | manual scram,power operated relief valve,reactor shutdown,safety relief valve,spring |  | EQUIPMENT PERFORMANCE (ER.1);
WER PAR 15-0259 | 2013-12-23 | Angra 1 1 | Manual Reactor SCRAM due to loss of external electrical power to 138kV | During normal operation, loss of 138 kV supply to bus bars and slow automatic transfer to 500 kV supply initiated the blackout loads sequencer. The turbine building refrigeration system pumps tripped and could not restart within the required time, which caused temperature rise in the turbine generator. The reactor was manually scrammed to address the problem. | The cause was that operators did not reset the blackout loads sequencer before trying to restart the turbine building refrigeration system pumps. The shift foreman did not access the proper procedure in due time. | load sequencer,loss of offsite power,manual scram,procedure adherence |  | OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);
WER MOW 15-0090 | 2015-01-04 | Kola 3 | Unit 3’s Load Reduction from Turbine Generator Loss-of-Excitation Protection Actuation to Trip Turbine Generator No.6 | While operating at 445 MWe, loss of generator excitation resulted in the field breaker and generator breaker of a turbine generator tripped. Power was reduced to 53%. | The direct cause was a fault in the rotor dc circuit caused by an insulation sleeve failure. The root causes was deficient fabrication of the insulation sleeve. The contributing cause was deficiency in vendor documentation. | documentation,exciter,insulation,power reduction,sleeve,turbine generator,turbine trip,vendor |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); CONDUCT OF MAINTENANCE (MA.2);
WER MOW 15-0089 | 2015-03-07 | Leningrad 4 | Leaks from Reactor Pressure Tube Detachable Joints Due to a Worn Reinforcing Belt on Gaskets | During normal operation, an increased specific volumetric radioactivity of airborne substances was observed in the non-attended premises of the reactor main circulation circuit. The reactor was manually scrammed for 90.3 hours to address the problem. | The direct cause was a worn reinforced belt on the gaskets installed on the detachable joints of stop and control valves associated with pressure tubes due to electrochemical copper corrosion. The root cause is not yet identified. | corrosion,joint,leak,reactor shutdown |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0455 | 2015-03-16 | Point Lepreau 1 | Impairment to Emergency Core Cooling Due to Pneumatic Valve Failing to Meet the Closed Limit Switch Within the Prescribed Stroke Time Tolerance | During normal operation and while performing a routine auto transfer logic test for medium pressure emergency core cooling to low pressure emergency core cooling, a pneumatic valve did not fully close. This resulted in the valve's stroke time being outside of tolerance, and entered a LCO. | The direct cause was that the hydraulic override control valve was in incorrect position, which limited stroke of the valve due to trapped hydraulic pressure against the pneumatic piston in the actuator. The incorrect position was caused by incidental contact or other undocumented manipulation. | configuration control,control valve,emergency core cooling system,human error,hydraulic actuator,pneumatic actuator |  | OPERATION CONFIGURATION CONTROL (CM.2);
WER ATL 15-0453 | 2015-02-11 | Sequoyah 1 | Contract Worker Fractures Ankle While Moving Concrete | While transporting concrete in a wheelbarrow, the load shifted and caused loss of balance when the worker went down a step. This resulted in a fractured ankle and lost time. | The direct cause was loss of control of the wheelbarrow and inadequate pre-job briefing. | contractor,industrial safety,injury |  | INDUSTRIAL SAFETY (IS.1);
WER ATL 15-0452 | 2015-02-19 | Peach Bottom 3 | Reactor Recirculation Pump Trip on Motor Generator Lockout Results in Forced Loss Event | During normal operation, a reactor recirculation pump motor generator set tripped. The reactor power was lowered to 49% to carry out repair. | The apparent cause was an intermittent failure of the voltage regulator resulting in a generator output voltage spike and subsequent exciter field overcurrent trip. | motor generator,power reduction,reactor recirculation pump,voltage regulator |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0451 | 2015-01-07 | Quad Cities 1 | Diesel Generator Fuel Oil Transfer Pump Trip | During maintenance and surveillance activities, both feed breakers for the fuel oil transfer pump to the common diesel generator were tripped. The station did not recognised that it should have entered a shutdown limiting condition for operation (LCO), and that the LCO time would have exceeded. | The direct cause was failure of a relay in the breaker control circuit. The apparent cause was the high resistance contacts on the relay lowered voltage enough to the main contactor coil that it could chatter and caused an instantaneous trip of the breakers. | ageing,circuit breaker,diesel generator,fuel pump,relay,technical specification,trip |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0448 | 2015-02-18 | River Bend 1 | Operations Prohibited by Technical Specifications Due to Deficient Local Leak Rate Test Procedures Containing Erroneous Valve Alignments | While developing a new leak rate surveillance test procedure (STP) for main steam isolation valves (MSIV), it was discovered that four STPs contained a similar error since 1992 resulting in improper test configuration. | The cause was incorrect valve configuration in the procedure and inattention to procedure revision development. | configuration control,main steam isolation valve,procedure deficiency,surveillance,technical specification,test procedure |  | OPERATION CONFIGURATION CONTROL (CM.2); ENGINEERING FUNDAMENTALS (EN.1);
WER ATL 15-0447 | 2015-01-31 | Callaway 1 | Unexpected Load Reject When Changing Turbine Controls | During normal operation and when preparing for main turbine control valve testing, the electrohydraulic control (EHC) system unexpectedly reduced turbine load. During stabilization actions, it reduced load again. This resulted in reactor power reduction to 46% for 5 days. | The most probable cause was poor seating of the load limit and load set runback card. The contributing cause was that operators did not understand the EHC malfunction and did not transfer to standby controls to lessen the severity of the event. | circuit card,connector,electro hydraulic control,power reduction,reactivity management | SOER 2013-1 Rec 3b | MAINTENANCE FUNDAMENTALS (MA.1); OPERATIONS FUNDAMENTALS (OP.1);
WER ATL 15-0446 | 2015-02-03 | Callaway 1 | Turbine Load Perturbation during Power Supply Replacement | During operation at 545 MWe and while transferring from permanent magnet generator (PMG) power supply to house power supply (HPS), the turbine generator power increased by 25 MW. The event resulted in a reactor power transient and a reactivity management event. | The cause was incorrect work instructions and inadequate review of these instructions. | human error,power supply,power surge,procedure deficiency,reactivity management,troubleshooting,turbine generator |  | CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0445 | 2015-01-19 | Clinton 1 | Entered Reactor Coolant Leakage Off Normal Procedure for Leakage in Drywell (Part of containment structure) | During normal operation, the unit entered the reactor coolant leakage off normal procedure due to a drywell unidentified leakage increase. Leakage stabilized when reactor power was reduced to 83%. The reactor entered a planned outage the day after. | The direct cause was leak from packing of the reactor core isolation cooling (RCIC) system steam line inboard isolation valve. The root cause was that maintenance did not place priority on change to the valve packing program and did not drive to implement an industry best process in a timely manner. | emergency core cooling system,isolation valve,leak,preventive maintenance,reactor shutdown,valve packing |  | EQUIPMENT FAILURE PREVENTION (ER.2); CONDUCT OF MAINTENANCE (MA.2); SOLUTIONS IMPLEMENTATION (PI.3);
WER ATL 15-0443 | 2015-01-15 | River Bend 1 | Down-Power to Investigate Moisture Found in the Isophase Bus Duct Cooling System | During normal operation, moisture was leaking out of the isophase bus duct of normal station service transformers. This resulted in a decision to perform reactor power reduction to 10% to remove the generator from service so that further investigation could be performed. | The direct cause was rain intrusion. The root cause was lack of design information to prevent water accumulation. Inadequate preventive maintenance was a contributor. | drawing,isophase,power reduction,preventive maintenance,water intrusion |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); EQUIPMENT FAILURE PREVENTION (ER.2);
WER TYO 15-0058 | 2014-12-16 | Qinshan 1 | Reactor shutdown manually due to reactor coolant leak | During normal operation, leakage rate of reactor coolant system rose abnormally. The reactor was shutdown for seven days to rectify the problem. | The direct cause was stress corrosion cracking in a weld joint for connecting a flow transmitter to reactor coolant system. The root cause was inadequate design allowing vibration. The contributing cause was inadequate inspections. | design,intergranular stress corrosion cracking,leak,preventive maintenance,reactor coolant,reactor shutdown,vibration,weld |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); EQUIPMENT FAILURE PREVENTION (ER.2); MATERIALS RELIABILITY (ER.4);
WER TYO 15-0057 | 2014-11-06 | Qinshan 3 1 | Fracture of a spent fuel element caused by mis-operation | During normal operation and while installing a basket cover to a spent fuel dry storage drum in the spent fuel storage pool, a spent fuel element was fractured. The spent fuel dry storage was suspended for 10 days. | Before installation of the cover, operators noticed that the element slightly inclined outwards but failed to report it to the supervisor. The root cause was inadequate risk identification and lack of questioning attitude. Inadequate operating experience was a contributor. | fuel handling,spent fuel storage | SER 2004-2 | FUELLING ACTIVITIES (FA.1); NUCLEAR PROFESSIONALS (NP.1); PERFORMANCE MONITORING (PI.1);
WER MOW 15-0088 | 2015-03-09 | Bohunice 4 | Spurious activation of emergency flash protection on switchboard 2BB | During normal operation, spurious activation of emergency flash protection in a 6 kV switchboard resulted in tripping of unit transformer breaker and loss of power supply to 6 kV section. This caused start of a diesel generator and activation of the reactor limitation system, resulting in reactor power reduction to 75%. | The cause was ageing of the emergency flash protection relay. The root cause was non implementation of corrective actions on repeated failure of the emergency flash protection. | ageing,diesel generator,flashing,power reduction,switchboard |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); SOLUTIONS IMPLEMENTATION (PI.3);
WER MOW 15-0087 | 2015-01-30 | Bohunice 3 | Closing of the fast acting valve at the nominal unit output caused by depressuring of the fast acting valve | During normal operation, a fast acting valve closed and the bypass valve to atmosphere from a steam generator opened. Pressure in the main steam header and output of the turbine generator decreased. This resulted in reactor power reduction to 72%. | The direct cause was insufficient opening of a hand valve to the air receiver, which caused less than adequate air supply to the fast acting valve due to leakage in the system. The root cause was lack to use procedures. | instrument air,main steam,mispositioned valve,power reduction,procedure adherence,reservoir,valve |  | OPERATION CONFIGURATION CONTROL (CM.2); OPERATIONS FUNDAMENTALS (OP.1);
WER MOW 15-0016 | 2015-01-17 | Bohunice 3 | The Control rod HRK 12-25 dropped to the low limit position following reactor power of unit 3 reduction. | During normal operation, a safety and control rod assembly dropped to the low limit position. The reactor power was reduced below 44% to solve the problem. | The direct cause was loss of power supply to the low frequency converter for the control rod. The root cause investigation is planned to be performed during the next outage. | control rod drop,power reduction,power supply |  | EQUIPMENT PERFORMANCE (ER.1);
WER MOW 15-0084 | 2014-07-11 | Temelin 2 | Failure of the sealing of main safety valve of the pressurizer during unit shutdown | During an outage and while replacing steam cushion of the pressurizer with nitrogen cushion, leakage from a main safety valve of the pressurizer resulted in pressure increase in the bubbler tank. The shutdown was extended for approximately two days to rectify the problem. | The cause could not be clearly identified. | leak,pressuriser safety valve,valve seal |  | OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);
WER ATL 15-0441 | 2014-10-25 | Oconee 3 | Main Turbine High Vibrations During Down Power | During planned power reduction for reactor cooling pump maintenance, main turbine vibrations steadily increased to unacceptable levels. Reactor power was reduced to 20%, and the turbine was taken offline and placed on turning gear for 8 hours. | The direct cause was that a rub occurred in a turbine bearing due to thermal transients combined with close steam seal clearances. Vendor specifications for slant tooth packing clearance were not used. In addition, maintenance strategy did not ensure full train alignment. | bearing,preventive maintenance,rapid power reduction,turbine,vibration |  | EQUIPMENT FAILURE PREVENTION (ER.2); CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0440 | 2014-11-02 | Diablo Canyon 2 | Pressurizer Safety Valve Seat Leakage Results in Impact to Refueling Outage Critical Path | During startup and while pressurising reactor coolant system, leakage was found from two pressuriser safety valves. The outage was extended for 46 hours to rectify the problem. | The apparent cause was that the safety valve bodies were not adequately rigid to accommodate the nozzle loads imparted by the inlet and discharge piping flanges. The contributing cause was accumulation of hydrogen at the inlet of the safety valves which prevents the flexible disc of the valves from reaching thermal equilibrium with the pressurizer steam space environment. | design,leak,pressuriser safety valve |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1);
WER ATL 15-0439 | 2015-02-10 | Davis Besse 1 | Ankle Injury Due to Icy Conditions | A contractor was walking outdoors when he slipped and fell. This resulted in a fracture to the right ankle, requiring treatment beyond first aid. | The root cause was a missed opportunity to mitigate the icy conditions. | contractor,ice,industrial safety,injury |  | INDUSTRIAL SAFETY (IS.1);
WER PAR 15-0258 | 2014-11-04 | Asco 1 | Inoperability of the particle and gas radiation monitors in the containment building | During normal operation and while switching power supply of the panels supplying power to particle and gas radiation monitors in the containment building, the radiation monitors were momentarily left without power supply. After power was restored, monitors were automatically aligned to suction line of the containment purge system exhaust unit for 10 minutes, which was not in service. This caused two of the reactor coolant leak detection systems inoperable and entry into a limiting condition of operation. | The direct cause was a loss of power supply following power supply switchover due to a fault in a transformer. The root cause was damage of the winding insulation in the transformer due to ageing. The other root cause was delay in normalising alignment due to inadequate operator training and deficiency in radiation surveillance system document and relevant procedure. | ageing,documentation,insulation electrical,limiting condition of operation,procedure deficiency,radiation monitor,short circuit,training,transformer |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);
WER PAR 15-0257 | 2015-03-22 | Torness 2 | Fuelling Machine Low Power Refuelling exchanges being aborted due to lack of Nitrogen (N2) Plant Operability | During online refuelling, the minimum N2 stocks were found below the requirements of technical specification, and a 72 hour window was entered. The backup N2 supply to the fuelling machine was isolated to stem the loss of N2, which resulted in delay to the refuelling programme and subsequent generation loss. | The direct cause was a N2 relief valve lifting and not reseating. The root cause was that operation of a N2 control valve was not rapid enough to limit pressure transients in the N2 system. Inadequate operating procedures and lack of spare parts contributed to the event. | limiting condition of operation,nitrogen,procedure inadequacy,refuelling,relief valve |  | EQUIPMENT PERFORMANCE (ER.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3); CONDUCT OF OPERATIONS (OP.2);
WER MOW 15-0082 | 2015-02-16 | Rostov 2 | The Unit entered a forced outage due to a failure of the Control Rod Drive Mechanism (CRDM) cask resulted from a through crack found in the cask base metal. | During normal operation and while inspecting a control rod drive mechanism cask for boron traces, a crack was found in the base metal of the cask. The unit was shutdown to rectify the problem. | The direct cause was a crack in the base metal of the cask. The root cause was deficient design as an alloy susceptible to inter-crystalline stress corrosion cracking was used in the cask material. | control rod drive,crack,design,intergranular stress corrosion cracking,reactor shutdown |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); MATERIALS RELIABILITY (ER.4);
WER MOW 15-0081 | 2014-11-29 | Rostov 1 | The Unit tripped off line as a result of the main transformer gas protection actuation caused by a low oil level in the surge tank | During normal operation, the main transformer gas protection actuated, and resulted in the unit being taken offline. The fast power reduction system led reactor power to 37%. | The direct cause was that a leaky oil cooler tube due to fluid-induced pitting corrosion caused low level in the surge tank but the low level alarm did not actuate. Deformation of the protective film in the surge tank had the oil indicator float stuck. The root cause was deficient manufacturing and design. | corrosion,level switch,oil cooler,power reduction,transformer,tube leak |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); MATERIALS RELIABILITY (ER.4); CONDUCT OF MAINTENANCE (MA.2);
WER MOW 15-0080 | 2014-10-29 | Tianwan 1 | Abnormal thinning of recirculation pipeline at emergency feedwater system(1LAR14/24/34/44) | During normal operation and while conducting performance test on an emergency feedwater pump, water was found leaking from the elbow of recirculation pipeline at the discharge side of pump. The event resulted in one of four emergency feedwater system channels becoming unavailable. The ultrasonic testing revealed thinning in elbows of all four channels. | The direct cause was cavitation in the pipe elbow. The root cause was improper orifice structure in two channels and inadequate length of straight pipe section after the orifice in other two channels due to inadequate review of orifice design change. | cavitation,design change,feedwater,leak,orifice,recirculation,ultrasonic testing | SER 2005-3 | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); DESIGN CHANGE PROCESSES (CM.3);
WER MOW 15-0078 | 2014-12-22 | Dukovany 3 | Unit shutdown for the purposes of repairing a leak in a heterogeneous weld | During normal operation, leakage was found in a heterogeneous weld between the feedwater supply line and the steam generator feedwater pressure measurement line. The unit was shutdown for five days to carry out repair. | The direct cause was crack on an instrument line in the area of weld. The root cause was material fatigue and possible mechanical stress of the instrument line from a near fixed ladder. | fatigue,feedwater,instrument line,leak,reactor shutdown,weld |  | OPERATION CONFIGURATION CONTROL (CM.2); MATERIALS RELIABILITY (ER.4);
WER PAR 15-0256 | 2014-11-25 | Hinkley Point B2 | Vaporiser Auxiliary Boiler low back up air cylinder pressure alarm | During normal operation, a vaporiser auxiliary boiler (VAB) became unavailable due to drop in its back up instrument air system pressure, resulting in entry into a limiting condition of operation. | The cause was air leakage from a number of pipe fittings on the back up instrument air system. The fittings were disturbed during recent maintenance but no post maintenance testing was carried out to ensure leak tightness. | auxiliary boiler,fitting,instrument air,leak,limiting condition of operation,post-maintenance test |  | MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
WER MOW 15-0077 | 2015-05-04 | Khmelnitsky 1 | #PRELIMINARY# Reactor Coolant Pump (RCP) trip caused by actuation of ground-fault protection | During normal operation, a reactor coolant pump tripped on actuation of ground fault protection. The reactor power limiting system reduced reactor power. After addressing the problem, reactor power was reduced to 30% to restart the pump. | The cause was failure of a relay in the protection circuit. | power reduction,protection system,reactor coolant pump,relay,trip |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0436 | 2015-02-22 | Point Lepreau 1 | Capacitor Failure During Inverter Start-up | During normal operation and while performing post maintenance testing of a 600V inverter, its capacitors failed. This resulted in reduction in reliability of uninterruptable power supply for essential loads. A standby diesel generator was required to remain in service for an extended period. | The apparent cause was use of capacitors beyond their expected lifetime and inadequate preventive maintenance. | ageing,capacitor,inverter,preventive maintenance,uninterruptible power supply |  | EQUIPMENT FAILURE PREVENTION (ER.2); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0435 | 2015-02-16 | Pickering B6 | Main Output Transformer Cooling Control Failure Resulted in Unit Derating | During normal operation, the main output transformer (MOT) oil temperature increased. The unit was derated to 70% power to meet this condition. | The direct cause was loss of low pressure service water (LPSW) cooling flow to the MOT heat exchangers due to motorized valves being closed. The most likely cause was failure of all four mircoswitches in both temperature switches, or two separate electrical short circuits being developed on the control wiring. | cooling water,motor operated valve,oil cooler,power reduction,transformer |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0432 | 2014-10-05 | Browns Ferry 1 | As-Found Local Leak Rate Test was Outside Tech Spec Limits | During an outage and while performing primary containment local leak rate test, a main steam line outboard isolation valve failed to meet the technical specification allowable leakage rate. | The apparent cause was nonuniform scale buildup between the valve seat and plug due to mineral deposits left by steam. | containment integrity,degradation,leak rate,main steam isolation valve,surveillance,technical specification |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0431 | 2013-10-09 | Grand Gulf 1 | Main Turbine Would Not Accelerate After A Forced Outage Resulting in A Plant Shutdown | During startup and when attempting to raise the main turbine speed, the turbine would not accelerate. Unit startup was delayed approximately 2 days to address the problem. | The direct cause was failure of two electro hydraulic (E/H) control converters. The rotating pilot valves in both E/H converters were mechanically bound due to excessive wear caused by particulate contamination of the hydraulic fluid, which prevented building fluid pressure. | electro hydraulic control,FME,hydraulic fluid,turbine control valve |  | EQUIPMENT FAILURE PREVENTION (ER.2);
WER ATL 15-0430 | 2015-03-05 | Prairie Island 1 | 120 VAC Panel Fuse Opened | During normal operation, a transformer failure caused a 120V panel to de-energise resulting in loss of heater drain tank, feedwater heater and moisture separator re-heater level control. Loss of the heater drain tank level caused the heater drain tank pumps to lock-out, requiring a plant down power to 90%. | The failure of transformer caused a fuse to open and 120V panel de-energised. The transformer failed four months after installation and is attributed to infant mortality. | fuse,heater drain,power reduction,pump,transformer |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0429 | 2015-01-24 | Palo Verde 2 | Setpoint Drift on the Plant Protection System Steam Generator Differential Pressure was Outside of Technical Specification Limits for Thirteen Days | During normal operation, an alarm on the plant computer (PC) indicated a deviation between differential pressure setpoints of two steam generators on the plant protection system (PPS), but operators did not recognise that for 13 days. Therefore, a PPS channel setpoint was outside of technical specification limits longer than the allowed outage time. | The cause of the setpoint deviation was setpoint drift. The cause of the response delay was that operators did not understand the meaning of what the alarm condition was telling them. The alarm did not have annunciation with an associated response to ensure that the alarm was addressed correctly within technical specification time limitations. | alarm,computer,differential pressure,setpoint drift,steam generator,technical specification | SOER 2013-1 Rec 3 | OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);
WER ATL 15-0428 | 2014-11-30 | Turkey Point 4 | High Pressure Turbine Cylinder Heat Pipe Failure Led to a Manual Turbine Trip and resulted in an Unplanned Auxiliary Feedwater Actuation. | During normal operation, steam was found leaking from one end of the high pressure turbine. Consequently, the turbine was tripped manually and reactor shutdown was started. The reactor was scrammed at 23% power and an unplanned auxiliary feedwater (AFW) actuation occurred. | The direct cause was failure of a turbine cylinder heating steam pipe. The root cause was an oversized weld which created a significant stress riser at the toe to weld on pipe and coupled with vibrations from turbine resulted in failure of the pipe. The cause of AFW actuation was scram of reactor above the power level suggested in the procedure and inadequate training of operators. | auxiliary feedwater,design,fatigue,industrial safety,leak,manual scram,procedure adherence,steam,turbine trip,vibration,weld |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);
WER ATL 15-0427 | 2015-03-16 | Koeberg 1 | Nuclear Component Cooling System Maximum allowable frequency as per procedure exceeded resulting in a Statutory Non-Compliance | A common component cooling water safety valve with a 9 year test frequency, had not been tested since 1999. The valve was tested satisfactorily in March 2015, but the 16 year period resulted in a statuary non-compliance. | The possible cause of the incorrect management was errors made when processing a frequency change request and scheduling the test. | component cooling water,preventive maintenance,safety relief valve |  | EQUIPMENT FAILURE PREVENTION (ER.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
WER ATL 15-0426 | 2013-12-05 | Pickering B5 | Unavailability of Vacuum Priming Pumps and Shutdown of a Condenser Cooling Water Pump Increased Condenser Pressure Resulting in Unit Power Reduction | During normal operation and while a condenser cooling water (CCW) pump was shut down under a work protection isolation permit, tripping of the available vacuum priming pump resulted in increase of condenser pressure. The reactor power was manually reduced to 89%. | The cause was tripping of the only available vacuum priming pump on electrical protection with one CCW pump shutdown. The apparent cause was equipment deficiency and unavailability of two other vacuum priming pumps. | circulating water,condenser vacuum,power reduction,pump |  | EQUIPMENT PERFORMANCE (ER.1);
WER ATL 15-0425 | 2015-04-04 | Pickering A4 | Unavailability of Fuelling Machine Resulted in Unit Derating Greater Than Ten Percent | During normal operation and while pushing new fuel from the fuelling machine (FM) magazine into the fuel transfer mechanism, a FM mechanism stalled. The unit was derated to 89% power to address the problem. | The cause was failure of the FM magazine position error indicating alarm meter due to ageing. | ageing,power reduction,refuelling,setpoint drift |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); FUELLING ACTIVITIES (FA.1);
WER ATL 15-0424 | 2013-07-25 | Pickering A1 | Failure of Low Pressure Turbine Steam Intercept Valve Resulted in the Unit Derating | During operation at 97% power, a low pressure turbine steam intercept valve failed closed resulting in opening of the associated steam release valve, which was subsequently manually closed. Another steam release valve was already found faulty during a test. The unavailability of two steam release valves required the unit derating to 87% power. | The apparent cause was leakage from an instrument air line of the intercept valve due to detachment of a swagelok fitting as a result of ageing and vibrations. | ageing,air operated valve,fitting,leak,low pressure turbine,power reduction,vibration |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0422 | 2015-03-13 | Bruce B 6 | Liquid Zone Control Pump Trip – Wrong Unit Event | During normal operation, a worker assigned to confirm removal of de-energising devices on a liquid zone control (LZC) pump of unit 8, went to unit 6 instead of unit 8 and opened motor starter disconnect and attempted to open the motor control centre cell door. This caused tripping of a LZC pump, resulting in reactor power reduction of 2%. There was potential for exposure to live equipment and arc flash on re-closure of the circuit breaker. | The cause was human error due to improper situational awareness and self check. | human error,industrial safety,motor control centre,power reduction,self checking |  | INDUSTRIAL SAFETY (IS.1); MAINTENANCE FUNDAMENTALS (MA.1);
WER ATL 15-0420 | 2015-03-18 | Laguna Verde 1 | Emergency Diesel Generator inoperability due to the presence of diesel fuel in lubricating oil | During operation at 87.5% power, an emergency diesel generator (EDG) was declared unavailable due to mixing of diesel fuel in its lubricating oil. | The direct cause was diesel fuel leak through the engine fuel injectors. The root cause was inadequate supervision of contractor during maintenance. This led to not identifying the installation of counterfeit parts and original components not installed adequately. The other root cause was deficiency in maintenance procedure. Contributing causes include lack of supervisors training. | contractor,diesel fuel,diesel generator,fuel injector,leak,lube oil,procedure deficiency,spare part,training | SOER 2002-2 Rec 6 | LONG-TERM EQUIPMENT RELIABILITY (ER.3); CONDUCT OF MAINTENANCE (MA.2);
WER ATL 15-0415 | 2015-03-11 | Bruce A 3 | Unit Power Reduction Caused By Momentary Loss of Low Voltage Instrument Power Supply | During normal operation, momentary interruption of a 45V DC instrument power supply caused transients on several reactor control and regulating systems. This resulted in a 1.4% reactor power drop. The crew responded by taking manual control to stabilize the unit as per procedures. | The apparent cause was a loose connection between a fuse and a fuse holder in the instrument power supply. The fuse holder had degraded over time and lost its ability to maintain good electrical contact. The existing preventive maintenance strategy did not leverage thermography as a predictive monitoring method. | ageing,fuse,power reduction,power supply,preventive maintenance,transient |  | EQUIPMENT FAILURE PREVENTION (ER.2); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
WER ATL 15-0412 | 2015-03-12 | Chalk River NRU 1 | Control Rod Tachometer Gear Fasteners Found Sheared | During shutdown, control rod tachometer gear fasteners were discovered sheared. The outage was extended for three days to carry out replacement. | The apparent cause was inadequate design change of replacing gear fasteners with cotter pins. The contributing factors include inadequate testing, human errors and lack of communication of operating experience. | control rod,cotter pin,design change,human performance,operating experience,temporary modification | SER 2005-3 | DESIGN CHANGE PROCESSES (CM.3);
WER MOW 15-0058 | 2015-04-13 | Rovno 4 | #PRELIMINARY# Unit 4 was automatically unloaded and disconnected from the grid | During normal operation, a unit automatically unloaded and disconnected from the grid with the generator supplying house loads. | The direct cause was disconnection of the 750 kV overhead line. | grid,loss of offsite power,rapid power reduction |  | EQUIPMENT PERFORMANCE (ER.1);
WER MOW 15-0044 | 2015-03-30 | Kursk 2 | #PRELIMINARY# An Off-Site Fault on the High Voltage Overhead Line Caused Emergency Diesel Generators to Start with the Unit in a Planned Outage | During an outage, a fault on the 110 kV overhead power line resulted in loss of off-site power and actuation of the emergency diesel generators. | The direct cause was a phase-to-phase short on the off-site overhead line. The root cause was deficient design of non-vital power supply system. | design,diesel generator,fault,loss of offsite power,short circuit |  | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1); EQUIPMENT PERFORMANCE (ER.1);
WER MOW 15-0075 | 2015-04-29 | Kalinin 4 | #PRELIMINARY# Turbogenerator TG-4 was disconnected from the grid by the unit transformer phase “C” gas protection actuation | During normal operation, a unit transformer gas protection actuation lead one of turbine generators to be disconnected from the grid. Reactor power was automatically reduced to 40% and then manually reduced to 4%. | The cause is under investigation. | power reduction,transformer,turbine protection |  | EQUIPMENT PERFORMANCE (ER.1);

## Other Events
Reference Posted in 2015 | Event Date (DD/MM/YY) | Reference Unit | Title
WER PAR 15-0280 | 2014-10-29 | Fangchenggang 1 | One security guard from engineering project department crossing radiation prtotection isolation area
WER PAR 15-0279 | 2014-10-17 | Forsmark 1 | Unplanned loss of 70 kV incoming supply grid in conjunction with test of gas-turbine.
WER PAR 15-0276 | 2014-08-20 | Forsmark 1 | Failure to start a fan in the emergency ventilation system for active off-gases during test.
WER MOW 15-0101 | 2015-05-10 | Zaporozhye 4 | A High Voltage Breaker Removed from Service to Repair an Air Leak through a Longitudinal Crack on a Phase C Insulator
WER MOW 15-0100 | 2015-01-14 | Tianwan 2 | Transportation of radioactive substances led to an alarm in radiation monitoring channel.
WER MOW 15-0099 | 2015-01-12 | Tianwan 1 | Wrong type of electric heater contactor result in relay contact adhesion.
WER TYO 15-0064 | 2015-04-08 | Hanul 2 | The Leakage of Air at the Actuator of Main Feedwater Control Valve
WER PAR 15-0272 | 2015-03-19 | Fessenheim 2 | Deficient orange area marking off
WER ATL 15-0494 | 2015-03-25 | Pickering A1 | Electrical Hazard Identified After Work Protection Permit Applied and Working Rights Established Resulted in Potential Electrical Hazard Exposure to Workers
WER ATL 15-0493 | 2015-03-30 | Bruce B 5 | Individual hurt back lifting steel pipe
WER PAR 15-0270 | 2015-05-15 | Fangchenggang 1 | Disqualified SED Water
WER PAR 15-0269 | 2015-02-13 | Heysham A2 | Safety Rule Event during Emergency Boiler Feed Pump (EBFP) 4 maintenance
WER PAR 15-0268 | 2014-12-25 | Hunterston B 1 | Turbo Generator 7(TG7) Feed Heater Trip
WER PAR 15-0265 | 2015-03-04 | Hartlepool 2 | Control Rod Static Reversing Contactor (SRC) reliability
WER PAR 15-0261 | 2014-11-07 | Hunterston B 2 | Main Boiler Feed Pump (MBFP) 8 High Vibration Post Outage
WER ATL 15-0490 | 2015-02-06 | Vogtle 1 | Employee Finger Injury
WER ATL 15-0488 | 2015-01-25 | St. Lucie 1 | Injury Sustained While Exiting a Golf Cart
WER ATL 15-0487 | 2015-01-20 | Palisades 1 | Fire Inside Heating Unit Located Inside an Occupied Security Blast Resistant Enclosure
WER ATL 15-0485 | 2015-05-06 | Monticello 1 | Welding Blanket Smoldering During Hot Work Activities
WER TYO 15-0063 | 2015-01-19 | Fukushima Daiichi 5 | On leakage of the washing water in the container of the desalination equipment installed at the north side of Unit5 and Unit6
WER TYO 15-0061 | 2014-11-10 | Kashiwazaki Kariwa 1 | Leakage of fuel oil from the 2 ton truck fuel tank
WER ATL 15-0482 | 2014-11-06 | Point Beach 1 | Minor Leak on Emergency Diesel Generator Expansion Joint
WER ATL 15-0478 | 2015-01-05 | Indian Point 2 | Boric Acid to Blender Control Valve Fails to Fully Open on Demand
WER ATL 15-0476 | 2015-03-05 | Millstone 3 | Breathing Air Bank Found At Empty
WER ATL 15-0471 | 2015-03-25 | Brunswick 2 | Unable to Reset Half-Scram Signal During Testing Due to Disconnected Wire Clips
WER ATL 15-0460 | 2015-04-08 | Koeberg 2 | Unit 2 Radiation Monitoring System Tritium and C-14 bubblers were incorrectly taken out of service on Unit 2 instead of Unit 1
WER ATL 15-0459 | 2015-01-17 | Hope Creek 1 | Domestic Water Deepwell Pump Control Switch Mispositioned
WER MOW 15-0092 | 2015-02-11 | Beloyarsk 3 | Service water pump was removed from service due to a bearing failure
WER ATL 15-0454 | 2014-03-23 | Pickering A4 | Reactor Trip on Spurious Opening of a Channel While Another Channel was Open Due to Equipment Failure and Maintenance
WER ATL 15-0450 | 2014-02-07 | Davis Besse 1 | Permanently Stored Containment Building Palfinger Crane Hydraulic Boom Seal Failure Due To Incompatibility With Hydraulic Fluid
WER ATL 15-0449 | 2015-02-27 | Watts Bar 2 | Residual Heat Removal Pump ran for 4 minutes without discharge flowpath
WER ATL 15-0444 | 2015-02-14 | Pilgrim 1 | Manual Shutdown Due to Storm Neptune Blizzard Warning
WER MOW 15-0086 | 2015-02-27 | Temelin 1 | Failure to comply with radiation protection measures in work on the system containing active medium
WER MOW 15-0085 | 2014-07-30 | Temelin 1 | Shutdown of primary circuit low pressure safety injection pump due to high bearing temperature
WER MOW 15-0083 | 2014-06-25 | Temelin 2 | Release of essential service water pump coupling pins
WER ATL 15-0438 | 2014-06-27 | Wolf Creek 1 | Turbine Electrical Load Reduced And One Switchyard Transmission Line Source Disconnected To Repair Transformer
WER ATL 15-0437 | 2014-12-29 | Catawba 1 | Low Level Contamination Identified in Soil Outside Radiological Control Area Within Protected Area
WER PAR 15-0255 | 2015-01-08 | Hinkley Point B2 | Failure of Charge Machine Travelling Pick-up During Refuelling
WER PAR 15-0254 | 2015-04-14 | La Hague 2 | #PRELIMINARY# Disengagement of a vitrified waste container out of the required operating conditions.
WER MOW 15-0076 | 2014-08-31 | Kursk 4 | A Tilter Cask Stuck During Spent Nuclear Fuel Disassembly Operations in the Protective Chamber of the Spent Nuclear Fuel Storage / Handling Division
WER ATL 15-0434 | 2015-03-17 | Darlington 1 | Manufacturing Correlation of Recent Darlington Fuel Defect Experience
WER ATL 15-0433 | 2015-03-23 | Barakah 1 | Barakah Polar Crane Main Hoists are not Single Failure Proof
WER PAR 15-0253 | 2014-04-19 | Ningde 1 | Standard-Exceeding of Condensed Water Quality for Unit 1 Condensate Extraction System
WER ATL 15-0423 | 2015-03-13 | Darlington 4 | Condenser Cooling Water Screen Wash Pump Pit Flooding due to Non-Return Valve Leak
WER ATL 15-0421 | 2015-03-31 | Laguna Verde 1 | Personnel entered restricted area without electronic dosimeter
WER ATL 15-0419 | 2015-03-18 | Laguna Verde 2 | Inadequate special instructions generated for Reactor Water Clean Up demineralizer filter pre-coating
WER ATL 15-0418 | 2015-03-27 | Bruce A 3 | Opportunities Realized Through Problem Solving of Condenser Tube Leak Search Methods
WER ATL 15-0417 | 2015-03-16 | Bruce A 1 | Opportunities Realized Through Problem Solving of Adverse Trend in Acute Hand Injuries
WER ATL 15-0416 | 2015-03-11 | Bruce A 1 | Lessons Learned from Missed Active Liquid Waste Tank Sampling Event
WER ATL 15-0414 | 2015-02-25 | Bruce A 2 | Lessons Learned from Forklift Near-Miss Incident
WER ATL 15-0413 | 2015-04-22 | Chalk River NRU 1 | Non compliance to the NRU Reactor Facility Authorization
WER PAR 15-0252 | 2015-03-10 | Torness 1 | Integrity of an ‘Excepted Package’ was compromised during transport
WER PAR 15-0251 | 2015-02-16 | Dungeness B 1 | Reheat Outlet (RO) Valve Spuriously Closed