| AGREED BY : General Director NovEnergoProm JSC _______________ V.V.Sytov «____» _______________ 2017 г. | APPROVED BY: JSC _______________ / / «______»___________ 2017 г. |
| --- | --- |

Multiple Stud Tensioner

FOR REACTOR PRIMARY JOINT

TERMS OF REFERENCE

AGREED BY:

| __________________________________ ______________________ / / Ref.№ «____» _______________ 2017 г. | ______________________ / / «____» _______________ 2017 г. |
| --- | --- |
| ______________________ / / «____» _______________ 2017 г. Ref.№ | __________________________________ ______________________ / / «____» _______________ 2017 г. |
| Deputy Head of Department OKB „Hydropress“ JSC __________________________________ ______________________ / / «____» _______________ 2017 г. | Chief Designer NovEnergoProm JSC _______________ «____» _______________ 2017 г. |

Исх.№

2017

Table of Contents

| 1 | Description and Scope of Application |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 3 |
| --- | --- | --- | --- | --- | --- |
| 2 | Basis for Development |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 3 |
| 3 | Development Purpose and Designation |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 4 |
| 4 | Source of Development |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 5 |
| 5 | Technical Requirements |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 6 |
| 6 | Development stages and phases |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 20 |
| 7 | Control and acceptance procedure |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 21 |
| 8 | Quality assurance |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 23 |
| 9 | Supplier‘s warranties |  | . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 23 |
| Appendix А |  | Reactor primary joint sealing unit |  | . . . . . .. . . . . . . . . . . . .24 |  |
| Appendix B |  | Multiple Stud Tensioner. Dimensional drawing |  | . . . . . . . . . . . . . . . . . .25 |  |
| Appendix C |  | TTE warehouse |  | . . . . .. . . . . . . . . . . . . .28 |  |
| Appendix D |  | Test stand. Dimensional drawing |  | . . . . .. . . . . . . . . . . . . .29 |  |
| Appendix D1 |  | Layout of the test stand supports in the inserts at TTE warehouse |  | . . . . .. . . . . . . . . . . . . .30 |  |
| Appendix E |  | Transportation and storage stand. Dimensional drawing |  | . . .. . . . . . . . . . . . . . . .31 |  |
| Appendix E1 |  | Layout of the transportation and storage stand in the reactor building and at TTE warehouse |  | . . . . . . . . . . . . . . . . . .32 |  |
| Appendix F |  | Reactor cavity with guide rails |  | . . . . . . . . . . . . . . . . . .34 |  |
| Appendix G |  | Transport gate opening dimensions |  | . . . . .. . . . . . . . . . . . . .36 |  |
| Appendix H |  | Gate truck |  | . . . . . . . . . . . . . . . . . .37 |  |
| Appendix J |  | Layout of the MST half and Stud Turning Robot on the gate truck |  | . . . . .. . . . . . . . . . . . . .39 |  |
| Appendix K |  | Layout of the MST half on the transportation trailer-truck |  | . . . . . . . . . . . . . . . . . .40 |  |
| Appendix L |  | Layout of the transportation and storage stand on the transportation trailer-truck |  | . . . . . .. . . . . . . . . . . . .41 |  |
| Appendix N |  | Layout of the Stud Turning Robot and electric equipment on the transportation trailer-truck |  | . . . . . . . . . . . . . . . . . .42 |  |
| Appendix Р |  | Removable retainers for arranging the MST on vehicles |  | . . . . . . . . . . . . . . . . . .43 |  |
| Appendix Р1 |  | Overall dimensions of 32 t hook hanger of the reactor building crane and of 32 t hanger of the portal crane |  | . . . . .. . . . . . . . . . . . . .44 |  |
| Appendix R |  | Overall dimensions of 390 (205) t hanger fork of the reactor building crane |  | . . . . . . . . . . . . . . . . . .45 |  |
| Appendix S |  | The 32 ton hoisting capacity hook of the bridge crane at the TTE warehouse |  | . . . . .. . . . . . . . . . . . . .46 |  |
| Appendix Т1 |  | DBE level response spectra |  | . . . .. . . . . . . . . . . . . . .47 |  |
| Appendix U |  | Applicable rules and regulations |  | . . . . . . . . . . . . . . . . . .49 |  |

1 Наименование и область применения

The article name – Multiple stud tensioner for the Reactor primary joint.

Article KKS Code _____________________________

- Scope of application

1.2.1

The MST is intended for:

- automatic controllable simultaneous elongation of all RPJ-studs to the set value when sealing and depressurization the RPJ flange connection with ensuring the same (within the tolerance) design extraction of the studs when performing compressing operations;

- mechanized unscrewing and screwing of the stud connection nuts on the RPC flanges with the use of a manually operated tool after the RPJ-studs are extracted;

- automated screwing in and unscrewing of the studs from the reactor vessel flange stud seats;

- automated measurement of the RPJ-stud elongation value with the measured value recording;

- transportation of RPJ compressing elements (nuts, studs and washers) during assembly-disassembly of the reactor.

2 Basis for Development

The basis for development is OKB „Hydropress“ JSC technical requirements for the reactor primary joint multiple stud tensioner

3 Development Purpose and Designation

3.1 The development purpose of these Terms of Reference is to design an innovative RPJ multiple stud tensioner for reactor facility, to ensure the functions of simultaneous elongation of the RPJ-studs and the ability to transport fasteners to (from) the reactor vessel.

3.2 These Terms of Reference contain the main requirements and necessary technical data that determine the main parameters, characteristics and operating conditions, as well as information on the delivery completeness of RPJ multiple stud tensioner for NPP.

3.3 The task to be solved by the development is to create a MST design ensuring:

- sealing and depressurization of the RPJ by means of simultaneous and uniform elongation of the RPV-studs;

- simultaneous elongation of RPJ-studs within the design value (2,2±0,1) mm;

- protection of structural elements of the flanged connection of the reactor vessel against damage;

- reduction of labor costs and dose consumption by the maintenance personnel

- reducing the time for compaction and decompaction of the RPJ.

4 Source of Development

4.1 The source of development is:

- automatic multiple stud tensioner for simultaneous elongation of the RPJ-studs manufactured by;

- OKB „Hydropress“ JSC technical requirements for the reactor primary joint multiple stud tensioner).

5 Technical Requirements

5.1	Basis for design

5.1.1 Design, manufacture, testing and operation of the MST shall be carried out in accordance with the requirements of the normative documents specified in Appendix U, taking into account the experience of creating similar equipments and the experience of their operation.

5.2	General requirements

5.2.1	In accordance with NP-001-97, MST is classified as safety class 4.

5.2.2	In accordance with NP-031-01, MST and its component parts are assigned to seismic category III. Load-lifting devices that are part of the wrench (traverse of the half, the sling, cargo braces) - are classified as seismic category II in accordance with NP-031-01. MST seismic safety group - 3 in accordance with GOST 30546.1-98.

The quality assurance category is QNC  in accordance with STO SMK-PKF-015-06.

5.3	The equipment composition and requirements for the structural design

5.3.1 The equipment shall include:

а)	MST 54/8000-DR100 tensioner;

b)	a test stand for the MST, including 52 RPJ-stud imitators and two original RPJ-studs, the stand weight is maximum 13.5 tons;

c)  transport pull rods for transportation of the MST with a universal traverse – 1 set;

d)	a traverse for transporting the MST halves in the reactor building (RB) and to the transport-technological equipment  (TTE) warehouse – 2 pcs.;

e)	a transport and storage stand – 1 set;

f)	tools and devices for servicing the MST;

g)	a set of spare and wear parts for two years;

h)	a set of mounting parts;

i)	containers (boxes) for transportation of RPJ-washers to the TTE warehouse and back- 4 pcs.;

j)   removable retainers as per Appendix P;

k) transport packaging – 1 pc., transport plate 2 pcs. with fasteners Ml0 – 8 pcs.

5.3.2 The MST shall include the following parts:

-	the support ring;

-	support ring brackets;

-	tensioning units;

-	device for unscrewing (screwing in) RPJ-nuts;

-	compensation (Gap) cylinders;

-	piston stroke limitation;

-	three bushings for centering the MST;

-	set of adapters for RPJ-studs per one unit in the amount of 58 pcs. including 54 pcs. for RPJ-studs, 2 pcs. for the test stand, 2 pcs. – reserve;

-	a set of RPJ-nut adapters for one unit in the amount of 58 pcs. including 54 pcs. for RPJ-nuts, 2 pcs. for the test stand, 2 pcs. – reserve;

Note:

At the request of the customer, additional sets of adapters for RPJ-studs and RPJ-nuts can be supplied under a separate supplementary agreement to the contract for the screwdriver.

-	hydraulic aggregate;

-	hydraulic connections;

-	guiding devices for MST;

-	a set of electrical equipment;

-      power supply system;

-	an working platform for stud turning robots;

-	two stud turning robots;

-	a cabinet accommodating the control system;

-	central and local control panels

-      a computer;

-     manually operated and mechanized tools for RPJ-nuts with pre-setting of the limiting torque;

-	the stud extension control and recording system, systems for measurement of pressure in hydraulic jacks used for elongation the RPJ-studs, control of the RPJ-nut torque magnitude ;

-   a set of load-lifting means, in accordance with the requirements of clause 5.3.1 for performing transport-handling operations with the MST and its parts;

-	special tools;

-	stationary lighting;

-	the two-way communication system between the operator at the control panel and the operator at the MST.

5.3.3 The overall dimensions of the MST are shown in Appendix B.

5.3.4 The MST design shall provide:

- the ability of its transportation by separate parts within the NPP with subsequent assembly into a single structure in the reactor building or in the TTE warehouse;

- engagement of the MST load-gripping devices with cargo hangers (hooks) of load-lifting equipment of the NPP reactor building and the THE warehouse;

- mounting (installation) of the MST on the upper unit (UU) in the concrete cavity of the reactor using the upper unit guide rails;

- tightness of the hydraulic system, protecting against ingress of mineral oils to the reactor and the maintenance level of the reactor building;

- the ability of engagement with the RPJ-nut and RPJ-stud via the nut and stud adapters;

- sealing and depressurization functions of the RPJ;

- screwing (unscrewing) the RPJ-studs functions;

выполнение функций гайковерта по ввинчиванию (вывинчиванию) шпилек;

- the use of an electric drive for pumps, hydraulic system fittings, for the device designed for screwing (unscrewing) RPJ-nuts on the RPJ-studs, devices for screwing (unscrewing) traction RPJ-nuts on RPJ-studs and for Stud Turning Robots;

- the ability of fixing the RPJ-studs in the MST while moving;

- the possibility of removing the Stud Turning Robots;

- corrosion resistance under operating conditions according to clause 5.9.3;

- resistance to the action of deactivating solutions according to cl.5.9.6, cl.5.9.7;

- prevention from human errors when assembling the MST systems using locks;

- resistance to the load impact in accordance with 5.10.1.

5.4 Applicability indices

5.4.1 The MTS shall have the following applicability indices:

-	the MST type is electrohydromechanical;

-	the number of simultaneously extracted studs is 54 pcs.;

-	the maximum force developed by each hydraulic jack is minimum 8000 kN ;

-      deviation of the elongation force from the nominal drawing force - ±2%;

-     the estimated value of the RPJ-stud elongation when being elongated is (2,2 ± 0,1) mm;

-	the accuracy of measuring the RPJ-stud extension is 0.05 mm;

-	the RPJ-stud screwing torque is minimum 250 Nm;

-	the RPJ-nut tightening torque is minimum 5 Nm;

-	the RPJstud unscrewing torque is minimum 600 Nm;

-	time of RPJ sealing and depressurization (under the equipment normal functioning condition (crane of reactor building, traverse, grippers, etc.), compliance with the technological process of the MTS installation on the RPJ):

a) sealing is maximum 5 hours;

b) depressurization is maximum 4 hours;

-	electrical equipment parameters:

а)  power supply from the electric network of NPP via the TN-S system (3 phases, N and PE);

b)	the voltage is V,V;

c)	frequency is (50±1) Hz;

d)	power consumption is maximum 30 кW;

e)	supply voltage of the device for screwing (unscrewing) RPJ-nuts is 36 V (provided by MST electrical equipment);

-	the MST assembly weight is maximum 42 tons;

-	the weight of the MST crane-transported part with installed RPJ studs and nuts is maximum 63 t.

5.4.2 The pressure value in the hydraulic jacks of the tensioning units is converted into the force value of the RPJ-stud elongation according to the special tables given in the MST manual and additionally installed on the front panel of the hydraulic aggregate. Calibration of the tensioning units during the lifetime of the MST is not required.

5.5 Reliability requirements

5.5.1 Reliability requirements  in accordance with GOST 26291-84.

5.5.2 Reliabilities for operating time T = 10 hours is not less than P (t)> 0.99.

5.5.3 Assigned operation time is Tr =  8000 hours.

5.5.4 The availability factor is Кr ≥ 0,7.

Note:

Values according to cl. 5.5.2 – cl.5.5.4 are estimated.

5.5.5 The time to restore the working state (when used for its intended purpose) is not more than 50 hours.

The MST design does not provide for recovery of the resource (the assigned lifetime) by means of a capital or a mid-life repair.

The maintainability of the MST and its components shall be ensured by the restoration (in the event of failures) of its operable state in the process of maintenance and repair, including the replacement of failed parts with serviceable ones from the kit of spare parts.

5.5.6 The MST service life is least 65 years, provided that the wear parts are replaced.

5.5.7 The failure of the MST and its components is the failure of the main functions and non-compliance of the operating parameters to the specified limits.

5.5.8 The ultimate condition for the MST is the service life runout or presence of mechanical defects on the support rings (cracks between the seats, on welds of the joint flanges, change in the shape of the support rings half – appearance of an unacceptable ovality).

5.5.9 Average shelf life in the original packaging when stored in a closed heated room is minimum 3 years.

5.6	Manufacturability requirements

5.6.1 The design shall take into consideration the factors of operational manufacturability affecting the ease of operation and maintenance of the MST when carrying out transport and technological operations.

5.7	Safety requirements

5.7.1 The multiple stud tensioner shall be developed in accordance with the electrical, fire, general safety rules, as well as the requirements of radiation safety and environmental standards in accordance with the main regulatory documents and standards in force in Russian Federation.

5.7.2 When installing, operating and repairing the MST, it is necessary to comply with the safety requirements regulated by the rules and regulations in force in the operating organization:

-    Safety Requirements for Operation of Load-Side Electrical Installations;

-   Inter-Industry Occupational Safety and Health Regulations (Safety Regulations) for Operation of Electrical Installations;

-  Installation and Safe Operation Requirements for Pipe-Laying Machine Safety;

- Rules for the Arrangement and Safe Operation of Cranes for Nuclear Facilities NP-043-11.

- Occupational safety standards system. Industrial equipment. General safety requirements GOST 12.2.003-91.

5.7.3 The MST hydraulic system design shall to the fullest extent prevent the working fluids from penetrating the reactor and the reactor building maintenance level as much as possible.

5.7.4 The MST design and the organizational and technical measures for its operation shall ensure the safety of personnel in view of the high-pressure hydraulic system availability.

5.7.5 On the way to protect a person from electric shock, the MST must meet the requirements of GOST 12.2.007.0-75.

5.7.6	Guidelines for the implementation of safety requirements should be given in the MST manual.

5.8 Requirements for components, materials and welding

5.8.1 The MST components shall be made of materials that meet the requirements of the regulatory documents in force in the Russian Federation and ensure the strength and reliability of the article throughout its service life.

5.8.2 Welding of the MST assemblies and parts shall be carried out according to the manufacturer‘s welding procedure using welding materials that ensure the strength of structures.

5.8.3 Seals used in hydraulic systems shall have a service life of at least four years without replacement.

5.8.4 Quality control of welded joints shall be carried out according to the manufacturer‘s regulatory documentation in force in accordance with the requirements of the detailed design documentation.

5.8.5 The hydraulic fluid used in the hydraulic system shall have an ignition temperature of at least 200 ° C and be easily removed when using binders.

5.8.6 The multiple stud tensioner elements made of carbon steel shall have protective (galvanic, paint, etc.) coatings resistant to operating conditions according to cl. 5.9. Protective paint and varnish coatings must meet the requirements of GOST R 51102-97.

5.8.7 No additional anticorrosive coating is required for MST elements made of stainless steel. It is only necessary to provide the necessary protective measures for the MST transportation and storage.

5.8.8 Electric connectors for connecting the MST to the NPP power systems in the reactor building and at the storage site are supplied complete with the MST.

5.8.9 The measuring instruments used shall have valid calibration certificates; the multi- stud tensioner manual should specify the frequency and methods of conducting verifications (or calibrations). The measuring instrument design shall limit access for unauthorized settings and interventions.

5.9 Operation, repair, maintenance requirements.

5.9.1	The placement category is 4, the climatic category is  - Т, storage and operation atmosphere type is ПI (marine) according to GOST 15150-69.

5.9.2 The MST operating site is the reactor concrete cavity. The two halves of the MST are transported into the reactor building. Assembly of the two MST halves into one unit is carried out at the transport and storage stand. The transport and storage stand is also transported into the reactor building in two halves and is mounted on adjustable supports. The dimensional drawing of the transport and storage stand is given in Appendix E, method of fixation and layout of the stand support is according to Appendix E1.

The assembled MST is stored at the TTE warehouse on the test stand with the installed electrical equipment. The dimensional drawing of the test stand is given in Appendix D. The method of fixation and the plan for the location of the support of the test stand in accordance with Appendix D1.

The transport and storage stand is also stored at the TTE warehouse. The fixation method and the layout for stud storage stand according to Appendix E1.

Storage conditions of the MST components at the TTE warehouse - the temperature is (15-33) oС, relative humidity is up to 80%, the pressure is atmospheric, the premise category is D as per CR 12.13130.2009.

5.9.3 Environmental parameters on the multiple stud tensioner operation site:

a) the ambient air temperature in the RPJ location area after the reactor cooling down is (+ 15  +40)° C;

b) the surface temperature of the sealed flange is maximum 40 ° C;

c) the relative humidity of air (at 25 °C) is maximum 100%;

d) pressure, kPa is from 101,325 (atmospheric) to 101,125 (vacuum, 200 Pa);

e) the absorbed dose rate is maximum 1.0 Gy / h;

e) volumic activity is maximum 7.4 * 107 Bq / m3

5.9.4 The main dimensions of the RPJ are given in Appendix A..

5.9.5 The MST is mounted on the upper unit along the guide rails in the concrete cavity. The layout of the UU guide rails in the reactor cavity is in accordance with Appendix F.

5.9.6 Structural materials and protective coatings of MST equipment (MST, the transport and storage stand, transport pull rods, traverses for transporting of the MST halves) shall withstand the effect of deactivating solutions in accordance with RD 210.006-90.

5.9.7 The electrical equipment is deactivated by wiping with mixture (40...60)% Freon and  (60...40)% rectified ethyl alcohol. Wiping with water is not allowed.

5.9.8 Protective paint coatings shall be selected by the MST designer in accordance with the requirements of GOST R 51102-97.

5.9.9 Cables of electrical equipment shall be designed to operate under conditions of exposure to gamma radiation with a radiation power of up to 1.0 Gy/hr and are made in a flame-retardant design.

5.9.10 cables must comply with SRT 1.1.1.01.001.0902-2013 "Cable products for nuclear power plants" Table. А.2 cl.1.3.

5.9.11 The MST shall function properly after installation on the RPJ. Maintenance, adjustment of the MST with testing of all systems shall be performed in the TTE warehouse on the test stand after each regular repair of the MST and immediately prior to its use on the RPJ. The list and sequence of operations shall be stated in the operational documentation

5.9.12 The special stand can be used to check the extraction assemblies4 (this stand is optional and is supplied under a separate supplementary agreement to the MST supply contract) to check the MST tensioning units after the routine repair is completed (replacement of the seals).

5.10	 Requirements for resistance to loading.

5.10.1 The MST shall be designed taking into account the following types of impacts and loads:

а)	Normal operating conditions (NOC):

- loads (forces) acting on the elements during the technological operations aimed at elongation of the RPJ-studs;

- loads acting on the MST from its own weight, during transport and technological operations with the MST in the NPP reactor building and during the MST transporting to TTE warehouse.

b)	special dynamic effects:

- the seismic impact load is VII points according to MSK-64 scale. The DBE level response spectra are given in Appendix T1.

5.11	 Marking requirements

5.11.1 A nameplate with data in English shall be affixed to the MST:

-	the manufacturer‘s trademark;

-	product name and designation;

-      serial number according to the manufacturer‘s numbering system;

-      KKS Code;

-	year and month of manufacture;

-	weight in tonn.

The marking shall be provided by engraving on a metal plate made of corrosion-resistant steel.

5.11.2 Marking of parts, assembly units and welded joints of equipment is provided in accordance with the requirements of design documentation and regulatory documentation in force at the manufacturer and the territory of the Russian Federation.

The parts and assembly units shall be marked as shown in the drawings. The marking of assembly units shall be carried out by impact method (stamping). The marking shall be retained at any stage of the manufacture of parts and assemblies.

Instrumentation and control equipment shall bear an inscription in English.

5.11.3 When shipping the manufactured article, each shipping package shall be marked in accordance with the requirements of the documentation developed by the manufacturer on the basis of the requirements of the article supply contract concluded with the Customer.

5.11.4 Additional transport marking is applied clearly to the cargo packages with indelible paint and shall contain handling signs in accordance with GOST 14192-96 that establish methods of handling the cargo and adopted in international trade practice.

5.11.5 For cargo packages of equipment that is not packed, the transport marking shall be applied directly to the equipment or to labels / tags affixed to the equipment in any way that ensures the safety of labels / tags for the period of transportation and storage.

5.11.6 The equipment marking can be supplemented in accordance with the terms of the concluded supply contract.

5.12 Packaging, transportation and storage requirements

5.12.1 Packing shall be carried out in accordance with the requirements of GOST 23170-78.

5.12.2 Requirements for packaging according to GOST 24634-81. The lumber used for packing the cargo shall be processed in accordance with GOST 15155-99 to ensure protection against biological destruction by fungi and insects. Processing of the lumber used in the equipment packaging and fastening parts shall be confirmed by an antiseptic finishing certificate.

5.12.3 The MST in the package shall allow for transporting by road, rail and sea.

The MST transportation condition shall comply with:

-	when transported by rail or road transport – transport conditions 5 of GOST 15150-69 in terms of the effect of climatic factors, in terms of the effect of mechanical factors – “hard” GOST 23170-78;

-	when transported by sea – transport conditions 3 of GOST 15150-69 in terms of the effect of climatic factors (in covered premises of ships), “hard” in accordance with GOST 23170-78 in the terms of the effect of mechanical factors.

Temporary storage of equipment in anticipation of loading is carried out in open areas under the environment climatic aspects influence 9 in accordance with GOST 15150-69

5.12.4 Conservative and internal packaging of the article component parts shall comply with GOST 9.014-78 and shall ensure protection during storage in the manufacturer‘s packaging for three years. Conditions for the packaged multiple stud tensioner storage are 3 in accordance with  GOST 15150-69, type of atmosphere – III. Operation type of atmosphere – II.

5.12.5 Periodically, but at least once a year, the consumer shall monitor the packaging preservation state, if necessary, restore it.

5.12.6 The scope of requirements for packaging, transportation and storage can be changed in accordance with the terms of the concluded contract.

5.12.7 After depressurization of the RPJ, transportation of the RPJ-studs to the stand, the MST shall be disassembled to allow the parts to be transported through the transport gate to the TTE warehouse.

The transport gate opening dimensions and cross-section according to Appendix G.

The TTE warehouse gate opening dimensions: height is 70 00 mm, width is 4 000 mm.

The MST parts are transported in (transported out) to the reactor building on the gate truck via the transport gate. Dimensions of the gate truck are in accordance with Appendix H.

Layouts of the MST half and Stud Turning Robot on the gate truck are in accordance with Appendix J.

The stud turning robot (2 pcs.) shall be transported on the transport plate (2 pcs.), which comes with the MTS. The transport plate with the STR anchored on it when transported on the gate truck shall be secured to the floor of the truck with Ml0 bolts (4 pcs. each).

5.12.9 The largest dimension of the transported part (half) of the MST is 5500 mm in length, 3200 mm in width, and 5700 mm in height. To decrease the overall height of the MST half, the MST half is transported without the stud turning robots, so that the overall height is reduced to 3340 mm..

5.12.10	The multiple stud tensioner components are transported on the trailer-truck frame on the territory of the NPP.

The trailer Designer shall provide for installation of removable retainers and equip the semitrailer with a removable support beam to arrange the three multiple stud tensioner supports on the semitrailer in a horizontal plane and to prevent from being displaced during transportation. The design of the support beam is determined by the trailer-truck Designer.

The same principle shall be used by the trailer-truck Designer to provide for the installation and fixation of the transportation and storage stand half on the platform. Herewith dimensions of the stand support position on the trailer-truck shall be used from Appendix L. The design of the support beam for the transportation of the stand on the trailer-truck is determined by the trailer-truck designer.

Equipping the trailer-truck with additional elements (beams, fasteners) shall be included in the trailer-truck scope of supply. Removable retainers shall be included in the multiple stud tensioner scope of supply.

For the period of transportation, the articles to be transported shall be preserved according to the operational documentation

5.12.11 Lifting (lowering) the MST half onto the ramp, installation (removal) on the gate truck is carried out by means of the traverse for the multiple stud tensioner halves that is hung on the ramp crane and electric bridge polar crane hook with a hoisting capacity of 32 tons. The dimensions of the hook of 32 t hoisting capacity are according to Appendix S.

5.12.13 The MST halves transported during operation are hung through the slinging devices (or attachments) onto the electric bridge polar crane hanger hook of the 32 ton hoisting capacity.

In the reactor building the MST as the whole is transported using the universal traverse. The traverse is hung on the fork of 390 (205) t crane electric bridge polar crane. Overall dimensions of the fork are 390 (205) t – according to Appendix R.

Installation of the MST on the RPJ and removal are also carried out using the universal traverse along the guide rails of the upper unit (UU) in the reactor cavity.

When transporting the MST in the reactor building, the distance between the lower part of the MST and the ceiling, as well as over the heads of the reloading machine rails shall be no more than 100 mm.

Requirements for the universal traverse are according to cl. 5.13.2.

At the TTE warehouse the halves of the MST are transported using the traverse intended for the MST halves and mounted on the 32t hook of the bridge crane with a hoisting capacity of 32 / 5t. Dimensions of the 32 t hook of the bridge crane are according to Appendix S.

5.12.14 The test stand (Appendix D), where the multiple stud tensioner is tested, the use of the MST as a simulating tool for personnel training, and the storage of the MST prior to the next use, is kept at the TTE warehouse.

The layout of the transportation and storage stand with the MTS installed on it in the reactor building is according to Appendix E1, the required area is 6.5m x 6.5m.

The layout of the test stand on the embedded parts in the TTE warehouse is according to Appendix D1.

The site for the MST and the test stand in the TTE warehouse shall ensure the following:

а)	it shall be equipped with power supplies with parameters according to cl. 5.4, located at a distance of no more than 20 m from the test stand;

b)	a place for installation of two halves of the MST on two halves of the transportation and storage stand having the following dimensions – 6.5m x 6.5m;

c)	the place for installation of the test stand. The dimensions of the site for installation of the test stand are 7.5 m x 7.5 m, taking into account the passes for the personnel around the stand for assembling, setting up the MST.

5.13 Requirements for station systems

5.13.1 It is necessary to have a power supply with parameters as specified in cl. 5.4 for the normal operation of the multiple stud tensioner in the reactor building and in the TTE warehouse. Power supply is fed to 380V, 63A outlet of the RF. Outlets for the reactor building and for the TTE warehouse are supplied together with the MTS. Power supply to the outlet is ensured via the TN-S system (3 phases, N and PE), the cable brand is selected in accordance with the current norm and rules. The outlet locations in the reactor building and in the TTE warehouse is not more than 20 m from the control panel of the multiple stud tensioner, which is located next to the multiple stud tensioner. The need for areas in the reactor building and in the TTE warehouse is in accordance with cl. 5.12.12.

5.13.2 The requirement for a universal traverse

5.13.2.1 The universal traverse, provided in the design documentation of the NPP, for the possibility of slinging and transportation of the MST must be of a size 1270+150mm, Ø3800±10mm is according to Appendix B. The specified sizes are subject to specification after the development of the universal traverse and must be agreed with the developer of the MST.

5.13.2.2 The carrying capacity of the traverse when transporting the MST shall be minimum 63 t.

5.13.3 Requirements for the gate truck and the trailer truck shall be in accordance with clauses 5.12.7, 5.12.8.

5.13.4 The hydraulic system is mounted on the multiple stud tensioner and no individual requirements are imposed to the station systems.

5.13.5 According to cl. 5.12.12 there shall be no zones unserved by load-lifting equipment.

5.13.6 The requirements for the station systems, as specified in the ToR, include requirements to the MST. Additional requirements for station systems in other MST documents are not specified. Based on the results of the detailed design documentation development, the requirements can be clarified by agreement of organizations participating in the approval of these Terms of Reference.

5.14 Patent Purity Requirements

5.14.1 When objects of the patent law are created (used) in the development process, the information on the security documents issued by the Designer (patents, certificates, etc.) shall be notified to the Customer and recorded in the article operational documentation

5.15 Requirements for standardization and unification

5.15.1 The MST and its component parts shall be designed, manufactured, packaged and delivered in accordance with the requirements of the standards, norms and regulations in force in the Russian Federation.

5.16 Completeness

5.16.1 The multiple stud tensioner of the reactor principal connector and technical documentation are supplied in the scope specified in Table 5.16.1.

Table 5.16.1

| Description | Q-ty, pcs | Operating weight, kg |
| --- | --- | --- |
| Multiple stud tensioner of the reactor principal connector consisting of: Multiple stud tensioner MST 54/8000-DR100-ST (including hydraulic, mechanical, electrical equipment, spare parts, accessories, load-lifting equipment) in the specification scope, agreed with the Client prior to the delivery Test stand Transportation and storage stand Working platform Adapter for RPJ-nut Adapter for RPJ-stud RPJ-nut electrical tool RPJ-nut hand-operated tool Container for transporting the equipment Container (box) for transportation of RPJ-washers Transport pull rod Fastening parts for protection against displacements Operational documentation, including : - the data sheet with attached certificates for used materials and semi-finished products, declarations of conformity and other documents certifying the quality (certified copies), as well as test reports conducted in the process of the equipment manufacture and acceptance; - a set of DD, including the ToR, assembly drawings for the equipment and its main components with indication of dimensions; - technical documentation for component parts being a part of the equipment; - list of spare parts, tools and devices (SPTA) for installation, commissioning, operation and maintenance during the warranty period; - an operation manual that includes technical description, instructions for the depreservation (preservation), transportation, storage, installation, commissioning, operation and maintenance, as well as a list of control, management, signalling and automation devices, included in the delivery set and a diagram (instructions) for their installation; - repair documentation5, including guidance on the current repair, maintenance and repair program (s) (if the information is not reflected in the operation manual), assembly drawings and the information for ordering the equipment components with service life that is less than the service life of the equipment in general, the list of repair spare parts; | 1 set 1 set 1 1 1 56 56 2 2 1 4 2 cl.53.l j),k) 1 set 1 set 1 set 1 set 1 set 1 set | 66 500 46 100 13 100 2 500 3 100 112 868 16 12 580 570 80 20 |

5.16.2 Contents of delivery may be changed in accordance with the terms of the concluded contract.

6 Development stages and phases

6.1 Development stages and phases are given in the Table 6.1

Table 6.1

| Development stages | Work execution stages |
| --- | --- |
| - Detailed engineering documentation | Terms of Reference Development Detailed engineering documentation development Multiple stud tensioner manufacture and its completing as a set Preliminary tests Multiple stud tensioner acceptance tests |

6.2 The MST shall be produced as per GOST R 15.201-2000 and these ToR.

6.4 At the detailed engineering documentation intended for manufacture of electrical, hydraulic and mechanical equipment the following documents are developed:

-	assembly units and parts drawings;

-	specifications (including SPATm service tools);

-	assembly drawings;

-	electrical connection schemes and connections tables (cable logbooks);

-      hydraulic schemes;

-   instructions on installation, operations and maintenance, preservation and depreservation, transportation and storage;

-	reliability, strength and seismic resistance calculation;

-	program and procedure for Preliminary  testing;

-	program and procedure for acceptance testing.

6.5	The operation documentation supplied with the multiple stud tensioner shall be as that specified in table 5.16.1. In addition, in the structure of the documentation shipped with the MST the working drawings of the parts to be replaced.

6.6	Certain requirements of these Terms of Reference can be specified, supplemented and changed at any stage of the article development as agreed with the enterprises and organizations that agree and approve these Terms of Reference.

7 Control and acceptance procedure

7.1 In accordance with GOST R 15.201-2000, the MST is to be tested as a prototype model of the custom-made product.

7.2	In the process of the MST manufacture and acceptance, the following control types shall be carried out by the manufacturer:

-	complete control of materials and semi-finished products in the scope established by the manufacturer;

-	operational control for compliance with the requirements of detailed drawings and process documentation;

-	acceptance control.

7.3	The scope of acceptance control includes:

а)	check of overall and connecting dimensions;

b)	check of the following characteristics of the MST:

-	the maximum force developed by the MST;

-	the design value of the RPJ-stud elongation force;

-	the RPJ-stud elongation length;

-	the maximum RPJ-stud screwing torque value;

-	the maximum RPJ-stud unscrewing torque value;

-	performance of the RPJ-nut turning tool value;

-	performance of the stud turning robot value.

c)	completeness check;

d)	marking check;

e)	preservation and packaging check.

7.4	Verification of the indices in accordance with cl. 7.3 shall also be carried out according to the program developed by the manufacturer and the preliminary testing procedure (to be conducted for a preliminary assessment of the prototype product compliance with the requirements of ToR, and also for determining the prototype readiness for acceptance tests)

7.5	The program and methodology of preliminary tests should contain requirements for the conditions of testing, the composition of documentation required for testing, types of tests, the composition of the commission and organizations that agree on the program.

The program and methodology of preliminary tests shall include checking the indices (characteristics) for compliance with the requirements of the terms of reference, as well as for determining the multiple stud tensioner readiness for acceptance testing.

Preliminary tests are allowed to be conducted under the acceptance testing program and procedure.

The program and procedure of preliminary tests shall be submitted to the Customer for information.

7.6	Positive results of the preliminary tests are the basis for conducting the acceptance tests.

7.8 The program and the acceptance test procedure shall contain the types of tests and include the verification of the indices (characteristics) for compliance with the requirements of the terms of reference, including checking the conformity of the design method for monitoring the stud elongation force to clause 3.9 of technical requirements 509-Pr-043, and establishing the ability to use the MST for its intended purpose. Acceptance tests are carried out on the test stand supplied as part the multiple stud tensioner scope of supply.

Compliance verification of the real force developed by the tensioning units with the design value determined based on the pressure in the cylinder is carried out on the special stand that is not included in the scope of supply of the MST.

The positive results of the acceptance tests are the basis for deciding whether to use the MST for the purpose, which is specified in the acceptance test.

7.9 Defects and deviations identified during manufacture and acceptance shall be eliminated or approved appropriately.

If it is not possible to eliminate defects or approve the deviations, the article is rejected and not allowed for use.

7.10	 Completeness shall be checked visually.

7.11	 Marking shall be checked visually.

7.12	 Presevation and packaging shall be checked visually for compliance with the design documentation.

8 Quality assurance

8.1	The MTS developer shall ensure the quality of the article development in accordance with the current quality assurance system.

8.2	The manufacturer shall ensure the quality of the MST and its components in accordance with the terms of reference and the working documentation within the manufacturer‘s quality assurance system in force.

8.3	The Customer and his representatives have the right of access to the manufacturer to participate in monitoring and testing procedures, as well as in inspections.

9 Гарантии поставщика

9.1 The supplier shall ensure the compliance of the MST with the requirements of these terms of reference, provided that the consumer observes the conditions of transportation and operation.

The warranty period of storage ends after 24 (twenty-four) months from the date of the article shipment.

In case of postponement of the acceptance certificates signing for the start-up facility for a later period, the extension of the warranty obligations for the equipment is carried out subject to additional financing.

Appendix А

(mandatory)

Reactor primary joint sealing unit

Spread smoothly

No protrusion is allowed

8 slots

2 slots

Appendix B

Multiple Stud Tensioner. Dimensional drawing

Transportation and storage stand

Hanger folk 360(205)t

Pump

station

Working platform with stud turning robots

Support ring with tensioning units

Transport system

Fig. B-1

Fig. B-2

Guiding device

Guiding device

Fig. B-3

Appendix C

TTE warehouse

Transportation and storage stand

MST Halve

Halves traverse

Appendix D

Test stand.

Dimensional drawing

RPJ-Washers

RPJ-Nut

RPJ-Stud

RPJ-Stud mimic

Имитатор шпильки ГРР

52 mimics of the RPJ-stud and 2 original RPJ-studs are part of the stand scope of supply

Appendix D1

Layout of the test stand supports in the inserts at TTE warehouse

Loads on each plate

P = 10 t at NOC

)

Support plate

Insert details

Appendix E

Transportation and storage stand.

Dimensional drawing

Appendix E1

Layout of the transportation and storage stand in the reactor building and at TTE warehouse

of the Stand half

Connector line

(Лист 32)

from the supply scope

Detachable retainer

Insert plate is not supplied

The detachable retainer is

complete with theMTS

Stand support is supplied

Vertical load from each support is 11 t

(Лист 32)

Appendix F

Reactor cavity with guide rails

А (Sheet 35)

(Sheet 34)

А (Sheet 34)

Appendix G

Transport gate opening dimensions

Appendix H

Gate truck

Appendix J

Layout of the MST half and Stud Turning Robot on the gate truck

Stud Turning Robot

MST halve with traverse

Appendix K

Layout of the MST half on the transportation trailer-truck

MST axis

Trailer axis

MST halve with traverse

Appendix L

Layout of the transportation and storage stand on the transportation trailer-truck

Trailer-truck

Appendix N

Layout of the Stud Turning Robot and electric equipment on the transportation trailer-truck

Trailer-truck

Appendix Р

Removable retainers for arranging the MST on vehicles

MST support

3 places

Support plate of the vehicle

Retainer

Installation of the MST half on the gate truck

3 places

MST support

Support plate of the vehicle

Retainer

Installation of the transportation and storage stand on the gate truck

Retainer

MST support

Installation of the MST half on the detachable frame of the transportation trailer-truck

Appendix Р1

Overall dimensions of 32 t hook hanger of the reactor building crane

and of 32 t hanger of the portal crane

Note:

these dimensions are preliminary and are subject to clarification after receiving the BOD from the developer of an electric bridge polar crane

Appendix R

Overall dimensions of 390 (205) t hanger fork of the reactor building crane

Extending shaft diameter

Appendix S

The 32 ton hoisting capacity hook of the bridge crane at the TTE warehouse

Appendix Т1

DBE level response spectra

When using the response spectra, it should be borne in mind that seismic action should be applied simultaneously in three directions (horizontal action-in two mutually perpendicular in the horizontal direction, vertical-in the vertical direction).

The response spectra are given for relative damping of 1%, 2%, 4%, 5%, 7% and 15%. ответа даны для относительного демпфирования 1 %, 2 %, 4 %, 5 %, 7 % и 15%. The response spectra for intermediate relative damping values should be determined by interpolation. The response spectra for intermediate marks should also be determined by interpolation.

Reactor thrust truss

Appendix U

Applicable rules and regulations

| Обозначение документа | Наименование документа |
| --- | --- |
| GOST R 8.596-2002 | State system for ensuring the uniformity of measurements. Metrological assurance for measuring systems. Main principles |
| GOST R 12.1.019-2009 | Occupational safety standards system. Electrical safety. General requirements and nomenclature of kinds of protection |
| GOST R 15.201-2000 | System of product development and launching into manufacture. Products of industrial and technical designation |
| GOST R 51102-97 | Decontaminable protective polymeric coatings. General technical requirements |
| GOST 8.326-89 | State system for ensuring the uniformity of measurements. Metrological certification of measuring instruments |
| GOST 9.014-78 | Unified system of corrosion and ageing protection. Temporary corrosion protection of products. General requirements |
| GOST 12.1.003-83 | Occupational safety standards system. Noise. General safety requirements |
| GOST 12.1.004-91 | Occupational safety standards system. Fire safety. General requirements |
| GOST 12.2.007.0-75 | Occupation safety standards system. Electrical equipment. General safety requirements |
| GOST 12.2.049-80 | Occupational safety standarts system. Indastrial equipment. General egronomic requirements |
| GOST 14192-96 | Marking of cargoes |
| GOST 15150-69 | Machines, instruments and other industrial products. Modifications for different climatic regions. Categories, operating, storage and transportation conditions as to environment climatic aspects influence |
| GOST 23000-78 | Man-machine system. Control consoles. General ergonomic requirements |
| GOST 23170-78 | Packing for products of engineering industry. General requirements |
| NP-001-15 | General provisions for ensuring safety of nuclear power plants |
| NP-031-01 | Design standards of earthquake-resistant nuclear power plants |

| SHEET OF REVISIONS |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rev | Sheet (page) numbers |  |  |  | Total sheets (pages) in doc. | Doc. No. | Support doc. incoming No. | Signa-ture | Date |
|  | Revised | Substituted | New | Cancelled |  |  |  |  |  |

RPJ-studs with RPJ-nuts are transported using devices holding the tensioner. RPJ-washers are transported in special containers that are part of the tensioner

The nut tightening torque value is determined by setting the torque limit on the RPJ-nut tool being a part.

This force value is confirmed during the MST acceptance tests and is not subject to inspection when operating the unit

The stand is used to check the tightness of the tensioning units and the compliance of the hydraulic jack pressure and the elongation force value generated by each tensioning units