## Significant
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER ATL 16-1253 | 2016-11-20 | 2017-01-03 06:26 | Barakah-4 | Personnel Fatality due to Fall | Significant | During construction and while performing steel beam installation at turbine building, one individual fell 20 feet, causing injuries to the head and other parts of the body. The individual was taken to the hospital where he was declared deceased. The event is Significant because of a fatality. | The root cause was the individual failed to hook-up himself prior to his movement while he was wearing a full body harness. The contributing causes were the area where the individual was taking his break was a non-work area with no fall protection system installed. In addition, there were no physical barriers or signs to prevent access to the ladder without fall protection provided. |  | 1 - For information only, contractor, fall, fall protection, fatality, industrial safety | IS.1

## Noteworthy
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 17-0046 | 2017-01-20 | 2017-01-31 06:14 | Takahama-2 | #PRELIMINARY# Damage of crane boom at Takahama Nuclear Power Station | Noteworthy | During long term shutdown, the boom of a large crane fell on the reactor auxiliary building and fuelling handling building, resulting in partial deformation of the roofs of those buildings. This event was Noteworthy due to damage to the fuelling building roof that caused large equipment falling, posing a risk of fuels damage. | The event occurred after heavy winds was alerted. | SOER 2002-1 Rec 1 | 2 - Important lessons, fuel storage, lifting device | IS.1
WER TYO 17-0042 | 2016-09-28 | 2017-01-30 01:35 | Shika-2 | Inflow of rainwater into the reactor building | Noteworthy | With the plant in shutdown state, a total of 6.6m3 of rainwater entered into the emergency electric equipment room and other areas including controlled areas of reactor building. It led to a temporary actuation of an alarm indicating a short circuit in the normal and emergency lightening power distribution panels. This event is Noteworthy because of potential safety impact due to flooding. | The direct causes were a gap between the pit and the upper lid,the capacity of the temporary drainage pump was insufficient and water tight sealing not applied to the reactor building penetrations. Operators did not directly confirm the status of the trench in taking actions to respond to the alarm. Several organisational weaknesses were also identified. | SOER 2002-1 Rec 1 SER 2016-2 | 2 - Important lessons, drain, flood, seal, water intrusion | CM.1 , EN.1 , OP.1
WER PAR 17-0026 | 2016-02-17 | 2017-01-19 04:07 | Bugey-2 | Breach of seismic qualification requirements on the essential service water system | Noteworthy | During normal operation, leaks were identified in the concrete penetration between the pump house and the essential service water (ESW) tunnel and the place around pipe support structures. The event is Noteworthy because a maximum credible earthquake could result in total loss of the ESW system, making it impossible to take the unit into shutdown conditions on residual heat removal. | The cause was the design issues that the specific nature of the single piping section inside the tunnel makes maintenance operations complicated and there was no reliable non-destructive testing method. |  | 1 - For information only, corrosion, design criteria / design basis, essential service water, inspection, pipe, seismic event | CM.1 , ER.2
WER PAR 17-0021 | 2016-08-18 | 2017-01-31 04:26 | Ningde-2 | #PRELIMINARY# REPEATED DIESEL GENERATOR FAILURES DUE TO RELAY ISSUES | Noteworthy | During normal operation and while performing an emergency diesel generator (EDG) low power test, the EDG failed to start due to relays failure and was declared inoperable. EDGs at two other stations had also failed due to the same issue. The event is Noteworthy due to potential for common mode failure of EDGs at three stations. | The cause was failure of certain EDG systems relays (instantaneous relays, bistable relays and time-delay relays) supplied by same manufacturer. The root cause is under investigation. | SOER 2002-2 Rec 1 | 2 - Important lessons, common mode failure, diesel generator, relay, technical specification, time delay relay, vendor | ER.1 , ER.3
WER PAR 17-0003 | 2016-12-29 | 2017-01-16 07:13 | Lingao-2 | Cooling of Spent Fuel Pool not Meeting Requirement of Technical Specifications during a Test | Noteworthy | During an outage with all fuel assemblies in the spent fuel pool (SFP) and while performing a startup of the component cooling system (CCS) train A, a miscommunication between operation staff left two manual isolation valves in closed position. As a consequence, cooling of the SFP had been lost for one hour and 18 minutes. Water temperature in the SFP increased from 42.2℃ to 45.1℃. This event is Noteworthy due to loss of spent fuel pool cooling during outage. | The direct cause was a human error due to ineffective communication. The apparent cause was status of the CCS was not adequately controlled during outage. Contributing factor was la ack of operator's attention to the CCS pump flow and abnormal increase of water temperature in the SFP. | SOER 2010-1 Rec.6 | 1 - For information only, component cooling water, configuration control, cooling pond, technical specification | CM.2 , OP.1
WER MOW 17-0019 | 2017-01-27 | 2017-01-31 06:05 | Leningrad 2-1 | #PRELIMINARY# A Group Accident During Operations to Adjust Reactor Coolant Pump Motor Cubicles | Noteworthy | During commissioning stage and while adjusting a reactor coolant pump (RCP) motor cubicles and testing 10 kV RCP motors, two workers suffered an electric shock. The workers received burns to the head, body and arms as a result of arcing and were taken to the hospital. The event is Noteworthy because of severe injury to two workers. | The cause is under investigation. | SER 2002-4 | 1 - For information only, arc strike, burn, industrial safety, injury, short circuit | IS.1
WER MOW 17-0008 | 2016-09-07 | 2017-01-18 04:08 | Temelin-2 | Turbine Shutdown Due to High Vibrations | Noteworthy | During startup at 80% electrical power, the turbine generator was required to be manually tripped due to high vibrations. After a 37-day outage for repairs, the turbine was manually tripped again twice in 5 days for the same reason. This event is Noteworthy due to the substantial operational impact of the turbine vibration issues and potential for turbine damage. | The direct cause was contact between the rotor and the oil inserts causing local thermal deformations in the rotor. The root cause was that inappropriate technical data were provided by the manufacturer of the bearing to the manufacturer of the turbine. The issue started during a low pressure turbine renovation in 2015 and was not solved sufficiently during multiple shutdown repairs as well as a design modification during the extraordinary outage in 2016. | SER 2005-3 | 1 - For information only, modification, power reduction, troubleshooting, turbine generator, turbine trip, vendor, vibration | CM.3 , PI.2 , PM.1
WER ATL 17-0081 | 2016-09-29 21:00 | 2017-01-20 12:40 | Arkansas-1 | Unisolable Leak on Decay Heat Removal Piping due to Failed Socket Weld | Noteworthy | During a refuelling outage with fuel in the core and both trains of decay heat removal system in operation, a 0.125 gallon per minute un-isolable leak was identified in the decay heat system due to a cracked weld on a one inch common drain pipe. The event is Noteworthy because it resulted in inoperability of both trains of the decay heat removal system. | The direct cause was fatigue cracking of the socket weld due to vibration. The other causes were inadequate design of the drain pipe and insufficient corrective actions for previous socket weld cracks. The contributing causes include inadequate operating procedure and inadequate operators training regarding precaution to limit decay heat system flow. | SOER 2010-1 Rec 3 | 1 - For information only, decay heat removal, design criteria / design basis, fatigue cracking, leak, procedure inadequacy, training, vibration, weld | ER.3 , OP.2 , PI.2
WER ATL 17-0057 | 2016-10-15 | 2017-01-13 18:44 | Shearon Harris-1 | Indications Identified on Reactor Vessel Head Penetration Nozzles During Inservice Inspection Result in Outage Delay for Repairs | Noteworthy | During an outage, non-destructive examinations of the reactor vessel head identified rejectable indications in four penetration nozzles. The event is Noteworthy because the outage was extended by approximately 10 days to carry out repairs. | The cause of indications in three nozzles was primary water stress corrosion cracking due to the susceptibility of alloy materials, high tensile operating stresses and a conducive environment. The cause for indications in the&nbsp;fourth nozzle was a previous repair weld which opened up due to conditions encountered during operating cycle. | SER 2002-3 | 1 - For information only, crack, material deficiency, nondestructive examination, nozzle, reactor vessel head, stress corrosion | ER.3 , ER.4
WER ATL 17-0034 | 2016-11-28 | 2017-01-12 13:11 | Pickering-A4 | Unavailability of a Standby Generator While Another Standby Generator Was Out Of Service Resulted In Unavailability Of The Standby Generating System | Noteworthy | During normal operation, a standby generator (SG) tripped during a test and became unavailable while another SG was also unavailable due to planned maintenance. While these two SGs were unavailable, the remaining SG was connected to the class III electrical bus which resulted in its unavailability to respond o a total loss of the electrical power. This event is noteworthy due to the complete unavailability of the standby emergency power generating system for two units,. | The direct cause was not identified. The apparent cause was that the test procedure did not adequately address the safe state for the remaining SDGs when one of the SGs is not available. |  | 1 - For information only, emergency power, procedure inadequacy, test, work control | ER.1 , OF.2 , OP.2
WER ATL 17-0019 | 2016-10-21 20:28 | 2017-01-10 07:24 | Catawba-1 | Feedwater Heater Isolation Resulted in a Secondary Transient | Noteworthy | During normal operation, a high pressure feedwater heater (FWH) normal drain started closing due to an actuator air supply failure but an operator incorrectly concluded that the drain to the condenser was failing open and therefore isolated it to maintain the FWH level. This caused high level in the FWH, resulting in the FWH isolation, decrease in feedwater temperature and consequently increase in reactor power. The unit power was reduced to 93%. The event is Noteworthy because it resulted in a reactor power excursion to 102.2%. | The cause was human error as the operators did not correctly diagnose the failure of an air operated FWH drain valve. The other cause was that the operators did not use the senior reactor operator risk recognition process. | SOER 2013-1 Rec 3 | 1 - For information only, air operated valve, feedwater heater, heater drain, human error, power ascension, power reduction, reactivity management | OF.2 , OP.1
WER ATL 17-0009 | 2016-11-21 | 2017-01-06 19:12 | Pickering-A4 | Fuel Transfer Elevator Trough failure while transferring fuel to the irradiated fuel bay resulted in 2 Fuel-in-Air events. | Noteworthy | During on-power fuelling, the fuel transfer trough failed twice, preventing the fuel from being sent to the irradiated fuel bay. The first event resulted in one pair of fuel in the air for 2-3 minutes. The second event resulted in another pair of fuel in the air for seven minutes. Since the fuel-in-air event duration was more than the allowable 150 seconds, elevator sprays were turned on to cool the fuel. The event is Noteworthy because of potential for spent fuel damage. | The cause could not be determined. Some possible common mode failures identified include failure of relays used to swap a solenoid valve to either raise or lower the elevator support, failure of the hand-switch used to drive the elevator support/fuel stop and the solenoid valve. |  | 1 - For information only, fuel handling, refuelling | FA.1

## Trending
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 17-0041 | 2016-10-10 | 2017-01-26 19:36 | Rajasthan 4 | Turbine trip on low condenser vacuum followed by manual reactor trip | Trending | During normal operation, turbine tripped on low condenser vacuum and consequently reactor setback was initiated. The reactor was manually shutdown. | The cause was clogging of condenser cooling water (CCW) screen with paint flakes dislodged from CCW tunnel walls, which resulted in drop in CCW pump performance. In addition, air from the CCW header entered the air extraction pump heat exchanger and downgraded its performance. |  | 1 - For information only, circulating water, condenser vacuum, preventive maintenance, pump, reactor shutdown, turbine trip | ER.2
WER TYO 17-0040 | 2016-09-12 | 2017-01-25 23:44 | Wolsong 1 | Manual Reactor Trip Due to Earthquakes | Trending | While Units 1- 4 were in normal operation, several earthquakes occurred in the proximity of the plant. It was identified that the threshold of 0.1g site design earthquake (SDE) seismic response spectrum was exceeded. All four units were manually shutdown to carry out detailed inspections of safety equipment. | The cause was an earthquake. |  | 1 - For information only, earthquake, reactor shutdown, seismic event | CM.1
WER TYO 17-0038 | 2016-07-28 | 2017-01-25 23:21 | Shin-Wolsong 2 | Maintenance for Leak Detected at the Pressure Seal of Safety Injection Header Check Valve (SI-237, 247) | Trending | During an outage, a leak was detected at the pressure seal of safety injection header check valve. When the reactor coolant system was heat up and pressurised after the outage, an external leak was found on the same valve bonnet. The reactor coolant system was cooled down for repairs. | The direct cause was a gap between the inner diameter of valve body and the outer diameter of the pressure seal. The root cause was lack of fabrication technique of the valve manufacturer and inadequate maintenance manual. Inadequate work supervision and management was a contributor. |  | 1 - For information only, check valve, procedure inadequacy, safety injection, seal, torque | ER.3 , MA.1 , MA.2
WER TYO 17-0037 | 2016-10-31 | 2017-01-25 23:11 | Shin-Kori 3 | Current Transformer of Main Transformer Phase A Had Electric Arc | Trending | During commissioning and while performing the power ascending test, power was reduced from 45% to 4% because of phase A ratio differential relay alarm. After an electrical arc was observed inside the control panel, the turbine generator was tripped manually. | The direct cause was that the connection of a current transformer cable inside a main transformer control panel was broken down and overheated. The root cause was damage to the cable by a worker during construction. |  | 1 - For information only, arc strike, cable, fire, human error, power reduction, transformer, turbine trip | MA.1
WER TYO 17-0036 | 2016-06-25 | 2017-01-25 20:31 | Shin-Kori 2 | Fuse Blown Due to Capacitor Failure in the CEDM Control System | Trending | During normal operation, twenty-two status lights for the control rod drive mechanism (CRDM) control system went out and an alarm indicating the system as inoperable. | The cause was control power a blown fuse due to the failure of a capacitor on the circuit board. The short circuit caused by ageing of the capacitor. The circuit board was in operation for more than 18 years. |  | 1 - For information only, ageing, capacitor, circuit board, control rod drive, fuse | ER.3
WER TYO 17-0029 | 2016-04-27 | 2017-01-19 00:42 | Fuqing 1 | The ventilation system of emergency management center runs unstable | Trending | The ventilation system of emergency management centre was found operating unstably with defects found 23 times since 2014. Two of the defects resulted in two water chilling units out of service at the same time, affecting the ventilation and heat exchange of the air conditioners. Moreover, some rooms at the centre were not habitable because of inadequate cooling supply. | The root cause was lack of skill of operation and maintenance personnel. The contributors were inadequate supply of emergency management centre materials and incomplete preventive maintenance projects.   |  | 1 - For information only, chiller, heating ventilating and air conditioning, preventive maintenance, training | EP.2 , ER.2
WER TYO 17-0028 | 2016-09-28 | 2017-01-19 00:23 | Fuqing 2 | Primary pump failure due to charging pump trip out | Trending | During normal operation and while performing a test, all three reactor coolant pumps (RCPs) tripped due to abnormal operation of a charging pump, resulting in an automatic reactor scram. | The direct cause was improper protective delay setting in the RCP logic. The root cause was deficiencies in design change and temporary modification process during conmmissioning phase. | SER 2005-3 | 1 - For information only, automatic scram, design change, human error, reactor coolant pump, reactor coolant pump seal, setpoint | CM.3
WER TYO 17-0027 | 2016-03-26 | 2017-01-18 05:12 | Chasnupp 2 | Degradation of Condenser Vacuum during Normalization of High Capacity Blowdown Flash Tank leading to Unscheduled Power Reduction | Trending | During normal operation and while normalising steam generator blowdown system (SGB) after maintenance, condenser vacuum started decreasing rapidly. This resulted in increase in nuclear power by 0.6%. The unit power was decreased to 96% to maintain nuclear power within limits. | The cause was that the SGB system venting was open to atmosphere during maintenance and accumulated air in the system was then vented towards condenser, resulting in vacuum degradation. This was due to a procedure deficiency. Another contributing factor was that the plant was already operating with slightly degraded heat transfer capability of the condenser. |  | 1 - For information only, blowdown, condenser vacuum, power reduction, power surge, procedure inadequacy | ER.1 , OP.2
WER TYO 17-0023 | 2016-10-02 | 2017-01-17 23:28 | Fuqing 2 | Row-B shutdown breakers open result in control rods dropping | Trending | During cold shutdown, the reactor emergency shutdown enabling signal was triggered, resulting in all the control rods being dropped into the bottom of the reactor. | The direct cause was fluctuation of measured values of steam generator level instrument and two-loop steam flow instrument, producing steam-water mismatch signals to cause reactor scram. The root cause was inadequate design. |  | 1 - For information only, automatic scram, control rod, design criteria / design basis, instrumentation | CM.1 , ER.1
WER TYO 17-0022 | 2016-10-18 | 2017-01-17 21:36 | Changjiang 2 | Differential pressure high of drum nets of the circulating water filtering system caused circulating water pump trip and reactor trip | Trending | While operating at 25% power during a typhoon, debris deposited on the seabed was brought by the heavy storm into the water intake, resulting in the drum net pressure increase. The circulating water pumps tripped followed by deterioration of condenser vacuum, leading to an automatic reactor scram. | The root cause was inadequate design of the water intake that has poor wave eliminating capability. The contributors were back flushing channel clogged, outer open channel not cleared, insufficient monitoring ability of drum net differential pressure trend and inadequate operating procedures. | SOER 2007-2 Rec 3, 4, 5 | 1 - For information only, automatic scram, circulating water, condenser vacuum, debris / crud, intake, preventive maintenance, pump, storm | CM.1 , ER.2 , OP.2
WER TYO 17-0021 | 2016-08-26 | 2017-01-17 21:05 | Changjiang 2 | A-row circulating water pump (2CRF001PO) tripped | Trending | During normal operation, a circulating water pump tripped. This resulted in lowering of condenser vacuum and increase in nuclear power. The unit power was reduced to 54%. | The direct cause was actuation of the reverse rotation signal. The root causes include inadequate design of circulating water pump tripping logic, tripping of drawer protection due to instant earthing, too low gearbox heater insulation and incorrect operation due to fault of drawer circuit breaker. The contributing cause was high humidity in equipment operating environment. |  | 1 - For information only, breaker, circulating water, condenser vacuum, design criteria / design basis, insulation, power reduction, power surge, pump | CM.1 , ER.1
WER TYO 17-0019 | 2016-07-08 | 2017-01-17 00:02 | Changjiang 2 | Fierce pipeline vibration resulting in unit trip | Trending | During normal operation in commissioning stage, excessive vibration of main pipeline from steam and water separator drain tank to high pressure drain expander caused breaking of a small sampling pipe on the main pipe. This resulted in leakage of water, requiring reactor shutdown for repairs. | The direct cause was that sampling pipe valve being too near the main pipe, mass of sampling pipe and valve was concentrated and sensitive to main pipe vibration. The root causes were water hammer due to large differential pressure across the drain valve, inadequate operating experience use and frequent operation of drain control valve due to fluctuation of drain tank water level. |  | 1 - For information only, control valve, design criteria / design basis, installation, leak, pipe, reactor shutdown, vibration, water hammer | CM.1 , OE.1
WER TYO 17-0016 | 2016-05-24 | 2017-01-16 19:36 | Shika 2 | Possibility of a guard’s exposure to very low dose radiation | Trending | During an outage, a guard inadvertently entered into the prohibited entry area which was set for the purpose of radiographic inspection. There was a potential of unplanned overexposure. | The cause was procedure violation due to human errors. | SOER 2001-1 Rec 5, 8 | 1 - For information only, human error, procedure adherence, radiation area, radiograph | RS.1
WER TYO 17-0015 | 2016-05-18 | 2017-01-15 23:50 | Changjiang 2 | Implementation of intermediate range 2RPN023MA periodic test led to artificial introduction of Group 1 events | Trending | During intermediate shutdown in commissioning stage, the intermediate range neutron flux measuring channel periodic test was performed. This resulted in entry into a limiting condition of operation as an intermediate range measuring channel was artificially made unavailable, which increased the risk of wrong operation of protection at high intermediate range neutron flux signal. | The direct cause was that the periodic test was performed in the intermediate shutdown status instead of power operation status. The root causes include insufficient knowledge of operation technical specification, insufficient management expectation and inadequate procedure for the periodic tests. |  | 1 - For information only, human error, limiting condition of operation, procedure inadequacy, test, work control | MA.2 , OP.1 , WM.1
WER TYO 17-0011 | 2016-04-11 | 2017-01-12 02:21 | Fuqing 3 | Large amounts of safety valves are out of valid period after TOM (turnover for maintenance) of Unit 3 | Trending | During commissioning, it was found that 91 safety valves were already/nearly out of valid period, which might cause the valve to lose its over-pressure protective function. The calibration of large number of safety valves after fuel loading affected plant startup schedule. | The direct cause was that calibration of safety valves was not performed in time. The root cause was that standard was not defined for safety valve examination in turnover for maintenance (TOM) package. The contributors were lack of procedure adherence and insufficient capability of TOM package review personnel. |  | 1 - For information only, calibration, documentation, human error, procedure adherence, procedure inadequacy, safety relief valve, work control | MA.1 , MA.2 , WM.1
WER TYO 17-0010 | 2016-10-20 | 2017-01-11 21:30 | Qinshan 3 1 | Manual Shutdown Caused by High Tritium Concentration Exceeding the Pre-set Shutdown Threshold Value | Trending | During normal operation, the tritium concentration in an area of the reactor building exceeded the pre-set shutdown threshold value. The reactor was manually shut down for approximately 8 days to address the issue. | The cause was a leak on an adaptor at the branch pipe joint which connected the main pipe and the general activity level monitoring system's sampling pipeline. The possible root cause was cracks due to stress corrosion. |  | 1 - For information only, crack, leak, reactor shutdown, stress corrosion, tritium | ER.1
WER TYO 17-0008 | 2016-08-14 | 2017-01-11 03:31 | Qinshan 3 1 | Water leakage of main feed water pump shaft seal leads to unit power reduction | Trending | During normal operation, high vibration, steam and water leaks were identified on a main feed water pump. The power was reduced to 90% for the repairs. | The direct cause was the loose fastening bolts on the mechanical seal driving sleeve. The root cause was missing requirement on inspection of the bolts fastening steps and sequence in the maintenance procedure. |  | 1 - For information only, bolt, feedwater pump, installation, leak, o-ring , power reduction, procedure inadequacy, seal, steam, vibration | MA.2
WER TYO 17-0007 | 2016-09-15 | 2017-01-11 03:03 | Qinshan 3 1 | The common transformer tripped led to reactor shutdown | Trending | During normal operation, short circuit of a transformer at common section bus led to tripping of a liquid zone control system pump. The reactor power automatically stepped back to 70%.&nbsp;The local air cooling fan in the reactor building also tripped, resulting in increase in temperature of a reactor room to above 65 degree C. The reactor was shut down. | The direct cause was water intrusion in the common section box enclosure due to heavy rainfall. The root cause was inadequate design of the protection devices including relay for the local air cooling fan. The contributing cause was inadequate inspection and maintenance of the common bus box enclosure. |  | 1 - For information only, liquid zone control , preventive maintenance, pump, reactor shutdown, short circuit, storm, transformer, water intrusion | CM.1 , ER.2 , ER.3 , MA.1
WER TYO 17-0002 | 2016-10-18 | 2017-01-09 19:27 | Qinshan 2 3 | Oil leakage due to vent plug loose | Trending | During normal operation and while venting the pre-lubrication pump of an emergency diesel generator (EDG), the plug at the venting position was found loose, causing lube oil leakage. As a consequence, the EDG was declared unavailable. | The cause was inadequate design of the plug. |  | 1 - For information only, design criteria / design basis, diesel generator, leak, lube oil, plug | ER.3
WER PAR 17-0049 | 2015-11-07 | 2017-01-31 10:44 | Hunterston B 2 | Generator Transformer Unexpected Alarms | Trending | During normal operation, an unauthorised work was started on a live alarm panel of the turbine generator without any work order card or associated safety document. This resulted in an unexpected alarm in the control room. There was a potential for electric shock and personnel injury. | The direct cause was deliberate act to work on the turbine generator alarm panel without the appropriate planning, authorisation or associated control measures. The apparent causes were inadequate communication, inadequate pre job brief and not enforcing standards and expectations. |  | 1 - For information only, human error, industrial safety, prejob brief, work control | IS.1 , NP.1 , WM.1
WER PAR 17-0046 | 2016-06-09 | 2017-01-30 10:33 | Bugey 2 | Leak from Steam Generator level Sensor resulted in unplanned entry to group-1 LCOs | Trending | During an outage, a narrow-range steam generator level sensor malfunction was identified. The next day during a walkdown, a leak was identified and, when repaired, the level sensor returned within the range since the malfunction was related to the leak. As a result, a number of limiting conditions of operations were applied. | The direct cause of the leak was the vent bolts of the main steam flow sensor not torqued to the required value. The cause of failing to identify the narrow-range steam generator level sensor malfunction was operators deficiencies in decision making, alarm response, troubleshooting, procedure adherence and pre-job briefing. | SOER 2013-1 Rec 3 | 1 - For information only, bolt, human error, leak, limiting condition of operation, prejob brief, procedure adherence, reactor protection system, sensor, torque, troubleshooting | MA.1 , NP.1 , OP.1
WER PAR 17-0045 | 2016-06-06 | 2017-01-30 10:02 | Bugey 3 | Safety Injection Check Valve Closing Failure | Trending | During hot shutdown mode and while performing leak testing of safety injection check valves, one valve was found inoperable. The valve was blocked open and entry into a limiting condition of operation was made. | The cause was obstruction of the flow limiter located on the valve air supply due to excessive use of sealing paste during replacement of the solenoid valve in 2015. The worker did not adhere to the work procedure. |  | 1 - For information only, blockage, check valve, contractor, human error, limiting condition of operation, procedure adherence, safety injection, seal, solenoid valve | MA.1
WER PAR 17-0043 | 2016-05-17 | 2017-01-30 07:42 | Bugey 3 | Late detection of significant change in dose rate inside an orange area due to the formation of a hot spot | Trending | During decontamination of a spent fuel pool transfer compartment with a high-pressure cleaner in a walkway, a hot spot occurred on a drainage line. Five days later, a worker entered the area and his dose-rate alarm initiated. The area was declared red area. There was a potential for unplanned radiation exposure. | The cause was inadequate review of the work package and inadequate communication between radiation protection and maintenance departments. | SOER 2001-1 Rec 8 | 1 - For information only, contractor, radiation area, radiation dose, radiation protection, work control | RP.2 , RS.1 , WM.1
WER PAR 17-0042 | 2016-06-02 | 2017-01-30 04:58 | Bugey 3 | Unit shutdown Due to Unavailability of the Chemical and Volume Control discharging function | Trending | During normal operation, inadvertent closing of a valve on the chemical and volume Control system caused the discharging line to become unavailable. The reactor was shut down for 38 hours to address the issue. | The cause was that the diaphragm on the valve was torn due to assembly deficiencies. |  | 1 - For information only, air operated valve, chemical volume control system, diaphragm, installation, limiting condition of operation, reactor shutdown, valve | MA.1
WER PAR 17-0041 | 2016-06-03 | 2017-01-30 04:35 | Cattenom 1 | Unavailability of safety injection (RIS) valves in maintenance outage and refuelling outage modes | Trending | During an outage and while performing cleaning and inspection of protection control and safety action cabinets, a 48V power supply to the cabinets was cut-off when the unit was in refuelling outage mode. This resulted in unavailability of two safety injection valves and entry into two limiting conditions of operation related to a safety injection and containment spray system train. | The cause was lack of understanding of the interaction of protection cabinets 48 V power supply with the safety injection valves. The tagging procedures did not include recommendations from operating experience of another station to carry out work on these cabinets only in defueled mode. | SOER 1998-1 Rec 1 | 2 - Important lessons, containment spray, human error, limiting condition of operation, operating experience, power supply, procedure inadequacy, safety injection, tagging | CM.2 , OE.1 , OP.2
WER PAR 17-0040 | 2016-09-20 | 2017-01-26 10:56 | Hongyanhe 3 | Need for Main Feedwater Flow Measurement Correction Identified | Trending | During normal operation and while performing main feedwater flow measurement, four out of six measurements were found higher than the acceptable values. Main feedwater measurements were declared unavailable and a limiting condition of operation (LCO) was entered. | The cause was the venturi tubes were gradually worn due to erosion. |  | 1 - For information only, erosion/corrosion, feedwater, limiting condition of operation | ER.3
WER PAR 17-0039 | 2016-08-26 | 2017-01-26 08:33 | Hongyanhe 2 | Failures of Automatic start tests on Nuclear component cooling pump | Trending | During normal operation and while performing auto start test of a nuclear component cooling pump, the pump failed to start due to a design deficiency. It was the first time that the test was performed with unit in operation and similar problem may occur on other units and stations with similar design if tested in operation. | The cause was unexpected reset of the pressure switch due to inadequate design. When a low pressure signal was simulated, inter-train isolation valves opened before the start of auto pump and pressurised back-up train which reset the pressure switch, preventing start of the pump. |  | 2 - Important lessons, common mode failure, component cooling water, design criteria / design basis, pressure switch, pump | CM.1
WER PAR 17-0038 | 2016-08-13 | 2017-01-25 09:08 | Ningde 1 | Compromised Fire Fighting Functions Due to Construction and design Defficiencies | Trending | During a multiple units joint fire-fighting systems (FFSs) inspection, it was found that spray nozzles on some fire-fighting systems were not fitted in line with national design codes. This potentially impact the operability of the FFSs for electrical buildings, emergency diesel generator buildings and the nuclear islands. In a separate event, a deluge valve of the main transformer FFS were identified not activated as expected during a test. | The cause of nozzles installation deficiencies was that the construction company did not follow the national standards. A contributing cause was operating company personnel were not aware of detailed national requirements while taking over the systems. The cause of the deluge valve malfunction was low voltage of a solenoid valve due to design deficiency. The same failure occurred previously. |  | 2 - Important lessons, deluge valve, fire protection, fire suppression, installation, solenoid valve | FP.1 , PI.2
WER PAR 17-0036 | 2016-07-07 | 2017-01-24 06:56 | Tihange 2 | Turbine control fluid leak | Trending | During normal operation, a non-isolable leak on the turbine control fluid system (CFR) forced a turbine trip. As a consequence, the reactor power was reduced to 15% and it resulted in a loss of generation of 1.7 days. | The direct cause was a leak on the output side of the high-pressure CFR pumps due to an excessively thick O-ring. The O-ring was with wrong size due to inadequate work practice. |  | 1 - For information only, hydraulic fluid, leak, o-ring , power reduction, seal, turbine trip | MA.1
WER PAR 17-0035 | 2016-07-09 | 2017-01-24 06:33 | Golfech 1 | Automatic reactor scram during turbine trip for scheduled shutdown | Trending | While reducing power to shut down the reactor, the turbine power could not be reduced below 12% and therefore the turbine was manually tripped. The turbine generator output breaker opened as designed but at the same time main off-site grid supply breaker also opened unexpectedly. This resulted in automatic reactor scram on turbine trip, power greater than 10% and loss of offsite power signals. | The apparent cause was inability to reduce turbine power due to turbine governing system failure. The other cause was failure of the main offsite power breaker due to vibrations caused by opening of the turbine generator breaker as the two breakers were close to each other. The contributor was inadequate corrective actions after similar breaker failures in the past. |  | 2 - Important lessons, automatic scram, breaker, loss of offsite power, turbine trip, vibration | CM.1 , ER.1 , PI.2
WER PAR 17-0034 | 2016-11-08 | 2017-01-20 09:53 | Forsmark 3 | Reactor scram due to short neutron flux doubling time with a reactor power less than 10% during startup | Trending | During startup and while performing control rod drives test, the reactor automatically scrammed on intermediate range detector high neutron flux rate . | The direct cause was that the lineup for the pressure relief system was not verified due to inadequate planning of the resources. The test procedure was inadequate without the latest operating experience. |  | 1 - For information only, automatic scram, configuration control, control rod drive, human error, procedure inadequacy | OP.1 , OP.2 , WM.1
WER PAR 17-0033 | 2016-08-13 | 2017-01-20 09:30 | Tihange 1 | Reactor emergency shutdown and turbine trip due to very high steam generator level | Trending | While restarting and at 11% power with one turbine generator connected to the grid, an emergency shutdown took place following trip of both turbines as a result of very high level in a steam generator. | The cause was high level in a steam generator due to failure of feedwater pumps speed control when it was switched to delta pressure (DP) setting. The DP setting of the speed control did not change to automatic and remained stuck in manual mode due to a faulty electronic card. The root cause is under investigation. |  | 1 - For information only, automatic scram, circuit card, feedwater control system, feedwater pump, speed control, steam generator / boiler, turbine trip | ER.1
WER PAR 17-0032 | 2016-08-17 | 2017-01-20 07:47 | Cofrentes 1 | Simultaneous opening of circuit breaker of two residual heat removal pumps | Trending | During normal operation and while performing maintenance, the control voltage was removed from the power supply circuit breaker of residual heat removal (RHR) pump C instead of RHR pump B. Subsequently, the control power was removed from the power supply circuit breaker of RHR pump B without confirming the restoration of the control power of RHR pump C, causing the simultaneous opening of the circuit breakers of two residual heat removal pumps. | The direct cause was the opening of the circuit breakers providing control power to RHR pump B without checking RHR pump C due to two separate human errors. The root cause was dificiencies in self checking, alignment verification, prejob brief, communication and inadequate work permission. |  | 1 - For information only, circuit breaker, human error, misposition, power supply, prejob brief, residual heat removal pump, work control | MA.1 , WM.1
WER PAR 17-0031 | 2016-09-14 | 2017-01-20 06:01 | Atucha 2 | Reactor trip due to moderator pump low flow signal. | Trending | During normal operation, a 500 kV line reclosed after disconnection but voltage did not completely recover in the bus bars feeding moderator pumps. This resulted in tripping of the moderator pumps and consequently an automatic reactor scram on moderator pump low flow signal. | The cause was an unstable 500kV grid. The other cause was an inadequate interlock in the reactor protection system, which produced reactor scram during momentary stop of the moderator pumps for one second. | SOER 1999-1 Rec 1 | 1 - For information only, automatic scram, design criteria / design basis, grid, interlock, moderator, pump, transmission line | CM.1
WER PAR 17-0030 | 2016-10-08 | 2017-01-20 05:23 | Ringhals 1 | Reactor scram due to power increase on average power range monitor (APRM) channels | Trending | During normal operation, one of the two turbines tripped due to high vibration. Subsequently, the late opening of the dump valves on the turbine caused a reduction of the void in the core. The reactor automatically scrammed due to power increase on average power range monitor channels. | The direct cause of the turbine trip was that two redundant computer processors that monitors turbine vibration failed with unidentified reason. The cause for the late dump valve opening was a delay in a relay that controls the rapid opening of the dump valve, and a slightly lower pressure in one of four storage tanks to the dump valves. A contributing factor was the low pressure in the tank to dump valve was documented inadequately. |  | 1 - For information only, automatic scram, computer, digital control system / digital components, power surge, relay, steam dump valve, turbine trip, vibration | ER.1 , ER.3 , OP.1
WER PAR 17-0029 | 2016-07-07 | 2017-01-19 09:14 | Hongyanhe 1 | Partially clamped Fuse identified in a Voltage Transformer | Trending | During normal operation, a partially clamped fuse associated with generator output potential transformer phase C was identified. The unit was manually shutdown to correct the problem. | The cause was inadequate alignment of moving and fixed contacts of the potential transformer (PT) when the PT cabinet was racked in last time. |  | 1 - For information only, design criteria / design basis, fuse, human error, reactor shutdown, transformer | ER.3 , MA.1
WER PAR 17-0028 | 2016-12-01 | 2017-01-19 07:16 | Almaraz 1 | Load reduction due to failure of the moisture separator reheater A reheat stop valve to open during a surveillance test | Trending | During normal operation and while performing a turbine valves test, a moisture separator reheater reheat stop valve failed to open. The valve could not be open when the power was reduced to 90%. A further power reduction to 60% was initiated but stopped at 86%. | The cause was the test solenoid valve could not return to its initial position, resulting in the turbine control electrohydraulic fluid continuing to drain instead of being directed to the hydraulic actuator. |  | 1 - For information only, hydraulic fluid, moisture separator reheater, power reduction, solenoid valve, turbine control | ER.1 , PI.2
WER PAR 17-0024 | 2016-05-31 | 2017-01-18 09:15 | Ningde 2 | Reactor thermal power exceeded limited level of 2905MW | Trending | While Unit 2 in full power operation and Unit 1 in startup, thermal de-gassing of Unit 1 deaerator required steam from Unit 2. Unit 2 reactor thermal power exceeded limited value (2905MW) two times with a peak value of 5 MW due to fast opening of Unit 1 steam valve. | The cause was missing procedural requirement of power reduction during de-gas operation and insufficient risk analysis prior to work. A contributor was the operators had assumed that power rise would be below the limit. |  | 1 - For information only, human error, power surge, procedure inadequacy, reactivity management, valve | OP.1 , OP.2
WER PAR 17-0023 | 2016-05-10 | 2017-01-15 07:03 | Cruas 3 | Functional loss of a safety-injection pump due to a faulty spare part | Trending | During normal operation and while a safety-injection pump was actuated to fill safety injection accumulator tanks, the pump's dual piston failed to move. The pump was reported unavailable, resulting in entry into a limiting condition of operation. | The cause was broken bolt inside a distribution block installed during the pump's overhaul. The bolt was already inside distribution block when it was delivered to the site. There were shortfalls in the vendor's quality assurance process and inspection of spare parts. |  | 1 - For information only, bolt, foreign material, limiting condition of operation, procurement, safety injection pump, spare part, vendor | ER.3
WER PAR 17-0019 | 2016-07-31 | 2017-01-11 05:33 | Hinkley Point B1 | Reactor 3 manually shut down following rapid loss of condenser vacuum | Trending | During normal operation, failure of a liquid ring pump (LRP) on the vacuum maintaining unit caused the condenser vacuum to rapidly deteriorate. The reactor was manually shut down as the backup LRP could not be started in time. The event resulted in a seven-day outage. | The cause was failure of the pump impeller due to high cycle fatigue caused either by a resonant response of the affected impeller vane or an alternating stress due to design deficiency. |  | 1 - For information only, condenser vacuum, fatigue cracking, impeller, pump, reactor shutdown | ER.3
WER PAR 17-0014 | 2016-08-14 | 2017-01-06 06:03 | Hongyanhe 3 | Power Reduction due to Abnormal Closuse of a low pressure bled steam valve | Trending | During normal operation, a low instrument air supply pressure signal resulted in automatic closure of a low pressure bled steam valve and in two low pressure feedwater heaters isolation. This led to thermal power fluctuation and execution of transient control guideline to reduce power to 94%. | The cause was that a compressed air pressure switch setting point drift led to abnormal closing of a bled steam extraction valve. |  | 1 - For information only, feedwater heater, power reduction, power surge, pressure switch, setpoint drift, valve | ER.3
WER PAR 17-0011 | 2016-09-12 | 2017-01-05 09:09 | Hongyanhe 3 | Thermal Power Exceeding 2905MW for a Short Period when withdrawing control Rods during Power Increase | Trending | While increasing power after a grid test and operating at 99.9% power, the temperature adjustment control rods (rods R) were manually withdrawn by two steps at a time to control delta I. This resulted in increase in thermal power to 100.516%, exceeding the technical specification limit of 100.5% for about two minutes. | The root cause was misunderstanding about the thermal power limit specified in the technical specification. The power increase strategy was not adjusted in time and operators concentrated too much on monitoring and control of delta I, weakening emphasis on thermal power. The other cause was that lifting of rod R was not reported to the shift supervisor, losing one important barrier. | SOER 2007-1 Rec 2 and 4, SOER 2013-1 Rec 3 | 1 - For information only, human error, power ascension, reactivity management, technical specification | OP.1
WER PAR 17-0010 | 2016-09-18 | 2017-01-05 08:21 | Hongyanhe 3 | Feed water pump shutdown due to high shaft displacement | Trending | During normal operation, one operating feedwater pump experienced horizontal and vertical shaft displacement and the vibration value rose quickly approaching the trip value. The power was reduced to about 86% for the repairs. | The cause was a crack on the pump shaft due to manufacturing defects. |  | 1 - For information only, crack, feedwater pump, impeller, power reduction, pump shaft, vendor, vibration | ER.3
WER PAR 17-0009 | 2016-09-19 | 2017-01-05 07:45 | Ningde 1 | Delayed Detection of faulty γ dose rate monitors in Main Control Room Ventilation system | Trending | During normal operation, it was found that that the comparisons for two gamma dose rate monitors for main control room (MCR) ventilation system had not been evaluated properly between 2014 and 2015, leading to violation of surveillance requirements and delayed detection of a faulty dose rate meter. It affected accuracy of metering gamma dose rate in air of MCR ventilation system. | The cause was human error. The other cause was failure of a gamma dose rate meter due to moisture ingress caused by degraded sealing. The contributing causes were lack of supervision due to inadequate procedure, lack of procedure use and adherence and not tracking the historic database of dose rate meter periodic tests. |  | 1 - For information only, control room, heating ventilating and air conditioning, procedure adherence, procedure inadequacy, radiation monitor | ER.1 , MA.1 , MA.2
WER PAR 17-0007 | 2016-10-03 | 2017-01-04 09:49 | Lingao 2 | Inadvertent isolation valve closure for Pressurizer Level Measurement | Trending | During a refuelling outage, an isolation valve at bottom of the pressurizer level measurement was closed by mistake. The pressurizer level measurement was declared inoperable, violating relevant requirement of the technical specifications. | The direct cause was installation of wrong labels on the isolation valves. The root cause was inadequate management of use of labeling/identifications in the plant.  |  | 1 - For information only, configuration control, human error, isolation valve, label, management oversight, pressuriser level, technical specification | CM.2 , OP.2
WER PAR 17-0006 | 2016-10-22 | 2017-01-04 09:23 | Daya Bay 1 | Failure to restore high neutron flux alarm when a work was complete | Trending | During an outage and while inserting the shutdown rod group, the high neutron flux alarm circuit was found left blocked after a previous alarm value adjustment, causing violation of technical specification. | The cause was human error due to lack of procedure adherence. The contributors were deficiencies in work control, identifying key works and periodic panel inspections. |  | 1 - For information only, human error, nuclear instrumentation, procedure adherence, technical specification, work control | MA.1 , OP.1 , WM.1
WER PAR 17-0005 | 2016-11-21 | 2017-01-04 08:34 | Hongyanhe 2 | Inadvertant deactivation of Reactor Trip High Flux Alarm | Trending | During a refuelling outage and while isolating a reactor trip high flux alarm as required by fuel unloading plan, another source range detector alarm was blocked for about three minutes by mistake. This led to violation of operation technical specification. | The direct cause was human error due to ineffective communication between operator and isolation personnel. |  | 1 - For information only, alarm, configuration control, human error, source range monitor, technical specification | CM.2 , MA.1 , OP.1
WER PAR 17-0004 | 2016-12-29 | 2017-01-16 07:21 | Lingao 1 | Diesel Leakage Resulting in Emergency Diesel Generator inoperable | Trending | During normal operation and while performing an emergency diesel generator (EDG) test, oil leak was identified at a joint of oil return pipe. As a result, the EDG was declared inoperable for 24 minutes and a limiting condition of operation was entered. | The direct cause was insufficient tightening torque at the joint. The root cause was no requirement on tightening torque. Contributing cause was inadequate corrective measures for previous failures and failing to identify the defect during previous maintenance. |  | 1 - For information only, diesel generator, leak, limiting condition of operation, oil, pipe, procedure inadequacy, torque | MA.2 , PI.2
WER PAR 17-0001 | 2016-12-30 | 2017-01-16 07:03 | Lingao 3 | Accidental Diffusion of Radioactive Iodine during a Iodine Trap Efficiency Test | Trending | During normal operation, iodine trap efficiency test was performed in the security building. Ten minutes after iodine source was injected to the system, the radioactive iodine detector on site alarmed. An evacuation of the test staff from the building was required. The radioactive iodine detector hit a peak at 3500Bq/m3, and then dropped to 1700Bq/m3 quickly. The radioactive iodine accidentally diffused to 0-meter rooms of the building, fortunately no internal or external contamination was detected. | The direct cause was the iodine source injection point was not chosen based on the blower operating mode. Root cause was the test procedure was defective in that an important precondition of the test was not specified. Contributing factors were inadequate pre-job brief, ineffective supervision, insufficient coordination before the test and lack of signs on site. |  | 1 - For information only, human error, iodine, management oversight, prejob brief, procedure inadequacy, radioactive contamination | RS.1 , WM.1
WER MOW 17-0020 | 2017-01-28 | 2017-01-31 13:23 | Armenia-2 | One of the Two Running Turbine Generators ShedLoad to the Non-Vital Load Level | Trending | With unit at 92 % power, the 220 kV busbar differential protection actuated and one of two running turbine generators shed load to the non-vital load. The reactor power was reduced to 57%. Full power was restored after two hours. | The direct cause was grid related electrical component failures. |  | 1 - For information only, grid, power reduction | ER.1
WER MOW 17-0018 | 2017-01-23 | 2017-01-31 04:34 | Armenia-2 | Armenia Unit 1 Lost Power Due to 110 kV Switchyard Protection Actuations and Trip of Generator No.3 | Trending | With unit 1 in long-term shutdown and unit 2 at 92 % power, a 110 kV switchyard protection actuation led to loss of power to 110 kV busbar system in unit 1, trip of one of two running turbine generators and load reduction to 16% in unit 2. After the loss of the main transformer, two diesel generators started and powered the safety related busses. The reactor power was further reduced to around 5 % for transient prevention. Full power was restored after about seven hours. | The direct cause was electrical equipment failure. The root cause was external grid. | SOER 1999-1 Rec 1 | 1 - For information only, grid, loss of offsite power, power reduction, turbine trip | ER.1
WER MOW 17-0017 | 2016-12-08 | 2017-01-30 05:00 | Zaporozhye-4 | A Leaky Bellows Identified on the Main Valve Associated with Pilot Operated Safety Valve 4TX80S03 | Trending | During normal operation, a steam generator pilot operated safety valve (POSV) failed due to a leak from its bellows and an increase in temperature was observed on the control line associated with the POSV. The reactor was shut down for two days to carry out repair. | The direct cause was corrosion of the bellows. The root cause was defects in bellows fabrication. |  | 1 - For information only, bellows, corrosion, leak, reactor shutdown, safety relief valve | ER.3
WER MOW 17-0016 | 2016-07-14 | 2017-01-25 02:47 | Paks-1 | Unit 1 shutdown due to the fall of the 5th CRDM group assemblies | Trending | During normal operation, 4 assemblies of the 5th control rod drive (CRDM) group fell to the lower end position and could not be lifted up. As a result, both turbine were manually tripped and the reactor was shut down. The unit was offline for about 26 hours. | The direct cause was the failure of the low frequency converters of the 5th CRDM group due to ageing and obsolescence. Another cause was a short circuit in a diode of an associated power supply unit. | SOER 2007-1 Rec 5 | 1 - For information only, ageing, control rod drive, control rod drop, diode, power supply, reactivity management, reactor shutdown, short circuit, turbine trip | ER.1 , ER.3
WER MOW 17-0015 | 2017-01-23 | 2017-01-23 10:45 | Novovoronezh 2-1 | #PRELIMINARY# Unit 1 reactor scram during the test | Trending | During normal operation and while performing a test, the reactor scrammed automatically. | The direct cause was unstable instrumentation and control indicators. The root cause is under investigation. |  | 1 - For information only, automatic scram, Instrumentation and control | ER.1
WER MOW 17-0013 | 2017-01-21 | 2017-01-21 12:06 | Novovoronezh 2-1 | #PRELIMINARY# Unit 1 reactor scram on loss of all Reactor Coolant Pumps | Trending | During operation at 72% power after startup and while performing tests, the reactor scrammed automatically on loss of all reactor coolant pumps. | The causes are being investigated. |  | 1 - For information only, automatic scram, reactor coolant pump | ER.1
WER MOW 17-0012 | 2017-01-19 | 2017-01-20 22:02 | Novovoronezh 2-1 | Turbine Generator Tripped off Line Due to a Push-Button Breaker Failure | Trending | During normal operation and while performing measurement of generator rotor circuitry insulation resistance, a main turbine generator (TG) tripped after a push-button switch was pressed. Subsequently, motor driven condensate pumps tripped due to protection actuation on a low pressure heater level after turbine stop valves closed. The reactor power reduced to 40% automatically. | The TG trip was caused by a logic-generated input from the generator rotor insulation resistance manual control circuit due to the push-button breaker failure. The loss of the condensate pumps was caused by protection actuation on the low pressure heater level due to condensate boiling caused by a steam pressure drop in the heater. The root causes were deficient design and equipment fabrication. |  | 1 - For information only, breaker, condensate pump, power reduction, turbine trip | CM.1 , ER.3
WER MOW 17-0011 | 2017-01-19 | 2017-01-19 11:50 | South Ukraine-3 | #PRELIMINARY# The Unit disconnected from the grid due to vacuum degradation. | Trending | During normal operation, the unit was disconnected from the grid due to degradation in main condenser vacuum. | The cause is under investigation. |  | 1 - For information only, condenser vacuum, turbine trip | ER.1
WER MOW 17-0010 | 2017-01-13 | 2017-01-19 11:14 | Armenia-2 | Lo-Lo Grid Voltage Caused One Out of Two Running Turbine Generators to Trip | Trending | While operating at 92% reactor power, the reactor power reduced to 55% after one of the two turbines tripped. | The generator trip was caused by a low grid voltage. | SOER 1999-1 Rec 1 | 1 - For information only, grid, power reduction, turbine trip | ER.1
WER MOW 17-0007 | 2017-01-12 | 2017-01-13 10:48 | Loviisa-2 | #PRELIMINARY# The Unit was shut down for the leak repair | Trending | During normal operation and while performing radiation surveys in containment, a leak in the pressurizer pilot valve system flange was noticed. The reactor was shut down for repair of the leaking flange. | The event is under investigation. |  | 1 - For information only, flange, leak, pressuriser relief valve, reactor shutdown | ER.1
WER MOW 17-0006 | 2017-01-08 | 2017-01-11 03:20 | Armenia-2 | #PRELIMINARY# One of the Two Turbine Generators Tripped Off Line Due to High Hydrogen Content in the Generator Cooling System. | Trending | While operating at 92%, high hydrogen content occurred on one of the two main generators cooling system. The affected turbine was tripped for repairs. | The event is under investigation. |  | 1 - For information only, hydrogen, leak, turbine trip | ER.1
WER MOW 17-0005 | 2017-01-06 | 2017-01-10 04:34 | Kalinin-3 | #PRELIMINARY# Turbine Generator No.3 Was Manually Tripped Due to a High Concentration of Dissolved Gases in the Main Transformer Oil. | Trending | While operating at 73% power, dissolved gas-in-oil analysis of a main transformer phase revealed major increase in dissolved gas concentration with the hydrogen concentration limit reached. The turbine generator was tripped and the reactor power was reduced to 7% to rectify the problem . | Investigation of the root causes is in progress. |  | 1 - For information only, gas, oil, power reduction, transformer, turbine trip | ER.1
WER MOW 17-0004 | 2017-01-07 | 2017-01-10 04:11 | Leningrad-1 | #PRELIMINARY# Insulating Sheaths of the Cables Laid on the Cable Routing Racks in the Spent Fuel Storage Facility Burned Down. | Trending | During normal operation, cables on three cable routing racks in the spent fuel storage facility started burning. The fire was extinguished by the local fire-fighting service. | The event is under investigation. |  | 1 - For information only, cable, fire, spent fuel storage | ER.1 , FP.1
WER MOW 17-0003 | 2017-01-07 | 2017-01-10 03:15 | Mochovce-1 | #PRELIMINARY# Spurious actuation of main transformer protection | Trending | During normal operation, spurious actuation of main transformer high temperature protection resulted in switching to self-consumption from 400 kV line to reserve transformer supplied from 110kV line and trip of generator breakers of both turbines. The reactor power reduced automatically and then was manually stabilised at 1.5% power. | The cause is under investigation. | SOER 2011-1 Rec 3 | 1 - For information only, reactor shutdown, single point vulnerability, transformer, turbine trip | ER.1
WER MOW 17-0002 | 2017-01-06 | 2017-01-09 03:19 | Smolensk-1 | #PRELIMINARY# Turbine Generator No.2 Was Tripped to Repair an Oil Leak Through the Auxiliary Transformer. | Trending | During normal operation, one of the two operating turbine generators was tripped to repair an oil leak on the 6kV phase C feeder breaker associated with an auxiliary transformer. | The cause is under investigation. |  | 1 - For information only, breaker, leak, oil, power reduction, turbine trip | ER.1
WER MOW 16-0271 | 2016-12-25 | 2017-01-16 06:46 | Rostov-1 | Rostov NPP Unit 1 disconnected from the grid | Trending | During normal operation, a drainage leakage was identified at the generator gas system. The unit was disconnected from the grid for the corrective maintenance and the reactor was shut down. | The direct cause was a drainage leakage at the generator gas system. Breakage of the drain was caused by vibrations and deficient installation. A similar event occurred at Unit 2 in 2012. |  | 1 - For information only, hydrogen, leak, reactor shutdown, turbine generator, vibration | MA.1 , OE.1 , PI.2
WER MOW 16-0270 | 2016-12-20 | 2017-01-12 03:29 | Kalinin-2 | Chemistry Staff Injured During Containment Transportation | Trending | When manipulating the biological shield container using a crane beam in the water treatment building, chemistry operator suffered a foot fracture and was taken to hospital for treatment. | The direct cause was a crane beam control key jamming. The operator was manipulating the equipment without appropriate authorisation. The root cause was poor work management. | SOER 2008-1 Rec 1,4 | 1 - For information only, industrial safety, injury | CY.1 , IS.1
WER MOW 16-0185 | 2016-10-01 | 2017-01-12 05:34 | Zaporozhye-1 | Diesel Generator 1 was removed from standby mode. | Trending | During normal operation, while performing emergency diesel generator test at idle speed cooling water leaks on two of the exhaust cylinders were identified. The EDG was removed from hot standby. | The cause was inadequate preventive maintenance. |  | 1 - For information only, cooling water, diesel generator, leak, preventive maintenance | ER.2 , MA.1
WER MOW 16-0128 | 2016-06-29 | 2017-01-16 02:55 | Bohunice-4 | Turbine Generator TG 41 Power Jumping led to TG41 manual trip | Trending | During normal operation, one of two turbine generators was tripped manually due to a power drop caused by turbine power controller sensor malfunction. Reactor power was reduced to 50%. | The direct cause was interruption of power circuit of bus-bar disconnector auxiliary contacts. The root cause is unknown. Cleaning of auxiliary cylinders of disconnectors are very difficult because of limited&nbsp;access to some parts of the equipment. |  | 1 - For information only, controller, power reduction, sensor, turbine generator | ER.1
WER MOW 16-0061 | 2016-04-11 | 2017-01-17 02:27 | Zaporozhye-6 | Unit 6 disconnection from the grid | Trending | During normal operation, the generator cooling system was found degraded. The reactor power was reduced to 10% and the unit was disconnected from the grid to carry out repair. | The direct cause was a heat exchanger tube leak in the area of the gas cooler tube sheet supply line. The root cause was hydrogen-induced free running of heat exchanger tubes longwise in the gas cooler cartridge. Cyclic fluctuations on the heat exchanger tubes resulted in metal fatigue and cracks. |  | 1 - For information only, fatigue cracking, heat exchanger, leak, power reduction, turbine generator, turbine trip | ER.2 , ER.3
WER MOW 16-0022 | 2016-01-23 | 2017-01-12 01:36 | Tianwan-2 | The failure of 2CRD11 cabinet of TXP system Unit 2 resulting in power reduction | Trending | During normal operation, reactor protection alarms activated and one steam generator (SG) display was lost, leading to the fluctuation of feedwater flow and water level. Power was reduced to 79%. | The cause of malfunction was a component failure. |  | 1 - For information only, power reduction, steam generator / boiler | ER.1
WER MOW 15-0191 | 2015-08-29 | 2017-01-12 01:30 | Bushehr-1 | Reactor scrammed on ‘Local heat generation of maximum-duty fuel element over 448 Wt/cm’. | Trending | During normal operation, the turbine control oil pressure dropped. In the following 3 seconds, electrical load dropped and secondary pressure rose with subsequent electrical load recovery and secondary pressure drop. Reactor protection activated resulting in automatic reactor scram. | The root cause was lack of teamwork in control room. Inadequate design documentation was a contributor. |  | 1 - For information only, automatic scram, oil, turbine control | OP.1 , OP.2
WER MOW 15-0160 | 2015-08-18 | 2017-01-11 05:48 | Khmelnitsky-1 | With the Unit in a refueling outage, fuel assembly top nozzles were inspected to find foreign materials. | Trending | During refueling outage, several fuel assembly top nozzles were inspected and foreign material was found. | The direct cause was fiber fragments intrusion from the central hall ventilation system. The root cause was failure to exclude foreign materials. |  | 1 - For information only, foreign material, fuel assembly, nozzle | CM.4 , MA.2
WER MOW 15-0072 | 2015-04-21 | 2017-01-12 00:18 | Balakovo-1 | Electrical Load Reduction due to Circulating Water In-Leakage into a Turbine Condenser | Trending | During normal operation, power was reduced to about 75% to address circulating water leakage into the turbine condenser. | The cause was leaking turbine condenser tubes. The root cause was inadequate tubing material use. | SER 2003-4 | 1 - For information only, chemistry, circulating water, condenser tube, conductivity, leak, power reduction | ER.4
WER MOW 14-0195 | 2014-12-28 | 2017-01-11 23:34 | Bushehr-1 | The unit shut down due to transformer failure | Trending | During normal operation, the unit was disconnected from the grid due to transformer failure which supplies protection and safety systems. | The direct cause was a short circuit on the voltage transformer. |  | 1 - For information only, reactor shutdown, short circuit, transformer | ER.1
WER MOW 14-0152 | 2014-10-25 | 2017-01-11 23:27 | Bushehr-1 | A 27 kV Power Line Protection Actuation due to a Voltage Transformer Fault Caused the Main Generator to Trip off Line | Trending | During operation at 73% power, a main generator tripped off line on a phase A voltage transformer fault. During the following transient, the reactor automatically scrammed on low primary circuit pressure. | The direct cause of the transformer trip was a short circuit. An actuator torque switch failure associated to a control valve caused the primary pressure decrease. The root cause is under investigation. |  | 1 - For information only, automatic scram, control valve, short circuit, torque switch, transformer, turbine generator | ER.1
WER MOW 14-0086 | 2014-06-30 | 2017-01-12 05:51 | Bushehr-1 | High Pressure Heater Hi-hi level protection actuation of Unit 1 | Trending | During normal operation, high level in a high pressure heater resulted in disconnection of main generator from the grid and tripping of feed water pumps leading to decrease of water level in the steam generators. The reactor was scrammed manually. | The cause of the failure is unknown. |  | 1 - For information only, feedwater heater, feedwater pump, manual scram, steam generator / boiler | ER.1
WER MOW 14-0049 | 2014-04-11 | 2017-01-11 23:42 | Smolensk-1 | Low Insulation Resistance Observed on Integrated Instrumentation and Control System In-core Sensors in Core Locations 24-51 and 24-45 | Trending | During low power operation, two in-core sensors sent an automatic reactor setback signal. All control rods inserted into the reactor excluding control rods of fast reactor protection system as per design. | The direct cause was degradation of the in-core sensor insulation. The root cause is unknown. |  | 1 - For information only, incore detector, insulation | ER.1
WER MOW 14-0032 | 2014-03-20 | 2017-01-11 06:34 | Kursk-3 | A short circuit on the non-vital bus of metal clad switchgear 0.4 kV | Trending | While operating at 1045 MWe, a fire occurred inside the switchgear room and the switchgear bus was damaged. As a consequence, all related transformers and buses were de-energized and removed from service for repair, reducing&nbsp;the redundancy of the electrical power system. | The direct cause was a short circuit. The causes of the bus short circuit was equipment ageing. |  | 1 - For information only, ageing, bus, fire, short circuit, switchgear | ER.3 , FP.1
WER MOW 14-0012 | 2014-01-08 | 2017-01-12 04:56 | Zaporozhye-5 | Hydrogen leakage of nonisolable pipe flange joint to G5 generator body | Trending | While operating at 750 MWe, a hydrogen leakage was found from a non-isolable pipe flange joint to the generator body. The turbine generator was unloaded and disconnected from the grid for repair. Reactor was still in operation at 30% thermal power. | The cause was inadequate seal material selection. Inadequate fabrication and component monitoring were contributors. |  | 1 - For information only, contractor, hydrogen, leak, turbine trip | ER.2 , ER.3 , MA.2
WER ATL 17-0140 | 2016-10-04 04:09 | 2017-01-31 16:17 | Brunswick 1 | Incorrect Vendor Refurbishment Leads to Condensate Pump Failure and Unplanned Downpower | Trending | During normal operation, the reactor feed pump suction low pressure and condensate booster discharge/suction low pressure alarms were received simultaneously due to a running condensate pump internal failure. The reactor water level was low and the reactor power was reduced to approximately 70%. | The cause was that the unapproved gaskets was used during the refurbishment assembly, causing failure of the pump upper column joint. This allowed flow from the water column to recirculate back to the suction bell. The apparent causes were inadequate joint gasket design by the original supplier, no corrective actions for continuing use the unapproved gasket design, failing to document defective joint conditions by the refurbishment vendor and no approval of the deviation during procurements. |  | 1 - For information only, condensate pump, design criteria / design basis, gasket, installation, management oversight, power reduction, procurement, spare part, vendor, vibration | ER.3 , MA.1 , MA.2 , PI.2
WER ATL 17-0138 | 2016-12-04 | 2017-01-31 16:11 | Laguna Verde 2 | Reactor SCRAM due to turbine trip caused by spurious over speed signal | Trending | During normal operation, the main turbine average speed signals caused the turbine trip followed by an automatic scram. As a result, the unit was off line for about 2 days for troubleshooting. In the same month, an automatic reactor scram occurred due to the same reason. | The cause of the main turbine average speed alarms was that the speed sensor leads were in contact with the main turbine shaft and the material used for holding the speed channels leads was metallic causing continuity between the sensors. The apparent cause was inadequate maintenance procedures. A contributor was a lack of supervision and monitoring during routing of speed sensor channel leads. |  | 1 - For information only, alarm, automatic scram, insulation, lead, overspeed, procedure inadequacy, sensor, troubleshooting, turbine trip | MA.1 , MA.2 , PI.2
WER ATL 17-0132 | 2016-10-11 14:00 | 2017-01-30 19:22 | Palo Verde 1 | Employee Rolled Ankle Resulting in a Recordable Injury | Trending | While conducting preparation for pipe expansion joint bolt removal, one employee was traversing a catwalk from one side of the pipe to the other when a misstep caused the individual&rsquo;s foot to roll resulting in a right ankle injury. He was transported to hospital for additional examination. | The cause was lack of situational awareness. Individual failed to exercise adequate situational awareness when traversing within the work area and to ensure that footwear is in satisfactory condition. |  | 1 - For information only, industrial safety, injury | IS.1
WER ATL 17-0129 | 2016-10-12 13:38 | 2017-01-30 18:27 | Byron 2 | Malfunction Causes Loss Of Power to Motor Control Center Resulting In A Manual Scram. | Trending | During normal operation, failure of a circuit board to a motor control centre caused a loss of power to valve relays and consequently closing of two feed water isolation valves. This resulted in decrease in steam generators level and the reactor was manually scrammed. | The apparent cause was a manufacturing defect on the circuit board. |  | 1 - For information only, circuit board, feedwater valve, manual scram, motor control centre, power supply, single point vulnerability | ER.3
WER ATL 17-0123 | 2016-12-11 | 2017-01-30 17:56 | Bruce A 1 | Unit 1 Turbine Trip During Emergency Transfer Scheme Testing | Trending | During operation at 89% power and while performing emergency transfer scheme testing, a 4.16 kV distribution transformer tripped and de-energised the transfer bus. This resulted in tripping of turbine governing system fire resistant fluid (FRF) pump and subsequent trip of the standby FRF pump caused turbine trip and a reactor power stepback to less than 65% power. The unit was shut down for 3.6 days. | The cause was spurious tripping of the transformer on current differential. |  | 1 - For information only, hydraulic fluid, power supply, reactor shutdown, transformer, turbine control, turbine trip | ER.1
WER ATL 17-0121 | 2016-10-06 22:40 | 2017-01-27 18:55 | St. Lucie 2 | Intake Cooling Water Header Inoperable Due to Actuator Bolting Issue | Trending | During normal operation, actuator bolts of an intake cooling water backwash outlet valve were found backed out and damaged. The intake cooling header was declared inoperable and entry into a limited condition for operation was made. | The direct cause was that the actuator was assembled without the proper torque applied. The apparent cause was inadequate work order lacking documentation of torque values and reference to correct documents to perform the bolting. The contributing cause was ineffective supervisory review. | SOER 2007-2 Rec 4 | 1 - For information only, bolt, circulating water, component cooling water, intake, limiting condition of operation, management oversight, procedure inadequacy, torque, valve actuator, work control | MA.1 , MA.2 , WM.1
WER ATL 17-0120 | 2016-10-24 10:22 | 2017-01-27 18:48 | Fermi 2 | Unplanned Technical Specification Action Statement Entries due to Offsite Voltage | Trending | During normal operations, the grid operator informed that the post-trip voltage on the division 1 offsite feed could drop below allowable limits in case of turbine trip. This caused an unplanned entry into a limiting condition of operation (LCO). | The cause was lack of understanding, detection, and management of recent electrical system generation portfolio changes, that affect voltage drops resulting from trips of unit 2. Lack of early warning capability to flag degraded margin conditions prior to reaching the operability limit was a contributor. |  | 1 - For information only, limiting condition of operation, loss of offsite power | CM.1 , OP.1
WER ATL 17-0119 | 2016-06-25 15:03 | 2017-01-27 18:41 | Watts Bar 1 | Down Power Due to Turbine Building Sump Pump Failure | Trending | During operation at 86% power, one turbine building sump pump stopped while the other pump was already out of service. This caused flooding of the turbine building. The unit power was reduced by 20% to prevent heater drain tank pump motor submersion. | The cause was equipment degradation over time. The other causes were inadequate process to identify and prioritize non-critical and run to failure work and decisions made on corrective work and non-critical preventative maintenance work orders to be removed from the schedule. | SER 2016-2 | 1 - For information only, ageing, flood, ground fault, power reduction, pump, work control | ER.3 , OF.1 , WM.1
WER ATL 17-0118 | 2012-09-17 03:13 | 2017-01-27 18:30 | Browns Ferry 3 | Emergency Diesel Generator Control Power Breaker Trip During Post Modification Testing | Trending | During normal operation and while performing post-modification testing of an emergency diesel generator (EDG), the control circuit breaker tripped, causing a loss of governor control power for the EDG. It resulted in the loss of the reactor protection system B bus and the transfer of the instrument and control B bus to an alternate power supply. This event led to delays in restoring the EDG and unplanned entry into Limiting Conditions of Operation (LCO). The unit power was decreased to 80%. | The cause of the event was that the procedure did not include guidance related to routing of ground cable from surge suppressors such as varistors used to protect circuits from voltage transients. | SER 2005-3 | 1 - For information only, cable, condenser air ejector, condenser vacuum, diesel generator, limiting condition of operation, power reduction, procedure inadequacy | CM.3 , MA.2
WER ATL 17-0116 | 2012-10-16 13:00 | 2017-01-27 07:51 | Waterford 3 | Plant Down-power due to Improper Assessment of a Main Steam Safety Relief Valve Test | Trending | During normal operation, a test failure of one of the main steam line safety relief valves caused the relief valve to be declared inoperable. As a result, the plant entered a limiting condition of operation and power was reduced to 88%. | The apparent cause of the misinterpretation of the data was inadequate procedural guidance to ensure critical steps are identified and verifications are performed. A contributing factor was the over-reliance on the vendor. |  | 1 - For information only, limiting condition of operation, main steam safety valve, power reduction, procedure inadequacy, vendor | MA.2 , OP.2
WER ATL 17-0115 | 2016-09-29 | 2017-01-27 07:48 | Oyster Creek 1 | Main Steam Safety Relief Valve Failed As Found Testing | Trending | During a refuelling outage and while testing a removed main steam shutoff valve (MSSV) in a factory, the MSSV did not meet the as-found pressure test criterion. This resulted in a condition prohibited by technical specifications. | The cause was set point drift due to mechanical issues such as spring relaxation. |  | 1 - For information only, main steam safety valve, setpoint drift, spring, technical specification | ER.3
WER ATL 17-0114 | 2016-09-19 | 2017-01-27 07:43 | Oyster Creek 1 | Electromatic Relief Valve Failed to Stroke | Trending | During cold shutdown and while verifying the actuators capability to open the pilot valves, one of the five electromatic relief valve (EMRV) actuators failed to stroke using the main control room control switch. The valve was inoperable longer than allowed by technical specifications. | The cause was an error during relief valve reassembly. Electrical maintenance technicians failed to follow the work order steps for refurbishment of the EMRV actuator, which resulted in missing the star washers between the cut out switch hinge pins and lever arm. |  | 1 - For information only, actuator, human error, relief valve, technical specification | MA.1
WER ATL 17-0111 | 2016-12-10 | 2017-01-27 07:19 | Darlington 1 | Welding Sparks result in Igniting Combustible Material Directly below the Welding Area | Trending | During welding activities for a construction project, welding sparks and slag fell seven meters below and ignited combustible material located directly below the welding area. This resulted in damage to some equipment and cables. | The apparent cause was inadequate monitoring of welding slag by the fire watch personnel. The other causes were that fire blankets were not used to cover the combustible material and the combustible material was allowed to collect on the work site. |  | 1 - For information only, contractor, fire, fire protection, industrial safety, weld | FP.1 , NP.1
WER ATL 17-0108 | 2015-12-04 | 2017-01-25 19:59 | Sequoyah 1 | Chemistry Samples Indicate Nuclear Fuel Leak | Trending | During normal operation, routine reactor coolant system chemistry sample results showed increasing xenon activity indicating fuel leak. The reactor coolant system activity remained below the technical specification limit. | The fuel leak was caused by grid-to-rod fretting or debris. |  | 1 - For information only, debris / crud, fuel assembly, fuel leak | CM.4
WER ATL 17-0107 | 2016-03-10 14:30 | 2017-01-25 19:55 | Oconee 1 | Lee Combustion Turbine Temperature Signal Failure | Trending | While one of the two off-site combustion turbine (CT) generators was operating, the primary liquid manifold temperature signal fail alarm was received. This caused the CT to decrease power to minimum load and rendered it incapable for providing emergency power to the nuclear site. | The cause was that the cannon connector was not tightened properly when it was installed by contract personnel following offsite refurbishment. |  | 1 - For information only, contractor, emergency power, human error, installation | MA.1
WER ATL 17-0105 | 2015-12-17 22:16 | 2017-01-25 10:51 | Turkey Point 4 | Heater Drain Pump Mechanical Seal Leak Results in Down Power to Repair | Trending | During normal operation, steam and water leakage occurred from a heater drain pump (HDP) mechanical seal. The reactor power was reduced to 85% to carry out seal replacement. | The direct cause was age related hardening of the seal. The apparent cause was inadequate preventive maintenance. |  | 1 - For information only, ageing, heater drain, leak, power reduction, preventive maintenance, pump seal, steam | ER.2 , ER.3 , PI.2
WER ATL 17-0104 | 2016-02-20 15:00 | 2017-01-25 10:49 | LaSalle 1 | Recordable Hand Injury Contacting Blower Impeller | Trending | A supplemental worker inadvertently placed their hand inside the exhaust discharge port of an operating ventilation unit. The glove got caught in the rotating blower impeller which pulled the hand into the device resulting in an injury and required off site medical treatment. | The cause was inadequate situational awareness. The apparent cause was the absence of the required equipment guarding (a cage or a screen). |  | 1 - For information only, industrial safety, injury | IS.1
WER ATL 17-0103 | 2015-12-18 | 2017-01-25 10:47 | Hope Creek 1 | Late Reactor Protection System Trip During Valve Testing | Trending | During normal operation and while performing main turbine stop valve (MSV) test, one pair of MSVs did not generate the reactor protection system (RPS) trip signal immediately. One channel of the RPS was declared inoperable, which led to entry into a limiting condition of operation. | The cause was mechanical binding of the switch arm and the mounting bolts for the limit switch. The other cause was inadequate procedure for turbine steam control valve limit switch adjustment. |  | 1 - For information only, limit switch, limiting condition of operation, procedure inadequacy, reactor protection system, turbine stop valve | ER.1 , MA.2
WER ATL 17-0102 | 2016-04-14 16:48 | 2017-01-24 14:29 | Prairie Island 1 | Reactor Vessel Injection Line Valve to the Reactor Vessel has a Broken Gland Follower | Trending | During normal operation, a leak was reported on the reactor vessel injection line manual valve during a containment entry. The valve was declared inoperable&nbsp;and resulted in entry into a shutdown technical specification action statement. | The cause of the leakage was a broken gland follower. Component degradation was a contributor. |  | 1 - For information only, leak, limiting condition of operation, valve | ER.1
WER ATL 17-0100 | 2014-07-15 | 2017-01-24 14:24 | Millstone 3 | Turbine Driven Aux Feedwater Pump Inoperable due to Failure During Surveillance Test | Trending | During normal operation, the turbine driven auxiliary feedwater (TDAFW) pump failed to achieve and sustain rated speed during surveillance test. This resulted in entry to a 72 hour limiting condition of operation (LCO). | The direct cause was a relay failure of the pump speed control system. The apparent cause was inadequate review of subcomponents for preventive maintenance strategies. The contributing factor was less than adequate technical rigor in identifying critical components internal to vendor supplied equipment in a risk significant system. |  | 1 - For information only, auxiliary feedwater pump, limiting condition of operation, preventive maintenance, relay, speed control | ER.2
WER ATL 17-0099 | 2013-05-22 | 2017-01-24 13:50 | Millstone 2 | Emergency Diesel Generator Trip Due to Service Water Ingress to Lube Oil System | Trending | During normal operation and while testing an emergency diesel generator (EDG), the EDG tripped on high crankcase pressure. This resulted in entry into a limiting condition of operation. | The cause was service water ingress to the EDG lube oil system due to a lubricating oil heat exchanger tube leak because of corrosion. The other cause was inadequate monitoring of the lube oil for presence of water. |  | 1 - For information only, corrosion, diesel engine, diesel generator, heat exchanger, limiting condition of operation, service water, tube leak | ER.2 , ER.3
WER ATL 17-0098 | 2015-12-06 23:59 | 2017-01-24 13:39 | Prairie Island 2 | Test Failure of Over Excitation Limiter on Automatic Voltage Regulator | Trending | During an outage and while conducting online acceptance testing of the automatic voltage regulator (AVR) over excitation limiter, the system oscillated and adjustment of the AVR was required to control the voltage. The event caused a delay in plant startup for 2.5 days. | The cause was incorrect settings of the overexcitation limiter. |  | 1 - For information only, exciter, human error, setpoint, voltage regulator | MA.1
WER ATL 17-0097 | 2016-10-10 12:46 | 2017-01-24 13:24 | St. Lucie 2 | Injury During Indicating Bulb Replacement | Trending | While replacing an indicating light bulb of a main feedwater pump motor heater, an operator received an electrical shock and burns to his fingers. The operator received off-site medical treatment. | The cause was a failed rheostat that allowed 120V AC to be present at the light socket. The other cause was a legacy design issue from initial construction where the light socket was not wired using standard failsafe design. |  | 1 - For information only, burn, design criteria / design basis, electric shock, industrial safety, injury | ER.3 , IS.1 , WM.1
WER ATL 17-0095 | 2016-09-14 11:49 | 2017-01-24 13:15 | Fitzpatrick 1 | Unplanned Power Reduction on Loss of a Feedwater Pump Turbine | Trending | During operation at 84% power, a reactor feed pump turbine (RFPT) stopped unexpectedly leading to a reactor water recirculation runback. This resulted in reactor power reduction to 49%. | The direct cause was failure of the auxiliary oil pump motor resulting in loss of hydraulic oil pressure to the RFPT stop valves.The apparent cause was failure of the main shaft driven oil pump to supply sufficient hydraulic oil pressure and failure of the check valve to close when the auxiliary oil pump motor failed. Contributing causes were lack of preventive maintenance and improper operation of the feed pump lube oil system. |  | 1 - For information only, check valve, feedwater pump, lube oil, lube oil pump, power reduction, preventive maintenance | ER.1 , ER.2
WER ATL 17-0094 | 2016-08-18 10:09 | 2017-01-24 13:08 | Hatch 2 | Emergency Diesel Generator Trip on Low Lube Oil Pressure Due to Sheared Cross Drive Shaft | Trending | During normal operation and while performing an emergency diesel generator (EDG) test, the EDG tripped on low lubricating oil pressure, resulting in entry into a limiting condition of operations. | The direct cause was the cross drive shaft damage. Historical factory testing caused the damage due to a defect was initiated internally on the cylindrical bearing rolling elements and / or contact surfaces which propagated over time. The preventive maintenance was not sufficient on the front end gear train or the engine driven lube oil pump. |  | 1 - For information only, diesel engine, diesel generator, limiting condition of operation, lube oil pump, preventive maintenance, vendor | ER.2
WER ATL 17-0093 | 2015-10-01 17:00 | 2017-01-24 13:02 | Fermi 2 | Loss of Power to Reactor Building Crane | Trending | During a refuelling outage and while lifting the reactor vessel head, the reactor building crane lost power due to actuation of thermal overloads, suspending the head approximately two feet above the flange. | The cause was that the crane was being operated on temporary power with reduced voltage due to incoming 120 kV line voltage drops. The other cause was a recent magnetorque brake adjustment, which caused the crane to draw more current. | SOER 2008-1 Rec 2, SER 2005-3 | 1 - For information only, crane, industrial safety, modification, power supply | CM.3 , IS.1
WER ATL 17-0092 | 2015-07-30 05:41 | 2017-01-24 12:52 | Fermi 2 | Low Oil Level in South Heater Drains Pump Results in Downpower | Trending | During normal operation, oil leakage was identified from the heater drains pump motor. The pump was taken out of service for repair and reactor power was reduced to 88%. | The most likely cause was a design deficiency in the upper bearing reservoir. The motor was sent to vendor for disassembly and inspection. |  | 1 - For information only, bearing, leak, oil, power reduction, vendor | ER.1 , ER.3
WER ATL 17-0091 | 2016-03-05 | 2017-01-24 12:43 | Dresden 3 | Main Turbine Control Valve Driven to Full Open Position During Quarterly Valve Cycling | Trending | During operation at 75% power and while performing main turbine control valve fast closure test, one control valve went to the full open position. This resulted in a reactor pressure and level transient and increase in reactor thermal power. The event resulted in unit power reduction to 74%. | The cause was separation of the control valve switch rod from the linear variable displacement transducer (LVDT) on the digital electro-hydraulic control system. The apparent cause was inadequate work order instructions for the LVDT assembly installation and inadequate preventive maintenance inspection procedure, which did not include the manufacturer's requirements. |  | 1 - For information only, electro hydraulic control, power reduction, power surge, procedure inadequacy, turbine control valve | MA.2 , WM.1
WER ATL 17-0090 | 2016-04-08 16:57 | 2017-01-24 11:14 | Cook 1 | Transformer Containment Berm Seal Failure During a Transformer Leak-Out Failure | Trending | During normal operation, a transformer trip caused an oil leak from oil containment system and a large oil spill into the catch berm which leaked oil outside of the berm into the soil. A total of 945 cubic yard of contaminated soil and gavel were removed. | The transformer tripped due to a phase failure. The apparent cause was a design flaw of the oil containment system. The seal between the concrete blast wall and the oil containment berm was not adequate to prevent the leak. The design drawing did not provide the appropriate detail to ensure a seal between the blast wall and the oil containment berm. | SOER 2011-1 Rev 1 Rec 4,5 | 2 - Important lessons, design criteria / design basis, leak, oil, seal, transformer | CM.1
WER ATL 17-0089 | 2016-09-10 10:26 | 2017-01-24 10:52 | Columbia Generating Station | Momentary Loss of 115 kV Offsite Power Source | Trending | During normal operation, a grid disturbance resulted in a momentary loss of 115 kV offsite power source and consequently entry into a limiting condition of operation. | The cause was a momentary fault on the transmission system grid for unknown reasons. |  | 1 - For information only, grid, limiting condition of operation, loss of offsite power, transmission line | ER.1
WER ATL 17-0086 | 2013-01-02 12:00 | 2017-01-24 10:44 | Arkansas Nuclear One 2 | High Pressure Safety Injection Pump Low Bearing Oil Level after Inadvertent Safety Initiation Actuation System (SIAS) Actuation | Trending | During normal operation, the high pressure safety injection pump bearing oil level was found low after an inadvertent safety initiation actuation system (SIAS) actuation. This resulted in the pump being declared inoperable. | The direct cause of the event was insufficient oil level due to a false oil level indication in the oil bubbler. Mechanical craft and operations did not check the bubbler stand settings during oil change out and during oil additions. Contributing cause was that the work order instructions lack detail of the amount of oil that is expected to be drained and replaced in the pump. |  | 1 - For information only, bearing, high pressure safety injection, oil level, procedure inadequacy | MA.1 , MA.2
WER ATL 17-0085 | 2016-12-06 | 2017-01-24 10:12 | Koeberg 1 | The Emergency Stop Button was accidentally depressed by cleaning individual in the Unit 2 Emergency Back-up Diesel room causing a Limiting Condition for Operation (LCO). | Trending | During normal operation, the emergency stop button of an emergency diesel generator (EDG) was inadvertently depressed by an individual performing cleaning of the EDG room. This led to unavailability of the automatic swap over function between Unit 1 and 2 and entry into a limiting condition of operation on both units. | The cause was human error due to inadequate situational awareness. The other cause was lack of cover on the emergency stop button. |  | 1 - For information only, diesel generator, human error, limiting condition of operation | CM.2 , NP.1
WER ATL 17-0083 | 2016-08-31 | 2017-01-20 12:57 | Salem 2 | Reactor Trip Due to Reactor Coolant Pump Trip | Trending | During normal operation, the reactor scrammed automatically due to tripping of a reactor coolant pump (RCP). The event resulted in an outage for nine days. | The root cause was a leak from a containment fan cooling unit (CFCU) motor cooler that propagated onto the RCP electrical penetration inner closure assembly due to inadequate procedural guidance during restoration of the CFCU. The contributing causes include low operating margin of the CFCU gaskets and inadequate corrective actions from previous similar events. |  | 1 - For information only, automatic scram, gasket, heat exchanger, leak, penetration, reactor coolant pump, water hammer, water intrusion | ER.3 , MA.2 , PI.2
WER ATL 17-0080 | 2016-09-26 19:26 | 2017-01-20 12:37 | Callaway 1 | Power Reduction Due to Spurious Alarms on the Main Feedwater Pump Control System | Trending | During normal operation, a main feedwater pump (FWP) had to be taken out of service to solve multiple system fault alarms on the digital feedwater operator station display screen. As a consequence, the unit power was reduced to 65%. | The cause was a loose termination in a FWP turbine servo position controller enclosure. The apparent cause was limited ability to visually confirm full wire insertion, difficulty in reaching the work location and no guidance was provided for confirmation of wire termination. |  | 1 - For information only, alarm, digital control system / digital components, power reduction, procedure inadequacy, wiring | ER.1 , MA.2
WER ATL 17-0079 | 2016-09-20 11:50 | 2017-01-20 12:34 | Pilgrim 1 | Momentary Loss of the 23KV Offsite Power Line Feeding the Station Shutdown Transformer | Trending | During normal operation, a 23KV offsite power line feeding the station shutdown transformer was lost. This caused a partial loss of offsite power. The event resulted in an entry into a limiting condition of operation. | The cause of the line tripping was a failed lightning arrester which tripped the breaker supplying the shutdown transformer. |  | 1 - For information only, lightening protection system , limiting condition of operation, loss of offsite power, transformer, transmission line | ER.1 , ER.3
WER ATL 17-0078 | 2016-09-21 | 2017-01-20 12:31 | Harris 1 | Containment High-Range Radiation Monitors Declared Inoperable Due to Potential for Erratic Indications | Trending | During normal operation, the containment high-range radiation monitors were declared inoperable due to the potential for erratic indications from a phenomenon known as temperature induced current, resulting in entry into a limiting condition of operations. | A regulator information notice 20 years ago was not properly evaluated and the recommendation of replacing cables that would cause the erratic indications was not implemented. |  | 1 - For information only, cable, limiting condition of operation, radiation monitor | OE.1
WER ATL 17-0077 | 2016-09-20 22:00 | 2017-01-20 12:29 | Susquehanna 2 | Failure of Swing Bus Automatic Transfer Switch | Trending | During normal operation and while performing the swing bus operability test, the reactor building essential service 480V motor control center (MCC) lost power when the alternate source breaker was opened to force the automatic transfer switch (ATS) back to its normal source. This resulted in entry into a limiting condition of operation. | The direct cause was lack of lubrication. The apparent cause was inadequate work instructions, which did not provide guidance on how to properly lubricate the ATS assembly. |  | 1 - For information only, limiting condition of operation, lubrication, motor control centre, preventive maintenance, procedure inadequacy, switch | ER.2 , MA.2
WER ATL 17-0075 | 2015-12-09 13:46 | 2017-01-20 08:37 | Waterford 3 | Condensate Pumps Failure Caused Outage Extension | Trending | During a refuelling outage, both condensate pumps tripped when started after their replacement with two rebuilt spares. This caused an extension to the outage for six days. | The pumps failed due to misalignment. The work package for alignment did not include the necessary documentation to ensure that the work was correctly performed. Other causes were inadequate communication when the project was transferred to a new project manager and inadequate management oversight. |  | 1 - For information only, condensate pump, contractor, management oversight, procedure adherence, procedure inadequacy | MA.1 , MA.2 , WM.1
WER ATL 17-0074 | 2016-08-01 03:42 | 2017-01-20 08:25 | St. Lucie 1 | Reactor Shutdown to Investigate Potential Reactor Coolant System Leakage | Trending | During normal operation, the reactor was shut down to investigate a reactor coolant system pressure boundary leakage. Investigation determined the leakage was not pressure boundary leakage. | The leakage was a instrumentation seal welded threaded connection leakage due to a fault in the weld with improper thread engagement. |  | 1 - For information only, leak, reactor coolant, reactor shutdown, seal, weld | ER.1 , MA.1
WER ATL 17-0073 | 2012-03-10 04:39 | 2017-01-20 08:16 | St. Lucie 1 | Auxiliary Feedwater Pump Discharge Flow Indicator Failure Leads to 72 hour Technical Specification Action Shutdown Statement | Trending | During normal operation, an auxiliary feedwater pump (AFW) discharge flow indicator was found inoperable. This resulted in entry into a limiting condition of operation. | The apparent cause was setpoint drift for the square root extractor in the flow indication circuitry. A contributing factor was that the AFW flow indicator loop square root extractor was not classified as a single point vulnerability. |  | 1 - For information only, auxiliary feedwater pump, flow transmitter, setpoint drift, single point vulnerability | ER.2
WER ATL 17-0072 | 2016-10-19 01:00 | 2017-01-20 07:51 | Wolf Creek 1 | Switchyard Clearance Order Error | Trending | During an outage, a manual 13.8 KV disconnect was closed, which had a owner company switching order tag in effect requiring the disconnect to be open. There was the potential to introduce unexpected energy into a tagged boundary when performing work in the switchyard. | The apparent cause was inadequate interface with the switchyard tagging process and insufficient communication between the shift operators. The disconnect tags were placed several feet away due to no standardized locations for hanging tags on switchyard components. |  | 1 - For information only, industrial safety, switch, tagging, work control | IS.1 , OP.1 , WM.1
WER ATL 17-0070 | 2016-11-10 | 2017-01-20 07:47 | Sequoyah 2 | Containment Spray Pump Flow Control Valve Failed to Open | Trending | During normal operation and while starting a cooler in containment spray pump room for preventive maintenance, a flow control valve failed to open. resulting in no cooling water to the room cooler. Consequentially the pump was declared unavailable and an entry into a limiting condition of operations was required. | The cause was the valve sticking in its seat due to silt. |  | 1 - For information only, containment spray, control valve, debris / crud, essential service water, heating ventilating and air conditioning, limiting condition of operation | ER.1
WER ATL 17-0066 | 2016-10-07 | 2017-01-20 07:26 | Limerick 1 | Operation on Residual Heat Removal Hand Switch Failure | Trending | During normal operation and while aligning a residual heat removal (RHR) exchanger, a RHR service water outlet valve failed to stroke open from the main control room hand switch, resulting in entry into 3 limiting conditions of operations. | The cause was the plastic spline of the hand switch was cracked, preventing proper alignment of the switch contacts. The apparent cause was a lack of preventive maintenance to the hand switch. |  | 1 - For information only, crack, limiting condition of operation, preventive maintenance, residual heat removal, switch | ER.2
WER ATL 17-0065 | 2016-08-03 09:00 | 2017-01-20 07:22 | Hope Creek 1 | Hand Injury While Performing Minor Maintenance | Trending | While performing maintenance on a heating, ventilation and air condition (HVAC) unit, a mechanic came into contact with the HVAC unit's running fan blade and injured his hand. The mechanic was taken to a hospital for treatment. | The causes were inadequate recognition of the danger of working in the proximity of exposed running fan blades and poor lighting inside the rotating fan. |  | 1 - For information only, human error, industrial safety, injury | IS.1
WER ATL 17-0063 | 2016-10-06 15:25 | 2017-01-20 07:10 | Calvert Cliffs 1 | Configuration Control Event Results in the Loss of a 120 Volt Vital AC Bus | Trending | During normal operation and while starting a 120V vital AC inverter after maintenance, a loss of 120V vital bus occurred. This resulted in Unit 1 and 2 entering a limiting condition of operation. | The apparent cause was an improperly performed procedure step due to inadequate use of human performance tools including procedure use and adherence and peer check. The other cause was inadequate prejob brief and supervisory oversight. | SOER 2013-1 Rec 3 | 1 - For information only, human error, inverter, limiting condition of operation, management oversight, prejob brief, procedure adherence | OP.1 , OP.2
WER ATL 17-0061 | 2016-12-17 | 2017-01-17 19:40 | Bruce B 7 | Unit 7 Turbine vibrations after unit startup | Trending | During startup after an outage and at 65% power, turbine was tripped due to increased vibration at the generator bearing. This resulted in extension of outage for eight days. | The direct cause was elevated turbine vibration levels from the recently rewound generator rotor. The apparent cause was rotor imbalance during rotor rewind carried out on-site since there was no method to confirm rotor balancing prior to initial run up. |  | 1 - For information only, bearing, procedure inadequacy, turbine generator, turbine trip, vibration | MA.1 , MA.2
WER ATL 17-0060 | 2016-08-13 03:00 | 2017-01-13 18:54 | Watts Bar 2 | Automatic Start of Turbine Driven Auxiliary Feed Water Pump | Trending | While the reactor was being stabilised following a pre-planned reactor shutdown, a turbine driven auxiliary feedwater pump automatically started on low steam generator water levels. | The direct cause was operator focusing on reactor core temperature and losing focus on steam generator water level. The apparent cause was an inadequate pre-job brief with a contributing cause of procedure inadequacy. | SOER 2013-1 Rec 3 | 1 - For information only, auxiliary feedwater pump, human error, prejob brief, procedure inadequacy | OP.1 , OP.2
WER ATL 17-0059 | 2016-10-01 12:56 | 2017-01-13 18:52 | Turkey Point 4 | Unplanned Downpower due to Steam Generator Feed Pump Bearing Vibration Amplitude Trends Coincident to Axial Movement of the Pump Shaft | Trending | During normal operation, a steam generator feed pump (SGFP) was found having high bearing vibration and axial movement of the pump shaft. The unit was down powered to 48% to remove the pump from service to carry out repairs. | The direct cause was the SGFP oil pump drive nut loosening. The apparent cause was procedure steps being incorrectly identified as not applicable and thus not implemented in the assembly process. The contributing cause was the wrong selection of a setscrew during the assembly process. |  | 1 - For information only, bearing, feedwater pump, nut, power reduction, procedure adherence, pump shaft, vibration | MA.1
WER ATL 17-0056 | 2016-08-31 | 2017-01-13 18:42 | Salem 1 | Power Reduction Due to High Vibration on Steam Generator Feed Pump | Trending | During normal operation, a steam generator feed pump turbine bearing vibrations increased and exceeded the operational limit. An unplanned power reduction to 58% was required for repairs. | The cause was a loosening of the coupling hub retention nut due to the installation of the incorrect set screw. The incorrect set screw was installed due to a legacy issue with work Instructions and worker practices. |  | 1 - For information only, bearing, feedwater pump, human error, nut, power reduction, procedure inadequacy, vibration | MA.1 , MA.2
WER ATL 17-0055 | 2016-08-14 | 2017-01-13 18:40 | Salem 1 | Station Blackout Diesel Generator Failed to Start | Trending | During normal operation and while performing a periodic test, a station black out (SBO) diesel generator failed to start. | The failure was caused by the lack of battery voltage. The other cause was untimely replacement of SBO generator starting batteries for a known degraded condition. |  | 1 - For information only, battery, diesel generator, preventive maintenance | ER.2 , PI.3
WER ATL 17-0053 | 2016-09-27 10:54 | 2017-01-13 18:35 | River Bend 1 | Failure of Residual Heat Removal Line Fill Pump | Trending | During normal operation, a residual heat removal (RHR) line fill pump tripped on the motor breaker thermal overload. A main RHR pump was started in suppression pool cooling mode to avoid entry into a limiting condition of operation. | The cause was failure of the pump thrust bearing. |  | 1 - For information only, breaker, pump motor, residual heat removal pump, thrust bearing | ER.1
WER ATL 17-0052 | 2016-09-03 23:05 | 2017-01-13 18:34 | Quad Cities 1 | Control Rod Did Not Insert During Scram Timing Surveillance | Trending | During normal operation and while performing scram timing test, a control rod did not insert when the test switch was actuated at the panel. The rod was declared inoperable and entry into a limiting condition of operation was made. As a consequence, a planned power reduction of 16% was needed for repairs. | The apparent cause was the peening of the movable plunger which caused a scram solenoid pilot valve to stick in the core. |  | 1 - For information only, control rod, control rod drive, limiting condition of operation, pilot valve, power reduction, solenoid valve | ER.3
WER ATL 17-0051 | 2016-08-13 23:59 | 2017-01-13 18:32 | Prairie Island 1 | Notice of Unusual Event declared when Reactor Coolant Letdown Line Containment Isolation valve failed closed | Trending | During normal operation, water leak in the reactor coolant system occurred due to failure of a reactor coolant letdown line containment isolation valve. The leakage exceeded criteria and resulted in a notification of an unusual event to the regulator. | The cause was a manufacturing defect on the solenoid valve coil connections, which were not soldered. |  | 1 - For information only, isolation valve, leak, reactor coolant, solder, solenoid valve, vendor | ER.3 , MA.1
WER ATL 17-0050 | 2016-01-07 12:20 | 2017-01-13 18:30 | Oconee 1 | Hotspot on the Busline Disconnect Switch | Trending | During normal operation, reactor power was reduced to 19% to address a hotspot found on a motor operated disconnect switch at the main switchyard. | The cause was corrosion of the hinge end contacts due to water intrusion because of standing water in the barrel due to absence of weep holes. |  | 1 - For information only, corrosion, power reduction, switch, water intrusion | ER.3
WER ATL 17-0049 | 2016-09-13 12:33 | 2017-01-13 18:28 | North Anna 1 | Emergency Diesel Generator Developed Coolant Leak During 24 Hour Surveillance Run | Trending | During an outage and while performing an emergency diesel generator (EDG) 24 hour run test, a coolant leak greater than the allowed limit occurred on a cylinder coolant return line at the gasket between the cylinder coolant return line and the coolant return header. The EDG was shut down for repair. | The cause was failure of the gasket between the cylinder coolant return line and the coolant return header due to loosening of bolts over time. There was no specified torque value for the fasteners. |  | 1 - For information only, bolt, diesel cooling water, diesel engine, diesel generator, gasket, leak, procedure inadequacy, torque | ER.2 , MA.2
WER ATL 17-0045 | 2016-09-21 02:35 | 2017-01-13 18:20 | Indian Point 2 | Component Cooling Pump Discharge Valve Fails to Close | Trending | During normal operation and after shutting down a component cooling water (CCW) pump, the discharge check valve for the pump did not close as expected. This resulted in CCW low pressure and the CCW system was declared inoperable. This caused entry into a limiting condition of operation for two minutes until another CCW pump was started. | The cause was an improperly designed hanger extension on the check valve which was not installed in accordance with the vendor drawing. This resulted in degradation of the hanger extension over time, causing failure of the check valve. |  | 1 - For information only, check valve, component cooling water, configuration control, installation, limiting condition of operation | MA.1
WER ATL 17-0042 | 2016-01-24 01:04 | 2017-01-13 18:16 | Fitzpatrick 1 | Frazil Ice Results in Scram | Trending | During power ascension at 89% power following planned maintenance, frazil ice formation at the intake structure caused the screenwell intake water level to decrease and led to a manual reactor scram. | The root cause was a design vulnerability of the intake structure to frazil ice accumulation. The contributors were leadership acceptance of mitigation instead of risk elimination, ineffective mitigating procedure and a lack of detail in the design basis documents. | SOER 2007-2 Rec 1 | 1 - For information only, design criteria / design basis, documentation, ice, intake, manual scram, procedure inadequacy | CM.1 , OF.2
WER ATL 17-0039 | 2016-09-25 01:33 | 2017-01-13 18:10 | Cooper 1 | Automatic Actuation of Group One Isolation While Opening Main Steam Isolation Valve | Trending | During plant cooldown for refueling outage, all inboard main steam isolation valves (MSIVs) were closed to minimize steam flow to control cooldown rate. While attempting to unisolate a main steam line (MSL) by opening an inboard MSIV, a MSL high flow signal occurred, resulting in actuation of containment isolation. | The apparent cause was insufficient procedure guidance regarding limitations on opening the MSIVs. Contributing cause was that the main turbine bypass valve was unable to fully close and the gland sealing steam rupture diaphragm was ruptured, reducing main steam pressure downstream of the MSIVs. |  | 1 - For information only, containment isolation, diaphragm, gland seal, main steam isolation valve, main steam line, procedure inadequacy, turbine steam bypass valve | ER.1 , OP.2
WER ATL 17-0038 | 2016-09-10 11:31 | 2017-01-13 18:08 | Beaver Valley 2 | Throttle Valve Failed to Open During Routine Turbine Valve Test | Trending | While performing a turbine valve test, a turbine throttle valve failed to re-open, resulting in the valve being declared inoperable and entry into a limiting condition of operation. As per the test procedure requirement, the reactor power was reduced from 97% to 72%. | The cause was a throttle valve card failure. |  | 1 - For information only, circuit card, limiting condition of operation, power reduction, software, throttle valve, turbine control | ER.3
WER ATL 17-0037 | 2016-10-16 17:06 | 2017-01-13 18:06 | Arkansas Nuclear One 2 | Fix It Now Mechanics Uncoupled the Incorrect Boric Acid Pump | Trending | During an outage, two mechanics inadvertently uncoupled a boric acid makeup pump which was energized and in the auto position when they were supposed to be working on another boric acid pump. This resulted in unavailability of all boric acid pumps and potential for injury. | The direct cause was human error as the mechanics did not verify the correct pump. The apparent cause was inadequate use of human performance tools. |  | 1 - For information only, boric acid, human error, industrial safety, pump | CM.2 , MA.1
WER ATL 17-0023 | 2016-08-11 19:00 | 2017-01-10 08:50 | Watts Bar 1 | Emergency Safety Function Cooler Bearing Failure | Trending | During normal operation, the inboard bearings of a room cooler supplying emergency cooling to the safety related high-efficiency particulate air (HEPA)/charcoal auxiliary building ventilation system failed. The cooler was isolated for maintenance, which resulted in entry into a limiting condition of operation. | The direct cause was over-tensioning of the room cooler fan belts, which caused the fan inboard bearing to be overloaded and the fan shaft to operate in a bowed condition. The root cause was procedure deficiency due to inadequate procedure revision process. The contributing causes were lack of knowledge and failure to evaluate and resolve the true cause of the room cooler failure on two previous instances. |  | 1 - For information only, bearing, fan, heating ventilating and air conditioning, limiting condition of operation, procedure inadequacy, vibration | MA.1 , MA.2 , PI.2
WER ATL 17-0022 | 2016-09-22 03:20 | 2017-01-10 08:44 | Susquehanna 2 | Loss of Secondary Containment Differential Pressure | Trending | During normal operation, the secondary containment zone 2 differential pressure lowered unexpectedly and could not be maintained due to a stuck non-safety related exhaust damper, resulting in entry into a limiting condition of operation. | The cause was age-related degradation of the brass bushings and grease hardening on the linkage between the damper and the actuator. |  | 1 - For information only, ageing, damper, grease, heating ventilating and air conditioning, limiting condition of operation, secondary containment, technical specification | ER.3
WER ATL 17-0015 | 2016-12-08 | 2017-01-10 07:15 | Koeberg 2 | When Unit 2 Reactor Cavity and Spent Fuel Pool System Filter was Being Lowered from the Chateaux into a Concrete Drum, a Large Part of the Filter was Protruding from the Concrete Drum | Trending | While lowering a reactor cavity and spent fuel pool system used filter into a concrete drum, the filter did not go into the drum but sat on top of the drum. The job was stopped and area was declared red zone due to high radiation and locked to prevent access. | The cause was use of wrong centraliser to guide the filter into the drum due to inadequate procedure. |  | 1 - For information only, human error, procedure inadequacy, radiation protection | MA.2 , RS.1
WER ATL 17-0014 | 2016-08-13 | 2017-01-09 15:46 | Darlington 1 | Falling Objects during Hoisting and Rigging Events result in an increased risk to Personnel Safety and Nuclear Safety | Trending | During a lifting activity, a shutdown cooling manway flange of approximately 450 Kg dropped approximately 3 meters. During a separate lifting operation, an emergency power generator exhaust stack of about 15 tons dropped approximately 1 meter when the sling attached to the lower end was cut by a sharp edge during the lift. There were potentials of personal injuries. | The common causes was deficiencies in procedure adherence, unqualified contractor operators, contractor oversight and communications between contractors and the station staff. | SOER 2008-1 Rec 1,4,5 | 1 - For information only, contractor, industrial safety, lifting device, procedure adherence, procedure inadequacy | IS.1 , MA.2
WER ATL 17-0013 | 2016-07-27 | 2017-01-09 15:43 | Darlington 1 | Use of Terminal Point tags for piping Tie-in result in Work Protection Code Violation | Trending | While issuing work authorization to complete work on the containment filter venting system (CFVS) project, it was discovered that a contractor tied in its CFVS piping to the station owned equipment without the use of station work protection and vendor lock out/tag out (LOTO). This resulted in a work protection code violation that could potentially expose a worker to energy. | The root cause was lack of clear direction on how to use terminal points to implement LOTO process. The contributing causes include lack of questioning attitude and lack of understanding of terminal points and the interface between station work protection and LOTO process. |  | 1 - For information only, contractor, human error, industrial safety, procedure inadequacy, tagging, work control | MA.1 , WM.1
WER ATL 17-0012 | 2016-11-28 | 2017-01-08 07:43 | Barakah 1 | Personnel Lost Time Injury While Performing Visual Inspection | Trending | While standing on a cable duct at a height of 70 cm performing a penetration visual inspection, one individual lost his balance and fell while stepping down from the duct, resulting in a fracture of the right ankle and a loss time injury. | The direct cause was that the individual failed to maintain three-point contact during his descent due to inadequate risk assessment. There was no proper access between the ground and cable duct and no proper handhold point available. |  | 1 - For information only, fall, human error, industrial safety, injury | IS.1
WER ATL 17-0011 | 2016-11-19 | 2017-01-06 19:34 | Darlington 4 | Air Conditioning Unit Tripped result in a Loss of Redundancy of Highly Critical Component | Trending | During normal operation, an air condition unit (ACU) for the secondary control area (SCA) tripped, resulting in loss of redundancy for the SCA containing critical components necessary to shutdown, cool down and monitor the unit from a remote location. | The apparent cause&nbsp; was ageing. The other cause was degradation of the ACU due to loss of humidity control&nbsp;because of&nbsp;excessive build-up in the humidification pan. |  | 1 - For information only, ageing, air conditioning, heating ventilating and air conditioning | ER.3
WER ATL 17-0010 | 2016-11-08 | 2017-01-06 19:21 | Pickering A1 | Collector Plate falls from Turbine Hall Crane resulted in a near-miss accident. | Trending | A part (collector shoe, weighting 0.68 kg) fell from the overhead turbine hall crane for approximately 27 meters and landed approximately 3-5 m from workers' area. There was a potential of personal injury. | The direct cause was the snagging of a power cable on adjacent support brackets. The apparent cause was the failure of a plastic cable management clip due to age related degradation. A lack of direct engineering support caused the absence of a formal performance monitoring programme and aging management strategy for the turbine hall crane. | SOER 2008-1 Rec 3 | 1 - For information only, ageing, cable, crane, fall, industrial safety, preventive maintenance | ER.3 , IS.1
WER ATL 17-0008 | 2016-11-29 | 2017-01-06 19:03 | Pickering B6 | Common Water Supply intake debris run resulted in unit forced outage | Trending | During normal operation, the common water supply intake travel screen differential pressure increased rapidly due to floating debris. An 8-day forced unit shutdown was needed to address the issue. | The apparent cause of the event was changing environment conditions that resulted in the formation of large algae. | SOER 2007-2 Rec 3 | 1 - For information only, debris / crud, environment, intake, reactor shutdown, travelling screen | CM.1 , OF.2
WER ATL 17-0007 | 2016-11-15 | 2017-01-06 18:52 | Pickering A1 | Incorrect Work Protection Method Used to Remove Sodium Meta-bisulphite Pump Resulted in Potential for Energy Source in Safe Work Area | Trending | During application of a personnel protection tag-out (PPT) work protection method for carrying out repair of a sodium meta-bisulphite pump, it was found that a relief valve (RV) on a shared discharge header was included on the PPT. The workers were potentially exposed to an energy hazard through the common relief line header as a result of a parallel sodium meta-bisulphite pump remaining in service at the time of the work. | The apparent cause was that workers failed to realize that the overpressure relief line was part of a common relief header due to which it was not isolated. The other cause was inadequate work protection method used as the number of items required to be isolated exceeded the bounds of the PPT procedure. |  | 1 - For information only, configuration control, human error, industrial safety, tagging, work control | CM.2 , IS.1 , WM.1
WER ATL 17-0005 | 2016-10-14 | 2017-01-06 17:52 | Haiyang 1 | CA31 neutron shield block boron-silicone leakage event | Trending | During commissioning and while performing hot functional test (HFT) at normal operating pressure and temperature, a boron-silicone shield material leakage occurred from the neutron shield blocks mounted in a structural module surrounding the reactor vessel below the flange of reactor vessel. The station had received feedback on a similar event at another station. | The root cause was inadequate design. The primary technical cause was the thermal expansion and pressurization of the material inside the neutron shield blocks. The contributing cause was the high temperature stagnant air volume between the top of the neutron shield blocks and the permanent cavity seal ring and the elevated temperature observed in the nozzle gallery during HFT. |  | 2 - Important lessons, construction deficiency, design criteria / design basis, leak, operating experience, shielding | CM.1 , OE.1
WER ATL 17-0002 | 2016-05-27 | 2017-01-06 17:51 | Haiyang 1 | Foreign Material (FM) Intrusion into Passive Core Cooling System (PXS) valve | Trending | During commissioning and while performing line-up of the passive core cooling system valves, a valve was leaking internally. During the subsequent repair, foreign material of a bolt and a metal part was found at the valve seat, causing the valve damage. It resulted in 2 days suspension of the primary side work. | The direct cause was that the bolt from another work site accidentally fell into the pipeline and then was flushed into the seat. The root cause was deficiencies in risk awareness and preventions of FM. The contributors were inadequate inspection and risk identification related to cross work as well as weaknesses in flushing programme and condition report system. |  | 1 - For information only, bolt, emergency core cooling system, foreign material, leak, work control | ER.3 , MA.2

## Other
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 17-0045 | 2016-11-28 | 2017-01-31 06:01 | Hamaoka 3 | Identification of a foreign material inside the inert gas system pipe | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0044 | 2016-08-31 | 2017-01-31 05:50 | Ikata 2 | Cracking in residual heat removal system vent pipe | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0043 | 2016-04-08 | 2017-01-30 01:51 | Hamaoka 3 | Leakage of heavy oil from A-auxiliary boiler heavy oil flow meter inlet strainer | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0035 | 2016-08-20 | 2017-01-25 20:24 | Shin-Wolsong 2 | Generator Power Reduction by Control Failure of Normal Drain Valve of High Pressure Feedwater Heater | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0034 | 2016-11-11 | 2017-01-25 20:16 | Kori 3 | Overload Trip of Air Compressor in Operation in Kori Unit 3 | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0033 | 2016-10-22 | 2017-01-25 20:05 | Kori 1 | High Pressure Turbine Control Valve #4 Closed Abnormally | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0032 | 2016-10-09 | 2017-01-25 21:02 | Kori 4 | Failure of AAC DG Governor Digital Controller | Other | See summary below. | See causes below.. |  | 2 - Important lessons
WER TYO 17-0030 | 2016-12-28 | 2017-01-25 18:33 | Hanbit 3 | Power Reduction after Supplementing Makeup Fluid to the Volume Control Tank of Chemical and Volume Control System | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0026 | 2016-09-01 | 2017-01-18 04:56 | Chasnupp 2 | Identification of Inappropriate Rated Current Settings Implemented at Breaker of Distribution Room Air Exhaust Fan | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0025 | 2016-09-25 | 2017-01-18 01:55 | Fuqing 6 | 6RS (Unit 6 reactor building interior structure) interior structure-6.70 m plate R1400 & R1403 wall joint bars deviation | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER TYO 17-0024 | 2016-10-27 | 2017-01-18 00:48 | Tokai 2 | INCREASE IN SFP WATER CONDUCTIVITY | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0020 | 2016-08-08 | 2017-01-17 00:46 | Changjiang 1 | Loss of formal water supply due to broken fresh water plant raw water intake pipeline | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0018 | 2016-04-06 | 2017-01-16 20:05 | Hamaoka 3 | Leakage of heavy oil from A-auxiliary boiler heavy oil automatic pressure reducing valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0017 | 2016-02-13 | 2017-01-16 19:50 | Kashiwazaki Kariwa 7 | Entry of foreign material during the modification work of condensate makeup water system piping | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0014 | 2016-02-25 | 2017-01-13 03:00 | Fuqing 3 | Repeated maintenance of seashell catcher and persistent triggering of high differential pressure alarm in essential service water system | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0013 | 2016-04-17 | 2017-01-13 01:59 | Fuqing 1 | The support under condensate fine treatment system (ATE) catcher is broken and resin catcher outlet pipe support lacks fixing blots | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0012 | 2016-05-27 | 2017-01-13 00:58 | Fuqing 3 | Damage of supporting bearings #7 and 8 of the generator in Unit 3 during bushing turning for times | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0009 | 2016-04-24 | 2017-01-11 21:09 | Qinshan 3 2 | Post-maintenance test could not be carried out due to power source failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0006 | 2016-09-20 | 2017-01-10 02:37 | Qinshan 3 2 | Failure of O-ring in the male quick union for the fuelling machine ram tail pipe led to heavy water leakage | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0005 | 2016-04-17 | 2017-01-10 01:14 | Qinshan 3 1 | Fan post-maintenance test failed multiple times | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0004 | 2016-03-12 | 2017-01-10 00:04 | Fangjiashan 1 | Unauthorized relocation of equipment by the contractor's personnel led to triggering of high circulating water level alarm in the main control room | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0003 | 2016-07-22 | 2017-01-09 21:49 | Fangjiashan 2 | Skipping of procedural step caused excessive concentration of sodium in the steam generator blowdown | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 17-0001 | 2016-10-09 | 2017-01-06 02:12 | Qinshan 2 4 | Retest of motor failed due to high temperature of bearing | Other | Se summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0048 | 2016-10-16 | 2017-01-31 09:13 | Heysham B2 | An Issue in Management and Control of Statutory Outage Cooling Water isolation | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0044 | 2016-05-24 | 2017-01-30 08:25 | Tricastin 2 | Insufficienct Space between containment spray system valve and safety injection system line | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0037 | 2016-05-06 | 2017-01-24 07:09 | Paluel 1 | Internal exposure below the dose evaluation threshold value for 4 workers setting up a contamination chamber | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0027 | 2016-07-03 | 2017-01-19 05:52 | Hongyanhe 4 | Safety valve releasing and damage Due delayed Filter replacement | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0025 | 2016-08-03 | 2017-01-19 03:51 | Hongyanhe 2 | Repeated occurance of alternator low stator cooling water flow | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0022 | 2016-05-04 | 2017-01-14 10:32 | Cruas 4 | Long-term contract worker exposed to an equivalent dose rate of more than 2 mSv/h without authorization | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0020 | 2016-06-22 | 2017-01-11 06:06 | Ningde 1 | Floodlight fire in Waste Auxiliary Building | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0018 | 2016-06-11 | 2017-01-10 10:05 | Hunterston B 2 | Main Boiler Feed Pump 8 tripped during testing | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0017 | 2016-02-02 | 2017-01-10 07:33 | Hinkley Point B2 | Cooling Water Pump 9 automatic shutdown following increased plant vibration levels in the Interconnector pit | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0016 | 2016-01-19 | 2017-01-10 06:58 | Hinkley Point B1 | High Condenser back pressure alarm on Turbine 7 due to fretted pipework | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0015 | 2016-07-23 | 2017-01-06 09:57 | Ningde 3 | Significant leak rate experienced during Containment Pressure Test | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0013 | 2016-08-28 | 2017-01-06 04:48 | Hunterston B 2 | Instrument Air supply found isolated to Turbine Generator 8 chloride protection valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0012 | 2016-08-22 | 2017-01-06 03:47 | Heysham B2 | Manhole Cover Fallen into Inspection Chamber | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0008 | 2016-09-22 | 2017-01-04 10:33 | Ningde 1 | Delayed Boron Concentration Analysis after Make-up of Spent Fuel Pool | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 17-0002 | 2016-12-30 | 2017-01-16 07:08 | Daya Bay 2 | Condensate Extraction Pump Tripped due to a Pressure switch Failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 17-0014 | 2016-10-05 | 2017-01-21 22:28 | Tianwan-2 | Breach of Welding Procedure Qualification Report during Welding | Other | During the 9threfueling outage of Unit 2, a contractorwas responsible for restoration on the sealing surface of bypass valve and inner wall of muffler at the outlet of valve seat. On October 4, the welder of this contractor provided overlaying and restoration regarding the erosion defects on the inner wall of muffler of bypass valve. Quality Assurance personnel found during onsite observation that the current of welding machine showed 172A. However, the Welding Procedure Qualification Report in thework document package required the welding current to be 150A, so there was discrepancy between actual value and specified value. QA personnel asked the welder to stop work at that time and start their work again after finding out the cause. | Direct cause: The interface engineer didn’t check the work documents adequately. Root cause: The interface engineer was notfamiliar with the management procedure Management of Welding Activity, and violated the procedure. Contributor: The qualification recording personnel filled in with erroneous current parameter. |  | 1 - For information only
WER MOW 17-0009 | 2016-10-14 | 2017-01-18 22:46 | Temelin-2 | Actuation of a Limitation System after the Loss of Condensate Pump due to Incorrect Manipulation | Other | Unit operated in Mode 1 at approx. 5.5% power level. In checking the displays, it was found that the feed-water tank make-up valve node is in manual mode. A command entered to change the mode to automatic (AUT). Upon the execution of this command, open valves at the condensate pipeline to gas strippers turned closed, and the limitation system (LS) actuated based on the “no condensate pump is working” signal. | The direct cause of this event was the human factor in the operating personnel performance: not thought out manipulating with the valves at the condensate pipeline to gas strippers; The root causes: insufficient self-check, ineffective independent check, not using the procedures. Human factor in the operating personnel performance contributed as follows: even-numbered valves instead of odd valves were opened; failure to identify the misposition of valves when putting the feedwater tank heating into service, failure to identify the misposition of valves during the shift turnover or in checking the displays. Other contributing factors: confusing graphics on the feedwater tank displays - incorrectly marked valves with the AUT/MAN mode option, deficiencies in the operating procedures - insufficiently defined positions of valves at the condensate pipeline to gas strippers. |  | 1 - For information only
WER MOW 17-0001 | 2016-09-30 | 2017-01-08 22:53 | Tianwan-2 | The grounding indicators were inconsistent with MCR display | Other | When energizing Unit 2 6kV A train bus cable on 30 Dep., 2016, the site operator opened grounding switch 2BBA05, 2BBA16 but grounding switches of cabinets 2BBA05, 2BBA16 were indicated in closing position on MCR display. The grounding indicators of 2BBA05, 2BBA16 were inconsistent with MCR display. | Direct cause: The installation angle of grounding switch actuater hexagonal pole auxiliary contact point stop block was not right. Root cause: 1. There were problems in training of 6kv switchgear cabinet maintenance for contractors’ workers. 2. The description of replacing aluminum castings was unclear in 6kv Switchgear Cabinets Maintenance Procedure and no requests to verify feedback signals after recovery. Contributors: Hexagonal position-supporting stop block was being dismantled without marking installation angle during replacing grounding switch aluminum casting |  | 1 - For information only
WER ATL 17-0136 | 2017-01-08 | 2017-01-31 10:54 | Cernavoda 1 | SDS#1 channel F spuriously tripped on low neutron power signal due to repetitive failure of EMI filters in signal amplifiers | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0135 | 2016-12-22 | 2017-01-31 10:51 | Cernavoda 1 | Fan motor 1-38310-FM90 was incorrectly connected after maintenance (rework) | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0134 | 2016-12-14 | 2017-01-31 10:49 | Cernavoda 1 | Low air pressure at instrument air stations in Reactor Building and Nuclear Services Building | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0133 | 2016-11-22 | 2017-01-31 10:48 | Cernavoda 1 | Decreased level in gadolinium tank 1-3271-TK3 due to leaks through valve 1-3271-PV16 | Other | See summary below. | see causes below. |  | 1 - For information only
WER ATL 17-0131 | 2016-10-08 01:12 | 2017-01-30 18:33 | North Anna 1 | Leak on Buried Service Water to Auxiliary Feed Water Suction Line | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0130 | 2016-10-15 07:40 | 2017-01-30 18:30 | Cooper 1 | Lost Time Injury - Pulled Calf Muscle | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0128 | 2016-10-01 04:20 | 2017-01-30 18:24 | Braidwood 1 | Inadequate Clearance Order Results in Gas Found in Chemical Volume Control System | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0127 | 2016-12-30 | 2017-01-30 18:09 | Darlington 1 | Current Environmental Qualification Temperature Envelope maybe affected by Existing Powerhouse Heating Steam Lines | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0126 | 2016-07-26 | 2017-01-30 18:08 | Darlington 4 | Administrative limit exceeded during Shim Mode Commissioning Test | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 17-0125 | 2016-08-31 | 2017-01-30 17:59 | Bruce A 1 | Secondary Guarding Results in Generator Stator Cooling Water Pump Motor Failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0124 | 2016-11-16 | 2017-01-30 17:57 | Bruce A 4 | Lessons Learned from Unit 4 Derate Due To Condenser Tube Leak | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0122 | 2016-12-27 | 2017-01-30 17:54 | Bruce A 1 | Unit 1 Derated Due to Fuelling Risk With Two of Three Trolleys Out of Service | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0117 | 2016-12-10 | 2017-01-27 18:14 | Bruce B 7 | Unit 7 Loose terminal connection on potential transformer during planned outage | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0113 | 2015-09-29 15:25 | 2017-01-27 07:39 | Fitzpatrick 1 | Power Was Found On a Fire Alarm Circuit during a Live-Dead-Live Check | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0112 | 2015-10-14 16:06 | 2017-01-27 07:29 | Diablo Canyon 2 | Pipe Rupture Restraint Coupling Found Completely Unthreaded on Main Steam Lead | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0110 | 2016-10-08 11:19 | 2017-01-25 20:07 | Vogtle 2 | Inclement Weather Causes Grid Instability and Unplanned Load Reduction | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0109 | 2015-10-28 14:16 | 2017-01-25 20:02 | Susquehanna 2 | Downpower Due to Grid Instability | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0106 | 2016-12-05 | 2017-01-25 19:47 | Laguna Verde 2 | Reactor Protection System actuation signal due to short period during cold shutdown conditions | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0101 | 2016-10-17 17:49 | 2017-01-24 14:27 | North Anna 1 | Failure of Shaft Sleeve O-Ring on High Pressure Heater Drain Pump | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0096 | 2016-08-02 16:09 | 2017-01-24 13:21 | Prairie Island 1 | Print and Work Plan Error Resulted in Level 2 Tagging Error | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0088 | 2016-09-13 12:30 | 2017-01-24 10:49 | Clinton 1 | A Loaded Dry Cask Multi-Purpose Canister Oriented 90 Degrees Off | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0087 | 2016-08-06 08:10 | 2017-01-24 10:45 | Arkansas Nuclear One 1 | Chemical Addition System Unable to Supply Biocide Due to Empty Temporary Tanker Truck | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0084 | 2017-01-07 | 2017-01-24 10:06 | Point Lepreau 1 | Operator Error Occurred when Manually Manipulating the Fuelling Machine Bridge | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0082 | 2015-11-28 | 2017-01-20 12:47 | Sequoyah 1 | Supplemental Radiation Worker Receives Unanticipated Dose Rate Alarm While Helping Move Trash | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0076 | 2016-12-04 | 2017-01-20 12:23 | Bruce B 7 | Shutdown System 1 trip after Moderator Pump start at end of planned outage | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0071 | 2016-09-27 02:43 | 2017-01-20 07:49 | Harris 1 | Motor Operator Casing Failure of Emergency Service Water Main Reservoir Intake Valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0069 | 2016-11-08 13:00 | 2017-01-20 07:44 | Seabrook 1 | Small Fire in Switchyard during Plasma Cutting Evolution | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0068 | 2016-10-12 | 2017-01-20 07:38 | Prairie Island 1 | Power Found During Work on Water Treatment | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0067 | 2016-10-24 17:40 | 2017-01-20 07:30 | Monticello 1 | Unexpected Auto Start of Emergency Diesel Generator Emergency Service Water Pump | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0064 | 2016-10-18 | 2017-01-20 07:13 | Hope Creek 1 | Breaker Discovered Out of Required Position per Clearance Document | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0062 | 2016-12-15 | 2017-01-17 19:42 | Bruce B 5 | Moderator Temperature Control Valve margins | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0058 | 2016-10-18 06:24 | 2017-01-13 18:48 | St. Lucie 1 | Ground Test Device Inadvertently Left Installed On Switchgear Feeder Breaker | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0054 | 2016-06-05 05:06 | 2017-01-13 18:36 | River Bend 1 | Reactor Water Clean Up Isolation on High Differential Flow Due to Equipment Misposition | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0048 | 2016-07-05 03:32 | 2017-01-13 18:25 | Mcguire 2 | Multiple Annunciator Alarms upon a Power Supply Failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0047 | 2016-04-03 00:15 | 2017-01-13 18:23 | Mcguire 1 | The Breaker For a Refueling Water Storage Tank Supply Valve Was Discovered to be Open | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0046 | 2016-03-05 | 2017-01-13 18:22 | LaSalle 1 | Refueling Outage Critical Path Delay Due to Reactor Recirculation Pump Coupling Fit Issue | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0044 | 2016-09-13 22:59 | 2017-01-13 18:19 | Grand Gulf 1 | Incorrect Body to Bonnet Studs Installed on a Containment Isolation Valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0043 | 2016-03-01 17:02 | 2017-01-13 18:17 | Fitzpatrick 1 | Inaccurate Risk Assessment on Scheduled Work | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0041 | 2016-10-08 | 2017-01-13 18:14 | Duane Arnold 1 | Main Steam Isolation Valve Failed Local Leak Rate Testing (LLRT) | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0040 | 2016-09-16 17:10 | 2017-01-13 18:12 | Davis Besse 1 | Essential Electrical Busses Not Aligned to Power Operations Transformers during Plant Startup | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0036 | 2016-11-27 | 2017-01-13 17:57 | Pickering A1 | End Shield Cooling Filter Clamp Failure During Post-Maintenance Pressurization Resulted in Unavailability of the Mechanical Filter and Cooling Water Leak Inside The Brick Housing | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0035 | 2016-10-01 | 2017-01-13 17:50 | Pickering A1 | Failure of Pickering Support Facilities 4KV Distribution System Resulted in Power Outage | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0033 | 2016-12-10 | 2017-01-12 13:05 | Chalk River NRU 1 | Incorrect Alarm Set Point | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0032 | 2015-12-18 10:00 | 2017-01-12 13:03 | Virgil C. Summer 2 | Supplier's Failure to have an adequate Program In Place that meets The Requirements for Identifying Non-conforming Materials, Parts or Components | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 17-0031 | 2015-02-17 09:00 | 2017-01-12 12:50 | Virgil C. Summer 2 | Containment Vessel Bottom Head Core Drilling Incident | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 17-0030 | 2015-01-26 10:00 | 2017-01-12 12:44 | Virgil C. Summer 2 | Personnel Access Data System Usage During New Plant Construction | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 17-0029 | 2014-05-02 09:00 | 2017-01-12 12:39 | Virgil C. Summer 2 | Hardened Foamy Concrete Found Adjacent to Containment Vessel Bottom Head | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0028 | 2015-10-02 09:00 | 2017-01-12 08:58 | Virgil C. Summer 2 | Storm response Lessons Learned - 1000 year Flood Event | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0027 | 2015-02-25 08:00 | 2017-01-12 08:51 | Virgil C. Summer 2 | Improper Wastewater Tie-in to Existing Sewer line | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0026 | 2014-03-04 | 2017-01-12 08:23 | Virgil C. Summer 2 | Adverse Trend Identified in Site Welding Quality and Procedures | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0025 | 2012-08-10 15:00 | 2017-01-12 08:16 | Virgil C. Summer 2 | Sub-Contractor Fitness for Duty (FFD) Policy Violation as defined in 10 CFR 26.719(b)(2)(ii) | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0024 | 2016-10-14 | 2017-01-10 08:53 | Virgil C. Summer 1 | Floor Drain Orifices Became Inadequate Steam Pressure Isolation Boundaries Due To Improperly Planned and Reviewed Work Orders | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0021 | 2016-10-04 00:46 | 2017-01-10 08:43 | Harris 1 | Failure of Reactor Makeup Water Pump Rotor | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0020 | 2016-10-10 10:00 | 2017-01-10 07:27 | Duane Arnold 1 | Main Steam Valve Drain Failed Local Leak Rate Testing | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0018 | 2016-09-27 08:00 | 2017-01-10 07:22 | Calvert Cliffs 1 | Electrical Tagging Boundries Inadequate during Emergency Diesel Tagout | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0017 | 2016-09-12 08:00 | 2017-01-10 07:21 | Calvert Cliffs 2 | Tagging Boundries Inadequate during Boric Acid System Tagout | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0016 | 2016-10-08 16:24 | 2017-01-10 07:20 | Brunswick 1 | Storm-Related Grid Instability Results in Unplanned Dual-Unit Downpower | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0006 | 2016-10-28 | 2017-01-06 17:53 | Haiyang 1 | Reactor Coolant Pump (RCP) 2B failed to operate at 100% speed when at the plateau of 292℃ | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0004 | 2016-10-09 | 2017-01-06 17:52 | Haiyang 1 | High-Vibration Happened on Automatic Depressurization System (ADS) B and D Train Pipe During Hot Functional Testing | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0003 | 2016-10-06 | 2017-01-06 17:51 | Haiyang 1 | Abnormal condition of pressurizer safety relief valve during unit 1 hot functional testing {HFT) | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 17-0001 | 2016-05-25 | 2017-01-06 17:50 | Haiyang 1 | Foreign Material (FM) Intrusion into Plate-type Heat Exchanger of Haiyang Unit 1 Component Cooling Water System (CCS) | Other | See summary below. | See causes below. |  | 1 - For information only