Yury Shchelik

MA-03-YS-pr

# CURRENT MAINTENANCE OF VENTILATION UNIT

## SCOPE OF OBSERVATION

## Observation over the ventilation unit maintenance was performed in the controlled access area at presence of maintenance department manager in course of two hours. Maintenance was performed by contractor’s workers group of 3 people.

## OBSERVATIONS

- Maintenance documentation missed at work place in the controlled access zone of ventilation unit current maintenance. Absence of maintenance documentation can cause errors and/or low-quality maintenance of equipment. (MA-03-YS-01-pr)

- One worker was seen to wear rubber gloves, while two other workers wore cotton gloves. One of the workers was seen to take off the gloves to perform some actions. Section “the applied personal protective equipment” fails to describe specific requirements on appliance of personnel protective equipment for hands. Uncertainties in specification of personnel protective equipment can cause injuries.  (MA-03-YS-02-pr)

- Two workers were seen to leave the work zone for about 15 minutes in course of ventilation unit maintenance in the controlled access area. The foreman explained, that the workers went to get longer push-up bolts for a replacer. Failure to properly prepare the needed tool can speak for poor maintenance arrangement. (MA-03-YS-03-pr)

- A worker was observed to use an open-end wrench instead of a standard device to turn the spindle in course of ventilation unit maintenance in the controlled access area. This can result in personnel injury and/or equipment damage. (MA-03-YS-04-pr)

- Workers failed to use pallets to store the tool and the dismantled fasteners in course of maintenance of ventilation unit. The workers placed fasteners on the equipment and on the floor. It can cause loss and/or damage of fasteners, moreover personnel injury. (MA-03-YS-05-pr)

- A worker was seen to use unspecialized (mountain skiing) glasses with a frame, which is hard to remove, in course of ventilation unit maintenance performance. It can cause unreasonable personnel exposure and worker’s eyes injury. (MA-03-YS-06-pr)

- The dismantled details (fixture, joint), replacers (3), polyethylene film etc. were seen placed on the floor of the controlled access area of ventilation unit maintenance. Failure to appropriately place the dismantled equipment and tools can cause personnel injury. (MA-03-YS-07-pr)

- The technological manual on maintenance of Ц4-70 type ventilator (NPP 0148 ДК) (approved in 1999) does not determine the appropriate tool and replacer for the ventilator wheel dismantling. Besides that, the manual contains links to the revoked regulatory documents. Failure to provide distinct instructions in documentation and to timely update it can cause errors and low-quality maintenance of equipment. (MA-03-YS-08-pr)

- Failure to connect input power to radiation level indicator of small parts (power cord was seen not connected) in personnel airlock on the third floor. This observation was brought to the attention of radiation safety service shift supervisor. However, after two hours the radiation level indicator remained unavailable, fault cause information table was missing.  This fact can speak for the personnel low bias to early identification and addressing the problems, associated with equipment operation. (MA-03-YS-09-pr)