s

ISLAMIC REPUBLIC OF IRAN

IRAN NUCLEAR REGULATORY AUTHORITY

NATIONAL NUCLEAR SAFETY DEPARTMENT

Report on Review and Assessment of

Seismic Probabilistic Safety Analysis (PSA) of

"Bushehr-2 NPP unit 2"

(Revision B01)

Doc. No.: NS-RT-053-21/02-0-Feb.2022

Tehran I.R. IRAN

فهرست دریافت کنندگان

| ردیف | دریافت کننده |
| --- | --- |
| 1 | شركت توليد و توسعه انرژي اتمي ایران |
| 2 | دفتر ايمني هسته‌اي |
| 3 | گروه ارزيابي ايمني هسته‌اي |
| 4 | مركز اسناد دفتر ايمني هسته‌اي |
| 5 |  |

Table of content

Subject                                                                                                 Page No

1. INTRODUCTION …………………….…………….…......……………………………... 2

2. COMMENTS ...……………………….…………….…......………………………….……3

- 2.1 General Comments …………………………………...…......……………………….…... 3

- 2.2 Detailed Comments Related to Each Individual Item ……..........……...……..……......... 5

3. REFERENCES ..…………………………………………....……..……………………… 44

- INTRODUCTION

This report contains the results of the NNSD review and assessment of 6 volumes of “Seismic Probabilistic Safety Analysis (PSA)” of Bushehr-2 NPP unit 2, Revision B01, issued in 2019.

The related IAEA requirements and recommendations (as listed below) and also the requirements mentioned in Russian documents that are listed in Appendix M to the Contract served as assessment criteria during the review:

- IAEA Safety Guide No. SSG-3, “Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants”, 2010

- IAEA TECDOC Series No. 1511, “Determining the Quality of Probabilistic Safety Assessment (PSA) for Applications in Nuclear Power Plants”, 2006

2. COMMENTS

2.1 General Comments

- Some parts of the submitted documents do not have enough descriptions (e.g. Book 3, sections 1.4.1 and 1.4.2 regarding the used time history records in calculation of probabilistic response spectra). Some other parts of the submitted documents have referred to PSAR without identifying the related chapter and sections. It is required to develop and submit more detail descriptions of engineering considerations that were implemented in BNPP-2 SPSA elements. Alternatively, it is needed to provide clear cross-references to the resources that contain relevant descriptions that are not mentioned in the SPSA books (include BNPP-2 PSAR sections).

- Most of the presented figures do not have acceptable quality and their details are not legible (e.g. Figures 1.1.10-15, 1.1.2.1-4). These figures shall be substituted with the acceptable and qualified figures.

- There are not presented any considerations related to seismically induced fires, flooding and spurious actuation. It shall be provided engineering considerations of seismically induced fires, flooding and spurious actuation.

- Contents of SPSA books that are provided in Russian language do not match with the English version.

- Some VVER NPPs design requires Main Steamlines isolation in response to seismic events (to isolate seismically rugged NPP parts from the rest of plant SSCs). If this is also the case for BNPP-2, then such requirement shall be included in SPSA logic.

- Fragility analyses were taken from Akkuyu NPP with the justification that the analyses provide conservative bounding estimates for BNPP-2. The provided explanation is that ground Seismic Spectrum for Akkuyu NPP can be conservatively used as a bounding envelope for BNPP-2 (in the range with fundamental frequencies).  However, Akkuyu NPP design has 2 safety divisions while BNPP design has 4 divisions, that implies design differences. Therefore, it provides a description of differences and engineering justification of seismic response similarity of both plants. In addition, if the Akkuyu equipment fragilities were applied, one would expect that in BNPP 2, equipment with the same fragility would be installed, otherwise the results of the study are not valid.

- The documented SPSA results do not provide any insights for SFP (Spent Fuel Pool) and POSs (Plant Operating States) other than full power.

- The analysis of PSA results is totally missing; though this task is very important for the further steps of the plant design process. It shall be provided the engineering discussion on the insights gained from the results.

- In determination of fragility curves for structure, system and components, the methods and assumptions used to consider aging effects shall be described.

- There is no formula numbering in some sections of the submitted documents. It shall be added.

2.2 Detailed Comments Related to Each Individual Item

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 1 |
|  |  | Section Number | Book 2, Sec. 1.1 |
|  |  | Page | 2-38 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Equipment list completeness |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In section 1.1, the list of components for PSA for seismic was developed based on some principles but, in this list some components such as relays are not presented. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. SEL (Seismic Equipment List) completeness with engineering considerations, i.e. no relays were included shall be justified. Justification basis for equipment exclusions shall be also provided. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 2 |
|  |  | Section Number | Book 3, Sec. 1.1 |
|  |  | Page | 1-19 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Covering all buildings |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| As it is mentioned in Book 5 of SPSA, 20UJA, 20UKC, 20UMA, 21UBN-24UBN, 21UQC, 22UQC, 21UKZ-24UKZ, and 21UQZ, 22UQZ buildings are considered in Seismic PSA assessment but in this section, only seismic response analysis for 20UJA and 21-24UBN are presented. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The response analysis of other mentioned buildings shall be presented in this book. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 3 |
|  |  | Section Number | Book 3, Sec. 11 |
|  |  | Page | 1-last |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Incomplete results |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In fragility function development using factor method for calculation of strength factor, it is needed to calculate maximum stresses from normal and seismic loads but, it is not presented such results. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The maximum stresses from normal and seismic loads for all buildings shall be presented. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 4 |
|  |  | Section Number | Book 5, Sec. 1.3.1 |
|  |  | Page | 10 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Incomplete referral |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| It is mentioned in this section: “The failure criteria were selected proceeding from the design seismic resistance criteria given in Chapter 3 PSAR.”. But it is not determined which criteria the author means. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. Failure criteria shall be determined and described with more details. If the author wants to determine them by referring to Chapter 3 PSAR, it shall be determined related criteria and related section in PSAR precisely. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 5 |
|  |  | Section Number | Book 5, Sec. 2.1.1.1 |
|  |  | Page | 12 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Incomplete referral |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “It is important to note that, according to SP 16.13330.2011, the critical to design load ratio for rod structures calculated as spatial systems with the use of certified computing systems shall not be less than the system stability safety factor γs = 1.3. The safety factor equal to 1.3 is also adopted for the components of metal structures calculated for strength according to ultimate stress.” |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It has some confusing expressions such as the critical to design load ratio, rod structures, certified computing systems, metal structures, and ultimate stress. The mentioned expressions shall be checked and be used technical expressions C2. SP 16.13330.2011 has been used in this statement but it is not written in the reference list. It shall be added to the reference list. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 6 |
|  |  | Section Number | Book 5, Sec. 2.1.1.1 |
|  |  | Page | 12 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Incomplete reference |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “The standardized values of material strength parameters given in SNiPs (SP 63.13330.2012 & SP 16.13330.2011) have been determined proceeding from the normal distribution law with the confidence probability of exceeding no less than 95 %.” |  |  |  |
| 2.2. Comments |  |  |  |
| In the above-mentioned paragraph, it has been used two different revisions of SP.63.13330.2011 & 2012. What is the difference between these two revisions of SP.63.13330? There are some confusing expressions such as normal distribution law and confidence probability exceeding. It seems these parts of the report have some translational problems. C1. The mentioned expression shall be checked and be used technical expressions. C2. It shall be described which revision of SP.63.13330 has been used. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 7 |
|  |  | Section Number | Book 5, Sec. 2.1.1.1 |
|  |  | Page | 12 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Determination of references |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “The standardized concrete strength variation value that is statistical average for a number of concrete manufacturing works has been taken equal to 0.135 – under compression, 0.18 – under tension. The standardized reinforcement strength variation value that is average for a number of metallurgical plants has been taken equal to 0.102.” |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It has not been determined any references for the presented values. The references for presented values shall be determined. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 8 |
|  |  | Section Number | Book 5, Sec. 2.1.1.1 |
|  |  | Page | 12 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Determination of references |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “For the normal distribution law, the median values of strength parameters Rmed can be expressed in terms of the design values of strength parameters R using the following formulas:” |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be determined reference for used formula in the report. C2. It shall be determined the existing variables in the formula. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 9 |
|  |  | Section Number | Book 5, Sec. 2.1.1 |
|  |  | Page | 12-14 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Strength factor determination methodology |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Two major considerations are involved in determination of the ultimate strengths of individual structural elements. One is the definition of the strengths of the materials composing the members. The other is the determination of the ultimate strength capacities of the structural members given the type of loading, material strength, member configuration, etc. In the used methodology for determining strength factor, only strengths of the materials are considered and ultimate strength capacities of the structural members are not considered. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. Ultimate strength capacities of the structural members shall be considered in determining strength factor. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 10 |
|  |  | Section Number | Book 5, Sec. 2.1.2.1 |
|  |  | Page | 14 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Inconsistency with Reference |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In Table 2.1.2.1, Standard values of the factors (Fμ) are presented. Its reference is TABLE III.2 of IAEA safety series No. 28. The used technical expressions in these two tables are not consistent. Addressing the used data from mentioned reference is not enough. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned inconsistency in issue description section shall be modified by reference. C2. It shall be referred the used table with more details. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 11 |
|  |  | Section Number | Book 5, Sec. 2.1.3.1 |
|  |  | Page | 15 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Unclear curve |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Figure 2.1.3.1 shows two different curves. There are some descriptions about these two curves in sentences presented in this section but, it is not clear what are these two curves. The shown guide beside curve is not clear, as well. The reference of the presented response spectra curves is not specified. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. More explanation shall be presented in this section. Curve guide shall be described in the presented text. C2. Specific location of the presented response spectra curves shall be specified. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 12 |
|  |  | Section Number | Book 5, Sec. 2.1.4 |
|  |  | Page | 15 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | ground motion incoherence factor data |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, the reduction coefficients are presented based on reference 4. By observing mentioned reference, there is not such information in the mentioned reference. Because of the mentioned reason, this section is not reviewable. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The section which the reduction coefficients are extracted from shall be specified. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 13 |
|  |  | Section Number | Book 5, Sec. 2.2.2 |
|  |  | Page | 18 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Strength factor determination |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In determination of strength factor, failure modes of structure will be determined at first. Based on the specified failure modes, dominant failure mode will be determined and finally, strength factor will be determined based on dominant failure mode. In the presented information in this section, failure modes are not determined. There are not any calculations for determining strength of structure for failure modes. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The requested information in issue description section, shall be presented in strength factor calculation section for all buildings. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 14 |
|  |  | Section Number | Book 5, Sec. 2.2.4.1 |
|  |  | Page | 25 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Building 20UJA seismic fragility assessment results |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, fragility development results for 20UJA building are presented. In table 2.2.4.1, fragility parameters are presented for 3 failure modes but in the previous section (2.2.3), calculation are done for only 1 failure mode. More description is needed to be presented in this section or in the previous section. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned parameters in issue description section shall be presented. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 15 |
|  |  | Section Number | Book 5, Sec. 3.1.1 |
|  |  | Page | 47 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Introducing used variables |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, two formula are presented for controlling stress in equipment which shown below: and There is not given any information regarding σ, σ1 and σ2. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be introduced variables σ, σ1 and σ2 in this section. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 16 |
|  |  | Section Number | Book 5, Sec. 3.1.1 |
|  |  | Page | 48 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Formula assumption |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| To derive the formula, it is assumed that the strength factor will reach its minimal value when the stresses caused by seismic loads are the main contributor to the stressed and strain state (SSS) of equipment and pipeline components. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The above-mentioned assumption or claim shall be proved. C2. The used variables shall be introduced. C3. The given formula shall be numbered. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 17 |
|  |  | Section Number | Book 5, Sec. 3.1.1 |
|  |  | Page | 47 - 48 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Strength factor calculation |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In calculation of strength factor, two groups of reduced stresses have been used. There is no information about these two groups. To determine the capacity median value of the second group of reduced stresses, the coefficient 1.3 has been used. The reference for using this value is not specified. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The two groups of reduced stresses shall be explained. C2. The used coefficient reference shall be specified. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 18 |
|  |  | Section Number | Book 5, Sec. 3.1.7 |
|  |  | Page | 51 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Strength factor calculation |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “3.1.7.1 According to PNAE G-7-002-86, in calculating the equipment, the seismic load components are added according to the method of calculating the square root from the sum of squares (SQRSS).” The method of SQRSS is generally used for combination of vibration modes and is not used for combination of seismic load components. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be justified that the used method for combination of seismic load components is acceptable based on the valid standards. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 19 |
|  |  | Section Number | Book 5, Sec. 3.2.1 |
|  |  | Page | 51 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Using Akkuyu NPP data |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “In figure 3.2.1.1 for comparison, horizontal envelope response spectra (2 % dampening) are shown for SSE at the elevation of the reactor plant for Unit 2 and 3 of the Bushehr-2 NPP and units 1-4 of the Akkuyu NPP.” Because the Akkuyu NPP response spectra are not available to NNSD, it is not possible to verify the presented data. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The presented data of Akkuyu NPP shall become available to NNSD for verification. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 20 |
|  |  | Section Number | Book 5, Sec. 3.2.1 |
|  |  | Page | 51 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Reference of the presented data |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “The lowest natural vibration frequencies of the reactor coolant circuit (RCC) equipment are summarized in table 3.2.1.1.” The reference for calculation of the lowest natural vibration frequencies of the equipment is not presented. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The calculation report or reference for the lowest natural vibration frequencies of the equipment shall be provided. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 21 |
|  |  | Section Number | Book 5, Sec. 3.2.2 |
|  |  | Page | 53 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Lack of calculations or reference |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, it is presented some values for forces and stresses without determining calculations or references. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The calculation report or reference for the given data shall be presented or specified. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 22 |
|  |  | Section Number | Book 5, Sec. 3.7.1.1 |
|  |  | Page | 73 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Undetermined acronym |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “3.7.1.1 The ITRs for valves to be used for the Bushehr-2 NPP have been developed in accordance with the document NP-068-05 “Pipeline Valves for Nuclear Power Plants.”’ It is the first time, ITR is used in the document. It is not clear this acronym stands for which term. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be specified that ITR stands for which words. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 23 |
|  |  | Section Number | Book 5, Sec. 3.9.2.1 |
|  |  | Page | 82 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Reference of the presented data |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “According to the results obtained from the design calculations of electrical and electromechanical equipment carried out for the similar designs of NPPs equipped with VVER reactors, the lowest safety margin is found in the welded and/or bolted connections through which the equipment is attached to its pedestal.” In this section, it is referred to the similar designs of NPPs equipped with VVER reactors without determining any reference. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be specified the used reference, as mentioned in issue description section. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 24 |
|  |  | Section Number | Book 5, Sec. 4 |
|  |  | Page | 94 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | completeness of fragility analysis |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| The documented set of fragility analyses is available for a subset of BNPP SSCs. The list is short since it is compared with the items listed in current Preliminary SEL. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be provided engineering considerations justifying completeness of fragility analysis scope. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 25 |
|  |  | Section Number | Book 5, Sec. 4 |
|  |  | Page | 94 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Title of the section |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| The title of this section is “NPP COMPONENRS’ SEISMIC FRAGILITY ASSESSMENT RESULTS”. It seems it means “NPP components’ seismic fragility assessment results” which have two problems: - Componer is a spelling mistake. - In subsection 4.1, results for building and structures are presented, not for component. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned problems in issue description section shall be solved and corrected. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 26 |
|  |  | Section Number | Book 5, Sec. 4.2 |
|  |  | Page | 96 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Seismic fragility assessment results for the ground level |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, a factor (FH) was calculated and multiplied in median acceleration of fragility parameter for consideration of difference between SSE acceleration (0.44g) and acceleration value in ground (0.287g). Based on main formula in calculation of Am which is as following: Safety factor is multiplied to ASSE which is 0.44g then considering SSE acceleration as 0.44g increased Am based on 0.44g. Therefore, multiplication of Am to FH is wrong and it causes wrong results. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. Am in SSE level or ground level shall be used in fragility parameter calculation. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 27 |
|  |  | Section Number | Book 5, Sec. 5.1.1 |
|  |  | Page | 98 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Reference of the presented data |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “5.1.1 To determine the frequencies of potential initial events with leaks due to seismic events of JSC OKB Gidropress, calculations of conditional probabilities of formation of leaks and breaks (failures according to the criterion "Pipeline leakage") were performed. At this stage, the calculations were performed on the basis of generalized data and are subject to refinement.” In this section, it is referred to the calculations performed by JSC OKB Gidropress without determining/presenting any reference. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be presented the calculations, as mentioned in issue description section. The review of section 5.1.1 is not possible without presenting the mentioned calculations to NNSD. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 28 |
|  |  | Section Number | Book 5, Sec. 5.2 |
|  |  | Page | 103 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Seismic fragility assessment results for the ground level |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, a factor (FH) calculated and multiplied in median acceleration of fragility parameter for consideration of difference between SSE acceleration (0.44g) and acceleration value in ground (0.287g). Based on main formula in calculation of Am which is as following: Safety factor is multiplied to ASSE which is 0.44g then considering SSE acceleration as 0.44g increased Am based on 0.44g. Therefore, multiplication of Am to FH=1.98 is wrong and cause wrong results. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. Am in SSE level or ground level shall be used in fragility parameter calculation. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 29 |
|  |  | Section Number | Book 6, Sec. 1.1.1 |
|  |  | Page | 3 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Unclear expression |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “The target screening criterion for seismic failures of components for the second case was set to 5E-07 per year.” The term “second case” is not clear. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned term (second case) shall be defined. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 30 |
|  |  | Section Number | Book 6, Sec. 2.1.2.2 |
|  |  | Page | 9 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | seismically correlated equipment group failures |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Because earthquake affected a lot of components at once, considerations related to seismically correlated equipment group failures shall be noticed. Reviewer could not find such considerations in the submitted reports. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be provided engineering considerations related to seismically correlated equipment group failures. If they are not used, it shall be provided justification why are not used. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 31 |
|  |  | Section Number | Book 6, Sec. 1.3.1.1 |
|  |  | Page | 6 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Referring the wrong number to table |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “Their list is provided below in Table 2.3.2.” Table 2.3.2 does not exist and Table 1.3.2 is given in following. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. Numbering of Table 2.3.2 shall be corrected in the text to Table 1.3.2. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 32 |
|  |  | Section Number | Book 6, Sec. 1.3.2.1 |
|  |  | Page | 6 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Addressing the reference |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “Adopted values of PGAs provided in JSC OKB "Gidropress" studies…” It is not determined which studies the author means. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned studies shall be presented. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 33 |
|  |  | Section Number | Book 6, Sec. 2.1.2.2.1 |
|  |  | Page | 10-29 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Undetermined acronym |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In these pages, seismic event tree and transfer event trees are shown. These trees are not supported with explanation at all. The abbreviations in the event trees are not specified that stand for which words, as well. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. All of the presented event trees shall be explained. C2. It shall be specified that the abbreviations stand for which words. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 34 |
|  |  | Section Number | Book 6, Sec. 2.1.4 |
|  |  | Page | 283 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Reference specification |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section it is mentioned: “When selecting a method for the account of personnel actions during seismic events, the approach previously used by EPRI SPRA Guide in the development of a PSA for seismic events was used.”. “the approach of the Swiss Federal Nuclear Safety Inspectorate (ENSI) was used to perform personnel analysis. An approach is illustrated in Figure 2.1.4.1.” It is not specified the reference for mentioned EPRI SPRA Guide and Swiss Federal Nuclear Safety Inspectorate (ENSI). |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned references shall be specified and added in the reference section of document. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 35 |
|  |  | Section Number | Book 6, Sec. 2.1.2.2 |
|  |  | Page | 30 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Building failure consequence assumption |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| In this section, it is assumed that building-level seismic failures imply failures of all components located inside the buildings. Then building level seismic failures propagate into dominant cutsets. Such assumption is not realistic at all and it may produce wrong results. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be improved description of engineering considerations associated with seismically induced failure consequences of the plant SSCs where it is not self-evident. C2. It shall be provided engineering considerations/assurance justifying that building failures are the real seismic weak-links and that equipment inside the buildings is seismically more rugged than the buildings. C3. It shall be provided descriptions of building failure induced consequences i.e. list of components or functions failed when a building is seismically damaged. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 36 |
|  |  | Section Number | Book 6, Sec. 2.1.2.2 |
|  |  | Page | 210 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Manually consideration of CCF |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Referring to the pdf version of seismic PSA fault trees, there were noticed manually inserted CCF basic events right next to RiskSpec-automatically generated CCF fault trees for pumps and fans (e.g. Figure 2.1.2.2.264 – Fault tree JNA-007). |  |  |  |
| 2.2. Comments |  |  |  |
| C1. It shall be provided a justification for handling CCF events in fault trees in such a manner. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 37 |
|  |  | Section Number | Book 6, Sec. 2.1.3.2 & 2.2 |
|  |  | Page | 262, 292 & 293 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Interpretation of analysis results |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Spot checks of seismically induced failure probabilities revealed that different probability values were implemented to DGs. (compare Tables 2.1.3.2.1 and 2.2.1.1 items 17, 18, 19 and 23) |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned differences in issue description section shall be explained. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 38 |
|  |  | Section Number | Book 6, Sec. 2.2 |
|  |  | Page | 286 - 290 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Dominant accident sequences |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Table 2.2.1 gives the list of 100 minimal cutsets obtained for the overall seismic-induced core damage frequency. There is not presented any discussion and detail description about the result of this table. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. Description of dominant accident sequences (seismic cutsets) shall be significantly improved. Current results do not provide reasonably detail description of dominant seismic sequences. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

| ISSUE SHEET |  |  |  |
| --- | --- | --- | --- |
| 1. ISSUE IDENTIFICATION |  | Issue Number | 39 |
|  |  | Section Number | Book 6, Sec. 2.2 |
|  |  | Page | 286 - 290 |
| Facility | BUSHEHR-2 NPP UNIT 2 |  |  |
| Issue Title | Interpretation of analysis results |  |  |
| 2. ISSUE CLARIFICATION |  |  |  |
| 2.1. Issue Description |  |  |  |
| Observation of the 100 dominant cutsets (CDF) is confusing: seismic intervals (seismic initiating events) S1 trough S7 are represented by a single dominant cutset associated with RB failure, which leads directly to CD. Seismic intervals (seismic initiating events) S7 & S8 contain all the other cutset from the top 100. FV importance measure of seismically induced LOCA reveals that Compensable and Small LOCAs should represent together according to Table 2.2.1.1. (S8 >70%, S7 >25%) more than 95% fraction of CDF. However, among the top 100 CD sequences is not a single one cutset that would include LOCA scenario. |  |  |  |
| 2.2. Comments |  |  |  |
| C1. The mentioned confusion described in issue description section shall be explained. |  |  |  |
| 2.3. Recommendations |  |  |  |
| 2.4. References |  |  |  |

- REFERENCES

- IAEA Safety Guide No. SSG-3, “Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants”, 2010

- IAEA TECDOC Series No. 1511, “Determining the Quality of Probabilistic Safety Assessment (PSA) for Applications in Nuclear Power Plants”, 2006