NPP OSART Mission

Potential Weaknesses and Strengths

Maintenance Area

Note:

The following are based on limited information and perspective in the AIP, future verification and observation in the field is required.

Potential Weaknesses:

- Human Errors in Maintenance Activities, supported by several reportable events from the plant, the potential or actual consequence of these events are severe:

  - Essential 48V DC secondary charger switched off during signage removal (CR00757650)

  - The incorrect filters were discovered fitted to Centrifugal Charging Pump A lube oil system. Following an extent of condition review it has been subsequently identified that a number of additional filters related to Emergency Core Cooling System pump lube oil systems were also of the wrong filter type. (CR00803462)

  - During the calibration of the Trevitest equipment for the pre outage testing of main stream safety valves, an error was made in reading the dial test indicator associated with the Wykham Farrance load ring. This misreading resulted in incorrect data being used during the calibration which lead to the valves pressure being incorrectly set. (CR00808684)

  - The Loop 2 steam generator power operated relief valve (PORV) was reported to be feathering and the associated controller, was thought to be the cause. The controller was replaced and a post maintenance test completed to confirm the controller was working correctly in automatic control.

  - On the 26th September 2014 the routine surveillance was performed and it was found that the PORV could not be manually opened or closed from either the main control room or auxiliary shutdown room and the valve was subsequently declared as inoperable. Investigations identified that the manual closed button opened the PORV and the open button closed the PORV. (CR00901111)

  - During defect maintenance on power operated relief valve (PORV) 'C' an incorrect controller was installed. Once discovered, the PORV was declared inoperable. However it is believed that the valve was capable of performing its safety function at all times. (CR0000917680)

- Maintenance practices and quality of maintenance activity, several reportable events revealed that practices and quality of maintenance has a direct impact on the safe operation of the plant:

  - An alarm was received in the Main Control Room to indicate a low oil level for the Reactor Coolant Pump (RCP) D Motor Lower Bearing. The Reactor was shut down to investigate the cause of the low oil level alarm.(CR00744912)

  - Restraints on the 48v DC Main distribution battery unit for separation group 5, which are there to prevent damage in the event of a seismic event, were not secured adequately. (CR00780049)

  - A boric acid leak was found on a High Head Safety Injection test recirculation line. The repair was completed but during a surveillance test, the flow was found to be below the acceptance criteria. A temporary gauge was fitted, and the flow was found to be in tolerance. An investigation was carried out and the flow elements orifice was found to have been fitted in the incorrect orientation (180 degrees out). (CR00821091)

- PM overdue.

- The shaft driven lubrication oil pump was unable to provide the necessary lubricating oil to Emergency Charging Pump A and in the event of a Secondary Protection System initiation, the lack of lubricating oil could have led to a gearbox failure. This situation has been shown to exist since overhaul work on the shaft pump during May 2013. (CR00866361)

- Increase of non-outage defect inventory (station wide):  There is an increase trend of non-outage defect inventory for 7 months in the plant performance indicator, and the cumulative impact of the defects needs to be further explored.  It is at the bottom of fleet performance for this PI (no. 6 in the fleet).

Potential Strengths:

- Labelling for Seismic room identification: This room contains seismically qualified plant, equipment must not be left in this room unless assessed and approved in accordance with plant procedure.  Easy to identify and to maintain.

NPP OSART Mission

Potential Weaknesses and Strengths

Operating Experience Area

A review was performed of the Advanced Information Package for each functional area, as well as the Condition Reports (CR) initiated for the past two years.  It should be noted that this is a limited perspective based on the presentations and a cursory review of the condition reports provided or initiated by each functional area.

Potential Strengths:

- Key performance indicators - These appeared to be comprehensive and critical, with comparison provided not only to other plants within the utility, but also with the top industry decile for that measured area.

- Condition report initiation – The condition report initiation was good cross functionally with most department initiating condition reports for low level deficiencies, events and near misses.

Potential Weaknesses

- Aging workforce – A review of the data provided in the AIP package revealed that 280 out of 540 (52 percent) of plant workers are 46 years old or older.  However there did not appear to be a discussion on how the NPP plans to retain the knowledge of these individuals for future business continuity.

- Operations performance – A review of KPIs, and significant and reportable events has shown that Operations department performance is affecting regulatory compliance and plant reliability.  This was evident from several sources.  The first observation was that many of the operations’ department key performance indicators (KPI) tend to be in variance (worse) than the fleet average.  Many of the significant and reportable events and near misses appear to be operations performance related.   A review of condition report initiation shows an affinity to generate CRs for Equipment issues, but not necessarily for precursors to Operations events such as configuration control problems. (ref CR 00856952 – 1/15/2014, 00875930 – 1/5/2014 inhibited)  This could be indicative of a potential “chilling” effect.  The graph below shows a steady decline in the initiation of condition reports by the Operations department over the past year.

- Supplier performance program.  Based on the data provided, there does not appear to be a robust supplier performance process.  A review of the Condition Reports has shown that events, near misses and precursors to events regarding parts availability and plant reliability are occurring due to quality of parts issues, however, there did not appear to be a programmatic supplier performance or parts quality strategy in the condition report trends or AIP information.   (ref 00866361 – 6/3/2014)

- Obsolescence – A review of the engineering AIP information as well as the condition reports has shown that there does not appear to be a robust obsolescence process at the site.  Condition Reports are being written on obsolescence issues, however these issues appear to reflect a unified or comprehensive (or possibly not well supported) obsolescence process.  Condition reports are documenting situations in which obsolete parts are not being managed proactively, or that obsolete parts are not getting the right level of priority. (ref CR 0087593 – 1/15/2015 for example)

- Spare parts Availability – Numerous CRs have been written to document that critical spares were not available when needed.  Most of these were written by maintenance and appeared to be written at the time of work execution.  There are various reasons that the spare parts were not available, including a lack of an overall critical spares identification or stocking strategy, as well as a failure to stock those items previously identified as being critical to plant operations.

- Operating Experience Utilization – A review of the significant events and regulatory significant issues implied that there were weaknesses in the utilization of Operating Experience in the prevention of similar events at the plant.  It should be noted that this is a preliminary observation based on the lists of significant and regulatory related events provided by the NPP.

NPP OSART Mission

Potential Weaknesses and Strengths

Accident Management Area

The plant uses Station Operating Instructions (SOI) that are based on the generic Westinghouse Function Restoration Procedures. The Severe Accident Management strategies, however, were developed in-house and are unique to The plant, and differ significantly from the generic Westinghouse SAMGs.

Potential Weaknesses:

Severe Accident Management is implemented through a control room procedure (SOI-8.8) rather than through guidelines in the TSC. This inflexibility may lead to problems in severe accident situations.

SOI-8.8 does not give a high priority to keeping the SG tubes covered with water to prevent creep rupture of the SG tubes. The technical basis of SOI-8.8 considers creep rupture failure of the pressurizer surge line to be more probable. This goes against the intent of NS-G-2.15 paragraph 2.12 that severe accident management guidance should be developed irrespective of predicted frequencies of occurrence of the challenge.

Guidance for accidents in the Fuel Storage Pond is contained in SOI-5.13.4, but it is not clear how this would integrate with SOI-8.8 during a severe accident in the reactor. A clear hierarchy should exist that prioritises operator actions for a Fuel Storage Pond accident that coincides with a reactor accident.

There does not appear to be an entry condition into SOI-8.8 for shutdown plant states where the vessel head is removed/disconnected and core exit temperature is not available.

The operators are allowed to exit SOI-8.8 back to an earlier Station Operating Instruction (SOI, equivalent to the Westinghouse Function Restoration procedures). The IAEA guide NS-G-2.15 paragraph 3.40 recommends against this.

Two severe accident training courses (respectively ‘overview’ and ‘full level’) are in the process of being developed for TSC personnel. This raises a concern over the current level of knowledge and capabilities in the TSC to support the Control Room during a severe accident.

Potential Strengths:

Strong post-Fukushima response through the Japan Earthquake Response (JER) project that identified several plant modifications to improve severe accident management such as installation of PARs and tie-in points for mobile equipment.

Mobile equipment for severe accident mitigation is stored at a centralized off-site storage facility.