<!DOCTYPE html PUBLIC "-//W3C//DTD XHTML 1.0 Transitional//EN" "http://www.w3.org/TR/xhtml1/DTD/xhtml1-transitional.dtd">

<html xmlns="http://www.w3.org/1999/xhtml">

<head id="ctl00_Head1">

<script type="text/javascript">

function CopyToClipBoard() {

var uri = document.getElementById('ctl00_cphBody_URIToCopy');

var uriValue = uri.value;

//copy to clipboard

window.clipboardData.setData('Text', uriValue);

}

</script>

<style>

table, td

{

margin-left:0;

}

.reportDetail_Formview

{

min-width:100%;

}

.reportDetail_TopMiddle p, .reportDetail_TopRight p, .reportDetail_TopLeft p

{

font-weight:bold;

color:Black;

}

.reportDetail_TopMiddle

{

width:50%;

}

.reportDetail_TopRight, .reportDetail_TopLeft

{

width:25%;

}

.reportDetail_TopRight p

{

text-align:right;

}

.reportDetail_TopLeft p

{

text-align:left;

}

.reportDetail_TopMiddle p

{

text-align:center;

}

.reportDetail_header

{

text-transform:uppercase;

color:#7c51a8;

font-size:14px;

cursor:hand;

min-width:100%;

margin-left:11px;

}

.reportDetail_lvl2header

{

text-transform:uppercase;

font-size:12px;

color:#7c51a8;

}

.reportDetail_confidentialtyNotice

{

margin-top:60px;

border:1px solid black;

font-style:italic;

text-align:center;

font-size:10px;

}

.reportDetail_CloseLink

{

float:right;

}

.reportDetail_EventInformationTable

{

width:100%;

}

.reportDetail_InformationContact

{

font-weight:bold;

}

.reportDetailEventInformation_block

{

}

.reportDetail_OECTMembreInformation

{

text-align:right;

}

.reportDetail_attachmentList li

{

list-style-type:none;

margin-left:2px;

float:left; /*for IE*/

}

.reportDetail_attachmentList li a

{

display:block;

float:left;

width:100px;

text-decoration:none;

padding:5px;

}

.reportDetail_ReportNote

{

font-style:italic;

text-align:center;

}

</style>

<title>

</title></head>

<body topmargin="0" leftmargin="0" LINK="#0066cc" VLINK="#666666" marginwidth="0" marginheight="0">

<form method="post" action="./EventReportDetail.aspx?mode=print&amp;ids=26080&amp;bt=" id="aspnetForm">

<div class="aspNetHidden">

<input type="hidden" name="__VIEWSTATE" id="__VIEWSTATE" value="/wEPDwUJOTg2ODcwODk5D2QWAmYPZBYCAgMPZBYEAgEPZBYCAgEPDxYCHgdWaXNpYmxlaGRkAgcPZBYIAgMPDxYCHwBoZGQCBQ8WBB4MRGF0YVNvdXJjZUlEBQlvZHNSZXBvcnQeC18hSXRlbUNvdW50AgEWAmYPZBYkAgMPDxYCHgRUZXh0BRFXQU5PIEV2ZW50IFJlcG9ydGRkAgUPDxYCHwMFEVdBTk8gVG9reW8gQ2VudHJlZGQCBw8PFgIfAwUEMjAxNmRkAgkPDxYCHwMFBDAzMjZkZAILDw8WAh8DBWJJbXBsYW50YXRpb24gb2YgVHJvamFuIHZpcnVzIGluIFVuaXRzIDEmMiBlbWVyZ2VudCBhdXhpbGlhcnkgZGVjaXNpb24gbWFraW5nIHN5c3RlbSBnYXRld2F5IHNlcnZlcmRkAg0PDxYCHwMFCEZ1cWluZyAxZGQCDw8PFgIfAwUKMTUvMDQvMjAxNmRkAhEPDxYCHwMFCFRyZW5kaW5nZGQCFQ8PFgIfAwUCMDBkZAIZDw8WAh8DBQozMC8wOS8yMDE2ZGQCGw8PFgIfAGhkZAIdDw8WAh8AaGRkAh8PDxYCHwNlZGQCIQ8WAh8CAgEWAmYPZBYUAgMPDxYCHwMFCEZ1cWluZyAxZGQCBQ8PFgIfAwUEMjAxNGRkAgkPDxYCHwMFCEZ1cWluZyAyZGQCDQ8PFgIfAwUDUFdSZGQCEQ8PFgIfAwUNTm90IEF2YWlsYWJsZWRkAhUPDxYCHwMFDU5vdCBBdmFpbGFibGVkZAIZDw8WAh8DBQoxNS8wNC8yMDE2ZGQCHQ8PFgIfAwUDTi9BZGQCIQ8PFgIfA2VkZAIlDw8WAh8DBWAgTmFtZSA6ICBPRSBQcm9ncmFtbWUsIFdBTk8gVG9reW8gQ2VudHJlICwgRW1haWwgOiAgb2VAd2Fuby10Yy5vci5qcCAsIFBob25lIDogICs4MS0zLTM0ODAtNDgwOSBkZAIlDw8WAh8DBQROb25lZGQCJw8PFgIfAGhkZAIpDw8WAh8AaGRkAisPZBZMZg8VAQ5kaXNwbGF5OmJsb2NrO2QCAQ8PZBYCHgVzdHlsZQUOZGlzcGxheTpibG9jaztkAgIPFQEOZGlzcGxheTpibG9jaztkAgMPD2QWAh8EBQ5kaXNwbGF5OmJsb2NrO2QCBQ8PFgIfAwXKAkR1cmluZyBub3JtYWwgb3BlcmF0aW9uLCBUcm9qYW4gdmlydXMgd2FzIGZvdW5kIGluIHRoZSBkZWNpc2lvbiBhc3Npc3RpbmcgY29tcHV0ZXIgaW4gZW1lcmdlbmN5IGNvbnRyb2wgY2VudHJlLiBUaGlzIHJlc3VsdGVkJm5ic3A7d2FzIHRoZSZuYnNwO3VuYXZhaWxhYmlsaXR5IG9mIFVuaXRzIDEgYW5kIDIgZW1lcmdlbnQgYXV4aWxpYXJ5IGRlY2lzaW9uIG1ha2luZyBzeXN0ZW0gYW5kIHBvdGVudGlhbCByaXNrJm5ic3A7dG8gdGhlJm5ic3A7ZGlnaXRhbCBjb250cm9sIHN5c3RlbSBvcGVyYXRpb24sIGFkdmVyc2VseSBhZmZlY3RpbmcgdW5pdCBub3JtYWwgb3BlcmF0aW9uLhYCHwQFDmRpc3BsYXk6YmxvY2s7ZAIHDw9kFgIfBAUOZGlzcGxheTpibG9jaztkAgkPDxYCHwMFigNUaGUgcG9zc2libGUgZGlyZWN0IGNhdXNlcyB3ZXJlIGludHJvZHVjdGlvbiBvZiBtYWxpY2lvdXMgY29kZSBieSB0aGUgdXNlIG9mIG1vYmlsZSBtZWRpYSBvciBpbnRyb2R1Y3Rpb24gdG8gdGhlIHNlcnZlciB2aWEgcHJpdmF0ZSBsaW5lIGJldHdlZW4gcHJpdmF0ZSBuZXR3b3JrIGFuZCB0aGUgZW1lcmdlbmN5IG5ldHdvcmsuIFRoZSByb290IGNhdXNlIHdhcyB0aGF0IHRoZSBlbWVyZ2VudCBjb21tYW5kIGNlbnRlciB3YXMgbm90IHBoeXNpY2FsbHkgaXNvbGF0ZWQgZnJvbSBleHRlcm5hbCBuZXR3b3JrcyBhbmQgZXF1aXBtZW50IHdhcyBwbGFjZWQgaW4gdGhlIG9mZmljZSB3aXRob3V0IGFjY2VzcyBjb250cm9sLiBUaGUgb3RoZXIgY2F1c2Ugd2FzIHVzZSBvZiBvbGQgaGFyZHdhcmUuFgIfBAUOZGlzcGxheTpibG9jaztkAgsPD2QWAh8EBQ5kaXNwbGF5OmJsb2NrO2QCDQ8PFgIfAwVsY29tcHV0ZXIsY29uZmlndXJhdGlvbiBjb250cm9sLGh1bWFuIGVycm9yLGRpZ2l0YWwgY29udHJvbCBzeXN0ZW0gLyBkaWdpdGFsIGNvbXBvbmVudHMsMiAtIEltcG9ydGFudCBsZXNzb25zFgIfBAUOZGlzcGxheTpibG9jaztkAg8PD2QWAh8EBQ5kaXNwbGF5OmJsb2NrO2QCEQ8PFgIfA2QWAh8EBQ5kaXNwbGF5OmJsb2NrO2QCFQ8PFgIfAwW8BER1cmluZyBub3JtYWwgb3BlcmF0aW9uIG9mIFVuaXRzIDEmYW1wOzIsIG5ldHdvcmsgY2hhcmFjdGVyaXN0aWNzIG9mIFRyb2phbiB2aXJ1cyB3ZXJlIGZvdW5kIHZpYSB0aGUgbmV0d29yayBzdXBlcnZpc29yeSBjb250cm9sIHBsYXRmb3JtLiBUaGUgdmlydXMgd2FzIHRoZW4gbG9jYXRlZCBhdCBlbWVyZ2VudCBhdXhpbGlhcnkgZGVjaXNpb24gbWFraW5nIHN5c3RlbSBnYXRld2F5IHNlcnZlci4gVGhyb3VnaCBhc3Nlc3NtZW50IG9mIHRoZSBob3N0IGNvbXB1dGVyIHdpdGggdmlydXMsIG1lYXN1cmVzIG9mIGZpbmRpbmcgYW5kIGtpbGxpbmcgb2YgdmlydXMsIG5ldHdvcmsgaXNvbGF0aW9uLCBhbmQgc3lzdGVtIG1pZ3JhdGlvbiBldGMuIGhhdmUgYmVlbiB0YWtlbiBmb3IgaGFuZGxpbmcuIFRoaXMgZXZlbnQgcmVzdWx0ZWQgaW4gdW5hdmFpbGFiaWxpdHkgb2YgVW5pdHMgMSZhbXA7MiBlbWVyZ2VudCBhdXhpbGlhcnkgZGVjaXNpb24gbWFraW5nIHN5c3RlbSBhbmQgcG90ZW50aWFsIHJpc2sgaW4gRENTIG9wZXJhdGlvbiwgYWR2ZXJzZWx5IGFmZmVjdGluZyB1bml0IG5vcm1hbCBvcGVyYXRpb24uZGQCGQ8PFgIfAwXdB0luIHRoZSBtb3JuaW5nIG9mIDIwMTYuNC4xNSwgZW1wbG95ZWUgb2YgSVQgJmFtcDsgRG9jdW1lbnQgRGVwdC4gZm91bmQgbmV0d29yayBzbmlmZmluZyBhdHRhY2sgaW4gY29tcGFueSBpbnRlcm5hbCBuZXR3b3JrIHZpYSB0aGUgbmV0d29yayBwZXJmb3JtYW5jZSBhbmFseXNpcyBwbGF0Zm9ybS4gQWZ0ZXIgYmFjay10cmFjayBhbmFseXNpcyBvZiBkYXRhLCB0aGUgc25pZmZlciB3YXMgbG9jYXRlZCBpbiB0aGUgZW1lcmdlbnQgYXV4aWxpYXJ5IGRlY2lzaW9uIG1ha2luZyBzeXN0ZW0gZ2F0ZXdheSBzZXJ2ZXIuIFRoaXMgZW1wbG95ZWUgZm9ydGh3aXRoIGNvbnRhY3RlZCB0aGUgSGVhbHRoIFBoeXNpY3MgRGVwdC4gdG8gbm90aWZ5IE5OU0EgYW5kIGdvIHRvIHRoZSBzaXRlIGZvciBlbWVyZ2VudCBoYW5kbGluZy4gVGhyb3VnaCBjaGVjayBvZiBlcXVpcG1lbnQgc3RhdHVzIGFuZCBhbmFseXNpcywgVHJvamFuIHZpcnVzIHdhcyBmb3VuZCBpbXBsYW50ZWQgaW4gdGFyZ2V0IGVxdWlwbWVudCBhbmQgdHJpZWQgdG8gY29ubmVjdCBleHRlcm5hbCBJbnRlcm5ldCBzZXJ2ZXIsIHRodXMgcmVzdWx0aW5nIGluIHN5c3RlbSBpbmZvcm1hdGlvbiBkaXNjbG9zdXJlIGFuZCBkYW1hZ2UsIGFuZCBwb3NzaWJsZSBmdXJ0aGVyIHBlcnZhc2lvbi4gU3lzdGVtIGFkbWluaXN0cmF0b3IgdHJpZWQgdmFyaW91cyB0eXBlcyBvZiB2aXJ1cyBraWxsaW5nIHNvZnR3YXJlIHRvIGZpbmQgYW5kIGtpbGwgdGhlIHZpcnVzLCBkZXRlcm1pbmVkIGRhbWFnZSBvZiB0aGUgc3lzdGVtIGJ5IHRoZSBtYWxpY2lvdXMgY29kZSwgYXNzZXNzZWQgcG9zc2libGUgbWVuYWNlIHRvIHRoZSBuZXR3b3JrIGVudmlyb25tZW50LCBhbmQgdGhlbiBpc29sYXRlZCBpdCBmcm9tIGV4dGVybmFsIG5ldHdvcmtzLCB0dXJuZWQgdGhlIHNlcnZlciBvZmZsaW5lIGFzIHNvb24gYXMgcG9zc2libGUsIGFuZCBjb21wbGV0ZWQgbWlncmF0aW9uIG9mIHN5c3RlbSBmdW5jdGlvbnMuZGQCHQ8PFgIfAwWYAVVuYXZhaWxhYmlsaXR5IG9mIFVuaXRzIDEmYW1wOzIgZW1lcmdlbnQgYXV4aWxpYXJ5IGRlY2lzaW9uIG1ha2luZyBzeXN0ZW0gYW5kIHBvdGVudGlhbCByaXNrIGluIERDUyBvcGVyYXRpb24sIGFkdmVyc2VseSBhZmZlY3RpbmcgdW5pdCBub3JtYWwgb3BlcmF0aW9uZGQCIQ8PFgIfAwX3DDEpIERpcmVjdCBjYXVzZSA8YnIgLz4NClRoZXJlIGFyZSB0d28gcG9zc2libGUgd2F5cyBhIFRyb2phbiB2aXJ1cyBjYW4gZW50ZXIgYSBzZXJ2ZXI6IGluc2VydGlvbiBvZiBtb2JpbGUgbWVkaWEgaW4gdGhlIHNlcnZlciwgYnJpbmdpbmcgaW4gbWFsaWNpb3VzIGNvZGU7IG1hbGljaW91cyBjb2RlIGVudGVycyBzZXJ2ZXIgdmlhIHByaXZhdGUgbGluZSBiZXR3ZWVuIG90aGVyIHByaXZhdGUgbmV0d29yayBhbmQgdGhlIGVtZXJnZW5jeSBuZXR3b3JrLiBIb3dldmVyLCBzaW5jZSBPUyhvcGVyYXRpb24gc3lzdGVtKSB2ZXJzaW9uIG9mIHRoZSBlbWVyZ2VudCBhdXhpbGlhcnkgZGVjaXNpb24gbWFraW5nIHN5c3RlbSBpcyB0b28gbG93LCBlcXVpcG1lbnQgb3BlcmF0aW9uIGluZm9ybWF0aW9uIGNhbm5vdCBiZSBpbnF1aXJlZCB2aWEgc3lzdGVtIGxvZywgc28gdGhhdCBzb3VyY2Ugb2YgVHJvamFuIHZpcnVzIGNhbm5vdCBiZSB0cmFjZWQuIDxiciAvPg0KMikgUm9vdCBjYXVzZSA8YnIgLz4NClRoZSBuZXR3b3JrIG9mIHRoZSBFbWVyZ2VudCBDb21tYW5kIENlbnRlciBpcyBub3QgcGh5c2ljYWxseSBpc29sYXRlZCBmcm9tIGV4dGVybmFsIG5ldHdvcmtzIHN1Y2ggYXMgdGhlIG9mZmljZSBuZXR3b3JrIGFuZCB0aGUgSW50ZXJuZXQuIEFjY29yZGluZyB0byByZXF1aXJlbWVudHMgYnkgJmxkcXVvO05OU0EgZW1lcmdlbnQgcHJpdmF0ZSBuZXR3b3JrIGludGVydmVudGlvbiBjb2RlICh0cmlhbCkmcmRxdW87LCBFbWVyZ2VudCBDb21tYW5kIENlbnRlciBuZXR3b3JrIHNoYWxsIGJlIHBoeXNpY2FsbHkgaXNvbGF0ZWQgZnJvbSB0aGUgSW50ZXJuZXQgYW5kIG90aGVyIHB1YmxpYyBuZXR3b3Jrcy4gPGJyIC8+DQpTaW5jZSB0aGUgRW1lcmdlbnQgQ29tbWFuZCBDZW50ZXIgaGFzIG5vIGRlZGljYXRlZCBlcXVpcG1lbnQgcm9vbSwgaXRzIHNlcnZlciBhbmQgbmV0d29yayBlcXVpcG1lbnQgYXJlIHBsYWNlZCBpbiB0aGUgb2ZmaWNlIHpvbmUsIHdpdGhvdXQgYWNjZXNzIGNvbnRyb2wgbWFuYWdlbWVudCBkZXZpY2UsIHNvIHRoYXQgYW55b25lIGNhbiBlbnRlciB0aGlzIHpvbmUgYW5kIGFjY2VzcyB0aGUgc2VydmVyIGF0IHdpbGwuIDxiciAvPg0KT3BlcmF0aW9uIGFuZCBtYWludGVuYW5jZSB3b3JrIG9mIHRoZSBFbWVyZ2VudCBDb21tYW5kIENlbnRlciBuZXR3b3JrIGhhcmR3YXJlIGZ1bmRhbWVudGFsIGVudmlyb25tZW50IGlzIG5vdCBzdXBwb3J0ZWQgYnkgbWFuYWdlbWVudCBwcm9jZWR1cmVzIGFuZCBoYXMgbm8gc3RhbmRhcmQgcmVxdWlyZW1lbnRzIG9uIGRhaWx5IG9wZXJhdGlvbiBhbmQgbWFpbnRlbmFuY2UgcGF0cm9sIGluc3BlY3Rpb24uIDxiciAvPg0KMykgQ2F1c2FsIGZhY3RvcnMgPGJyIC8+DQpVbml0cyAxJmFtcDsyIGVtZXJnZW50IGF1eGlsaWFyeSBkZWNpc2lvbiBtYWtpbmcgc3lzdGVtIGhhcyBubyBtYW51ZmFjdHVyZXIgbWFpbnRlbmFuY2Ugd2FycmFudHksIGhhcyBvbGQgaGFyZHdhcmUgZXF1aXBtZW50LCBoZW5jZSB0aGUgcmlzayBpbiBzYWZldHkgYW5kIGZhdWx0LCBhbmQgaGFzIHRvbyBsb3cgT1MgcGxhdGZvcm0gdmVyc2lvbiwgaGVuY2Ugc3lzdGVtIGxvb3Bob2xlcyB0aGF0IG1heSBiZSB1c2VkIGJ5IFRyb2phbiB2aXJ1cyBhbmQgb3RoZXIgdmlydXNlcy4gPGJyIC8+ZGQCJQ8PFgIfAwXZCzEuIEFkanVzdCBmdW5jdGlvbnMgb2YgVW5pdHMgMSZhbXA7MiBlbWVyZ2VudCBhdXhpbGlhcnkgZGVjaXNpb24gbWFraW5nIHN5c3RlbSBvbnRvIHRoZSBFbWVyZ2VudCBDb21tYW5kIFBsYXRmb3JtLCBhbmQgZW5zdXJlIHRoYXQgdGhpcyBzeXN0ZW0gY2FuIGdvIG9mZmxpbmUgPGJyIC8+DQoyLiBPcmdhbml6ZSByZWxldmFudCBkZXBhcnRtZW50cyBmb3IgYSBzeW1wb3NpYSBvZiAmbGRxdW87aW5jbHVzaW9uIG9mIEVtZXJnZW50IENvbW1hbmQgQ2VudGVyIGluIHByb2R1Y3Rpb24gem9uZSBtYW5hZ2VtZW50JnJkcXVvOyA8YnIgLz4NCjMuIEludml0ZSBleHRlcm5hbCBleHBlcnRzIGZvciBvdmVyYWxsIGFuYWx5c2lzIG9mIHRoaXMgc2FmZXR5IGV2ZW50IDxiciAvPg0KNC4gQ2Fycnkgb3V0IEludGVybmV0IGJvdW5kYXJ5IGF0dGFjayBhbmQgZGVmZW5jZSBleGVyY2lzZSA8YnIgLz4NCjUuIFB1Ymxpc2ggcHJvY2VkdXJlICZsZHF1bztFbWVyZ2VudCBDb21tYW5kIENlbnRlciBuZXR3b3JrIGhhcmR3YXJlIGVudmlyb25tZW50IG1hbmFnZW1lbnQmcmRxdW87IDxiciAvPg0KNi4gRGV0ZXJtaW5lIHBhcnRpY3VsYXIgZ3JhZGluZyBhbmQgbWFuYWdlbWVudCByZXF1aXJlbWVudHMgZm9yIGFsbCBpbmZvcm1hdGl6YXRpb24gdGVybWluYWxzIG9mIHRoZSBFbWVyZ2VudCBDb21tYW5kIENlbnRlciBhbmQgcmVsZXZhbnQgZXF1aXBtZW50LCBwdWJsaXNoIG1hbmFnZW1lbnQgcHJvY2VkdXJlLCBhbmQgY29tcGxldGUgcGh5c2ljYWwgcmVjb25zdHJ1Y3Rpb24gY29uc2lzdGVudCB3aXRoIHRoZSBtYW5hZ2VtZW50IHByb2NlZHVyZSA8YnIgLz4NCjcuIFJlbmV3IHBhc3N3b3JkIG9mIEVtZXJnZW50IENvbW1hbmQgUGxhdGZvcm0gc2VydmVyIDxiciAvPg0KOC4gQ29tcGxldGUgdGhlIGFjY2VzcyBjb250cm9sIHJlY29uc3RydWN0aW9uIHByb2plY3QgZm9yIHRoZSBvZmZpY2Ugb2YgRW1lcmdlbnQgQ29tbWFuZCBDZW50ZXIgbmV0d29yayBndWFyYW50ZWUgZ3JvdXAgPGJyIC8+DQo5LiBDaGVjayBuZXR3b3JrIGNvbmZpZ3VyYXRpb24gb2YgdGhlIGluZHVzdHJpYWwgY29udHJvbCBzeXN0ZW0gZm9yIHRoZSBFbWVyZ2VudCBDb21tYW5kIENlbnRlciwgYW5kIHByZXBhcmUgYW4gaW5zcGVjdGlvbiByZXBvcnQsIHRvIGVuc3VyZSBzYWZldHkgb2YgdGhlIGluZHVzdHJpYWwgY29udHJvbCBzeXN0ZW0gPGJyIC8+DQoxMC4gQ2hlY2sgZWZmZWN0aXZlbmVzcyBvZiBpbmR1c3RyaWFsIGNvbnRyb2wgc3lzdGVtIG9uZS13YXkgaXNvbGF0aW9uIGRldmljZSBhbmQgcHJlcGFyZSB0ZXN0IHJlcG9ydCB0byBlbnN1cmUgc2FmZXR5IG9mIHRoZSBpbmR1c3RyaWFsIGNvbnRyb2wgc3lzdGVtLiA8YnIgLz4NCjExLiBBY2NvcmRpbmcgdG8gZXhwZXJpZW5jZSBmZWVkYmFjayBvZiB0aGlzIGV2ZW50LCBjaGVjayBwcm90ZWN0aW9uIGZvciBzYWZldHkgb2YgbGFyZ2UgcHJvZHVjdGlvbiB6b25lIG5ldHdvcmsgYW5kIGluZm9ybWF0aW9uIDxiciAvPmRkAikPFgIfAmZkAisPFgIfAmZkAjcPFgIfAgIBFgJmD2QWAgIBDw8WAh8DBQIwOGRkAjkPFgIfAgIBFgJmD2QWAgIBDw8WAh8DBTJPdGhlciBldmVudHMgaW52b2x2aW5nIHBsYW50IHNhZmV0eSBvciByZWxpYWJpbGl0eWRkAj0PFgIfAgIBFgJmD2QWAgIBDw8WAh8DBQIxMGRkAj8PFgIfAgIBFgJmD2QWAgIBDw8WAh8DBR5Ob24gY29uc2VxdWVudGlhbCBvciBuZWFyIG1pc3NkZAJDDxYCHwICARYCZg9kFgICAQ8PFgIfAwUDNzEwZGQCRQ8WAh8CAgEWAmYPZBYCAgEPDxYCHwMFQVBsYW50IC8gUHJvY2VzcyBjb21wdXRlciAoaW5jbHVkaW5nIG1haW4gYW5kIGF1eGlsaWFyeSBjb21wdXRlcnMpZGQCSQ8WAh8CAgEWAmYPZBYCAgEPDxYCHwMFAzcyMGRkAksPFgIfAgIBFgJmD2QWAgIBDw8WAh8DBRFDb21wdXRlciBTb2Z0d2FyZWRkAk8PDxYCHwMFAzExMGRkAlEPDxYCHwMFFlN0ZWFkeSBwb3dlciBvcGVyYXRpb25kZAJVDw8WAh8DBQIwNWRkAlcPDxYCHwMFG05vcm1hbCBlcXVpcG1lbnQgb3BlcmF0aW9uc2RkAlsPFgIfAgIBFgJmD2QWAgIBDw8WAh8DBQMzNTBkZAJdDxYCHwICARYCZg9kFgICAQ8PFgIfAwUKSW5zdHJ1bWVudGRkAmEPDxYCHwMFBDA1MDVkZAJjDw8WAh8DBTtDb21wdXRlciBzb2Z0d2FyZSBkZWZpY2llbmN5IChpbmNsdWRpbmcgYXV0byBjb250cm9sIGxvb3BzKWRkAmcPFgIfAgICFgRmD2QWAgIBDw8WAh8DBQQxMTMwZGQCAg9kFgICAQ8PFgIfAwUEMjAwMWRkAmkPFgIfAgICFgRmD2QWAgIBDw8WAh8DBYkBUG9saWNpZXMsIG9mZmljaWFsIGd1aWRhbmNlIChzdGFuZGFyZHMpLCBleHBlY3RhdGlvbnMsIGFkbWluaXN0cmF0aXZlIGNvbnRyb2xzOi1Ob3QgYWRlcXVhdGUgKG5vdCBzdHJpY3QgZW5vdWdoLCBjb25mdXNpbmcgb3IgaW5jb21wbGV0ZSlkZAICD2QWAgIBDw8WAh8DBRpPcmlnaW5hbCBkZXNpZ24gaW5hZGVxdWF0ZWRkAm0PFgIfAgIBFgJmD2QWAgIBDw8WAh8DBQQwODA3ZGQCbw8WAh8CAgEWAmYPZBYCAgEPDxYCHwMFIUNvbnRyb2wgb2YgY29udHJhY3RvcnMgaW5hZGVxdWF0ZWRkAgcPD2QPEBYCZgIBFgIWAh4OUGFyYW1ldGVyVmFsdWUFBTI2MDgwFgIfBWQWAgIEAgRkZAIJDw9kDxAWAWYWARYCHwUFBTI2MDgwFgECBGRkZIeKQ7DUvBr93HwSgzcxTOwvr1g7HCGhOmnk9LSG3MKw" />

</div>

<div class="aspNetHidden">

<input type="hidden" name="__VIEWSTATEGENERATOR" id="__VIEWSTATEGENERATOR" value="1278C7F0" />

<input type="hidden" name="__EVENTVALIDATION" id="__EVENTVALIDATION" value="/wEdAAOi5l+cr5DBjocZpfAQJb5LvtnLCO2al9e00J+wbcYDFksd8bpC0YG4vfjxmAhJED8+jlb9A4eU5t5oyctXazQIuOI/jaq0pSqJ977K9SS82g==" />

</div>

<div>

<div class="main_body">

<input type="hidden" name="ctl00$cphBody$URIToCopy" id="ctl00_cphBody_URIToCopy" value="http://www.wano.org/OperatingExperience/OE_Database_2012/Pages/EventReportDetail.aspx?&amp;ids=26080&amp;bt=" />

<input type="hidden" name="ctl00$cphBody$rptReports$ctl00$hfReportIdentifier" id="ctl00_cphBody_rptReports_ctl00_hfReportIdentifier" value="WER TYO 16-0326" />

<table class="reportDetail_Header" style="width: 100%;">

<tbody style="width: 100%">

<tr>

<td class="reportDetail_TopLeft">

<p>

<span id="ctl00_cphBody_rptReports_ctl00_lblReportFullType">WANO Event Report</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblReportCentreFullName">WANO Tokyo Centre</span>,&nbsp;<span id="ctl00_cphBody_rptReports_ctl00_lblReportYear">2016</span>-<span id="ctl00_cphBody_rptReports_ctl00_lblReportNumber">0326</span>

</p>

</td>

<td class="reportDetail_TopMiddle">

<p>

<span id="ctl00_cphBody_rptReports_ctl00_lblFullTitle">Implantation of Trojan virus in Units 1&2 emergent auxiliary decision making system gateway server</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblReportFullUnitName">Fuqing 1</span>,

<span id="ctl00_cphBody_rptReports_ctl00_lblEventDate">15/04/2016</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblSignificanceCode">Trending</span>

</p>

</td>

<td class="reportDetail_TopRight">

<p>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextRevisionNo">Revision Number</span>

<span id="ctl00_cphBody_rptReports_ctl00_lblReportRevision">00</span>

-

<span id="ctl00_cphBody_rptReports_ctl00_lblTextPosted">Posted date</span>

<span id="ctl00_cphBody_rptReports_ctl00_lblReportPostingDate">30/09/2016</span>

<br />

</p>

</td>

</tr>

</tbody>

</table>

<div class="reportDetail_ReportNote">

<span id="ctl00_cphBody_rptReports_ctl00_lblReportNote"></span>

</div>

<hr />

<table class="reportDetail_EventInformationTable">

<tr>

<td>

<table class="reportDetailEventInformation_block">

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextUnitAndYear">Unit (Year)</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblUnit">Fuqing 1</span>

(<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblYear">2014</span>)

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblAdditionalTextUnits">Additional Units</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblAdditionalUnits">Fuqing 2</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextReactorType">Reactor Type</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblReactorType">PWR</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextReactorManufacturer">Reactor Manufacturer</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblReactorManufacturer">Not Available</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextPlantDesigner">Plant Designer</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblPlantDesigner">Not Available</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextEventDate">Event Date</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblEventDate">15/04/2016</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextINESLevel">INES</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblINESLevel">N/A</span>

</td>

</tr>

</table>

</td>

<td class="reportDetail_OECTMembreInformation">

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextOEInformationContact" class="reportDetail_InformationContact">OE Station Information Contact</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblOEInformationContact"></span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextWanoInformationContact" class="reportDetail_InformationContact">WANO Information Contact</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_Label5"> Name :  OE Programme, WANO Tokyo Centre , Email :  oe@wano-tc.or.jp , Phone :  +81-3-3480-4809 </span>

</td>

</tr>

</table>

<table>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextReference">Reference</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblReference">None</span>

</td>

</tr>

</table>

<hr />

<br />

<br />

<br />

<br />

<div id="ctl00_cphBody_rptReports_ctl00_divOECT" class="accordion">

<div class="accordion_header" style="display:block;">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTInformation" class="reportDetail_header" style="display:block;">OECT Information</span><hr />

</div>

<div class="accordion_content" style="display:block;">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTSummary" class="reportDetail_lvl2header" style="display:block;">Summary</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTSummary" style="display:block;">During normal operation, Trojan virus was found in the decision assisting computer in emergency control centre. This resulted&nbsp;was the&nbsp;unavailability of Units 1 and 2 emergent auxiliary decision making system and potential risk&nbsp;to the&nbsp;digital control system operation, adversely affecting unit normal operation.</span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTCauses" class="reportDetail_lvl2header" style="display:block;">Causes</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTCauses" style="display:block;">The possible direct causes were introduction of malicious code by the use of mobile media or introduction to the server via private line between private network and the emergency network. The root cause was that the emergent command center was not physically isolated from external networks and equipment was placed in the office without access control. The other cause was use of old hardware.</span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTKeywords" class="reportDetail_lvl2header" style="display:block;">Keywords</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTKEYWORDS" style="display:block;">computer,configuration control,human error,digital control system / digital components,2 - Important lessons</span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTReferences" class="reportDetail_lvl2header" style="display:block;">References</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTReferences" style="display:block;"></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextSummary" class="reportDetail_header">Summary</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_lblReportSummary">During normal operation of Units 1&amp;2, network characteristics of Trojan virus were found via the network supervisory control platform. The virus was then located at emergent auxiliary decision making system gateway server. Through assessment of the host computer with virus, measures of finding and killing of virus, network isolation, and system migration etc. have been taken for handling. This event resulted in unavailability of Units 1&amp;2 emergent auxiliary decision making system and potential risk in DCS operation, adversely affecting unit normal operation.</span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextDecription" class="reportDetail_header">Description</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label1">In the morning of 2016.4.15, employee of IT &amp; Document Dept. found network sniffing attack in company internal network via the network performance analysis platform. After back-track analysis of data, the sniffer was located in the emergent auxiliary decision making system gateway server. This employee forthwith contacted the Health Physics Dept. to notify NNSA and go to the site for emergent handling. Through check of equipment status and analysis, Trojan virus was found implanted in target equipment and tried to connect external Internet server, thus resulting in system information disclosure and damage, and possible further pervasion. System administrator tried various types of virus killing software to find and kill the virus, determined damage of the system by the malicious code, assessed possible menace to the network environment, and then isolated it from external networks, turned the server offline as soon as possible, and completed migration of system functions.</span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextConsequences" class="reportDetail_header">Consequences</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label2">Unavailability of Units 1&amp;2 emergent auxiliary decision making system and potential risk in DCS operation, adversely affecting unit normal operation</span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextAnalysisComments" class="reportDetail_header">Analysis/Comments</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label3">1) Direct cause <br />

There are two possible ways a Trojan virus can enter a server: insertion of mobile media in the server, bringing in malicious code; malicious code enters server via private line between other private network and the emergency network. However, since OS(operation system) version of the emergent auxiliary decision making system is too low, equipment operation information cannot be inquired via system log, so that source of Trojan virus cannot be traced. <br />

2) Root cause <br />

The network of the Emergent Command Center is not physically isolated from external networks such as the office network and the Internet. According to requirements by &ldquo;NNSA emergent private network intervention code (trial)&rdquo;, Emergent Command Center network shall be physically isolated from the Internet and other public networks. <br />

Since the Emergent Command Center has no dedicated equipment room, its server and network equipment are placed in the office zone, without access control management device, so that anyone can enter this zone and access the server at will. <br />

Operation and maintenance work of the Emergent Command Center network hardware fundamental environment is not supported by management procedures and has no standard requirements on daily operation and maintenance patrol inspection. <br />

3) Causal factors <br />

Units 1&amp;2 emergent auxiliary decision making system has no manufacturer maintenance warranty, has old hardware equipment, hence the risk in safety and fault, and has too low OS platform version, hence system loopholes that may be used by Trojan virus and other viruses. <br /></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCorrectiveActions" class="reportDetail_header">Corrective Actions</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label4">1. Adjust functions of Units 1&amp;2 emergent auxiliary decision making system onto the Emergent Command Platform, and ensure that this system can go offline <br />

2. Organize relevant departments for a symposia of &ldquo;inclusion of Emergent Command Center in production zone management&rdquo; <br />

3. Invite external experts for overall analysis of this safety event <br />

4. Carry out Internet boundary attack and defence exercise <br />

5. Publish procedure &ldquo;Emergent Command Center network hardware environment management&rdquo; <br />

6. Determine particular grading and management requirements for all informatization terminals of the Emergent Command Center and relevant equipment, publish management procedure, and complete physical reconstruction consistent with the management procedure <br />

7. Renew password of Emergent Command Platform server <br />

8. Complete the access control reconstruction project for the office of Emergent Command Center network guarantee group <br />

9. Check network configuration of the industrial control system for the Emergent Command Center, and prepare an inspection report, to ensure safety of the industrial control system <br />

10. Check effectiveness of industrial control system one-way isolation device and prepare test report to ensure safety of the industrial control system. <br />

11. According to experience feedback of this event, check protection for safety of large production zone network and information <br /></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextAttachments" class="reportDetail_header">Attachments</span><hr />

</div>

<div class="accordion_content">

<ul class="reportDetail_attachmentList">

</ul>

<ul class="reportDetail_attachmentList">

</ul>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCoddedFields" class="reportDetail_header">Coded Fields</span><hr />

</div>

<div class="accordion_content">

<table style="text-align: left">

<tr style="text-align: center">

<th>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCdArrayField1" class="reportDetail_lvl2header">Field</span>

</th>

<th>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCdArrayField2" class="reportDetail_lvl2header">Code</span>

</th>

<th>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCdArrayField3" class="reportDetail_lvl2header">Description</span>

</th>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDCategory" class="reportDetail_lvl2header">Category</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptCategoryCodes_ctl00_lblCategoryCode">08</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptCategoryDescriptions_ctl00_lblCategoryDescription">Other events involving plant safety or reliability</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDConsequences" class="reportDetail_lvl2header">Consequences</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptConsequenceCodes_ctl00_lblConsequenceCode">10</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptConequenceDescriptions_ctl00_lblConsequenceDescription">Non consequential or near miss</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDSystems" class="reportDetail_lvl2header">Systems</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemCodes_ctl00_lblSystemCode">710</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemDescrptions_ctl00_lblSystemDescription">Plant / Process computer (including main and auxiliary computers)</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDComponents" class="reportDetail_lvl2header">Components</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentCodes_ctl00_lblSystemCode">720</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentDescriptions_ctl00_lblComponentDescription">Computer Software</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDStatus" class="reportDetail_lvl2header">Status</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblStatusCode">110</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblStatusDescription">Steady power operation</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDActivity" class="reportDetail_lvl2header">Activity</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblActivityCode">05</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblActivityDescription">Normal equipment operations</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDGroup" class="reportDetail_lvl2header">Group</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupCodes_ctl00_lblGroupCode">350</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupDescriptions_ctl00_lblGroupDescription">Instrument</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDDirectCause" class="reportDetail_lvl2header">Direct Cause</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblDirectCauseCode">0505</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblDirectCauseDescription">Computer software deficiency (including auto control loops)</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDRootCause" class="reportDetail_lvl2header">Root Cause</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptRootCauseCodes_ctl00_lblRootCauseCode">1130</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptRootCauseCodes_ctl02_lblRootCauseCode">2001</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptRootCauseDescriptions_ctl00_lblRootCauseDescription">Policies, official guidance (standards), expectations, administrative controls:-Not adequate (not strict enough, confusing or incomplete)</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptRootCauseDescriptions_ctl02_lblRootCauseDescription">Original design inadequate</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDCausalFactor" class="reportDetail_lvl2header">Causal Factor</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptCausalFactorCodes_ctl00_lblRootCauseDescription">0807</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptCausalFactorDescriptions_ctl00_lblRootCauseDescription">Control of contractors inadequate</span>

</td>

</tr>

</table>

<br />

</div>

</div>

<div class="reportDetail_confidentialtyNotice">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextConfidentialityNotice1">CONFIDENTIALITY NOTICE: Copyright  1987-2017 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale or commercial use. This document is protected as an unpublished work under the copyright laws of all countries which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. This document and its contents are confidential and shall be treated in strictest confidence. In particular, except with the prior written consent of the WANO Coordinating Centre, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations.<br/><br/>

LIABILITY DISCLAIMER NOTICE: This information was prepared in connection with work sponsored by the WANO. Neither WANO, WANO members, nor any person acting on the behalf of them (a) makes warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that use of any information, apparatus, method or process disclosed in this document may not infringe on privately owned rights, or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of any information, apparatus, method, or process disclosed in this document.</span>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextConfidentialityNotice2"></span>

</div>

</div>

</div>

</form>

</body>

</html>