WER MOW 12-XXX

| ** Note: |  |
| --- | --- |
| ** Station: | Bushehr Unit 1 |
| ** Event Date: | 26 May 2012 |
| **Title: | Inoperability of RCPS-1391 (YD10D001) due to impeller’s deflector tears off. |
| **Reference Unit: | - Bushehr 1 |
| **Station Event: | - Unit event |
| Summary: | When heating of the primary circuit, an unwanted noise was detected in U-section of MCP loop 1 with specific metal knocking. A foreign object was removed, which was an element of the impeller of RCPS-1 (deflector). |
| Event units: | No others |
| References: | - - |
| Report Description: | 23.05.12 12:11- When starting-up of RCPS-2 for heating of the reactor plant, special design Loosened articles detection system (LADS) detected unwanted sounds in U-section of MCP loop 1 12:35-Shift operating personnel confirmed foreign metal knocking in U-section of MCP loop 1. 20:00-Under supervision of RCM listening of the entire U-section of MCP loop 1 was performed over the whole length and regular unwanted sound was detected in the area of the down comer from SG-1. 24.05.12 When operation of RCPS-2 (YD20D001) for heating of the primary circuit and connection of RCPS-3,4 (YD30,40D001), unwanted sound in U-section of MCP loop 1 with specific metal knocking remained. 17:00 -Report № 167 was drawn-up in the DATEX logbook of «Reports of preparedness of the equipment of RC» about unwanted sound in U-section of MCP loop 1. 18:17 -According to request №46 of 24.05.12 cool down of the primary circuit was started. 25.05.12 08:22-Cool down of the primary circuit completed. Preparations for detection and removal of the foreign object were started. 26.05.12 14:15 - The works on organization of examination of the pipelines using a portable telesystem for identification of the source of the unwanted noise under a specially developed program were started. 20:15 - The foreign object was removed from the U-section of MCP loop 1. The removed object is an element of impeller of RCPS-1 (deflector). |
| **Consequences: | Damage of the deflector of impeller of RCPS-1 (YD10D001) due to tear off of fasteners. |
| Report Analysis and Comments: | State of the power Unit (NPP) before the event: «Cold» state: P1c = 1,61 MPa; Т1c = 67,8 ºС; CH3BO3NF =16,08 g/dm3; LPRZ=11,77 m; Teff=50,22 eff/day; CPS CRLLS; 1÷4 SST are in the mode «Duty», condition of heat circuit and auxiliaries power supply system is normal. Direct causes: Tear off of fastening of the deflector of impeller. Causal Factor: Degraded sub-component contributed to failure |
| Corrective Actions: | 1) For repair of systems (elements). -Replace the deflector and its fasteners on RCPS-1 (YD10D001). Inspect integrity of deflectors and -their fasteners on RCPS-2,3,4 (YD20,30,40D001). 2) For replacement of systems (elements). - Perform «shop» investigation of the causes of occurrence of cracks on the blades of impellers of RCPS-2,3,4 (YD20,30,40D001). - Replace impellers of RCPS–1,2,3,4 (YD10,20,30,40D001). 3) For operation of systems (elements). - Search for the undetected fasteners of the deflector of impeller of RCPS-1 (YD10D001) after full unloading of the fuel from the reactor core. - When starting up the Unit after PPM, perform the works as per item 6.10.2 4) For adjustment of systems (elements). -Include to the «Repair manual» 1391-00-0003РК the requirements to installation of the deflector of impeller, tightening torque of the fastening bolt of the deflector (1391-01-1098), which shall be 400 +40Nm, locking and control of condition of the bolt by penetration testing in the process of operation. - Develop a working program for putting into operation of RCPS after replacement of the impellers and monitoring of noises in the primary circuit. |
| Note: |  |
| INES Level: | 0 |
| Station Status: | - 155 -Cold shutdown - sub critical and coolant temperature < 93°C |
| Station Activity: | - 08 -Equipment start-up |
| Direct cause: | - 0106 -Break |
| Category: | - 3 -Major equipment damage |
| Consequence(s)*: | - 03 -Equipment damage |
| System(s)*: | - 150 -Reactor coolant system |
| Component(s)*: | - 210 -Pumps |
| Group(s)*: | - 210 -Shift - Control room operators - 301 -System engineering |
| Root cause(s)*: | - 2002 -Design documentation |
| Causal factor(s)*: | - 2304 -Degraded sub-component contributed to failure |
| List Attachments: | - - |