Начало формы

| WANO Event Report WANO Tokyo Centre, 2021-0460 | External Scaffolding for the Nuclear Power Information Center Construction Project Partially Toppled due to Poor Erection Quality Fangjiashan 1, 24.08.2021 Trending | Revision Number 00 - Posted date 22.10.2021 |
| --- | --- | --- |

| Unit (Year) :; Fangjiashan 1 (2014). Additional Units :. Reactor Type :; PWR. Reactor Manufacturer :; China First Heavy Industries. Plant Designer :; China Nuclear Power Engineering Co. Ltd.. Event Date :; 24.08.2021. INES :; N/A. | OE Station Information Contact WANO Information Contact Name : OE Programme, WANO Tokyo Centre , Email : oe@wano-tc.or.jp , Phone : +81-3-6722-5900 |
| --- | --- |

| Reference : | None |
| --- | --- |

OECT Information

Summary
During normal operation, the external scaffolding of a building under construction partially tilted and toppled when a sudden storm struck the construction site. All staff had been withdrawn from the site before the scaffold fell, so nobody was injured. 

Causes
The direct cause was insufficient structural stability of the scaffolding due to improper erection type and excessive erection height. The root causes were inadequate supervision and inadequate management oversight. 

Keywords
industrial safety,management oversight,scaffold,supervision 

References

Summary

On August 24, 2021, Fangjiashan-1 was under power operation. The external scaffolding for the Nuclear Power Information Center Construction Project partially tilted and toppled when a sudden storm struck the construction site due to insufficient structural stability of the scaffolding by an improper type of erection and excessive erection height without sufficient preventive measures for the toppling. However, the event did not cause casualties and direct economic losses.

Description

On August 24, 2021, Fangjiashan-1 was under power operation. According to the construction plan, two operators were arranged for the scaffolding area of the nuclear power information center construction project to set up the external scaffolding climbing ladder on the south side, and no person was arranged for the construction on the north side.
At 14:40, a sudden storm struck the construction site (the on-site tower crane on the wind meter showed wind speed of 14m/s, wind level seven), and the on-site personnel had to withdraw from the construction area.
At 15:03, the wind and rain suddenly intensified, a 3 36-meter-long, 8.5-meter-high external scaffolding under construction (which has been installed with dense mesh net) in the Construction I area to the north side of the construction site tilted and toppled (see Attachment 1). However, it did not cause casualties and direct economic losses.

Consequences

Actual consequences: The event did not affect the operation of the power station and equipment safety nor cause casualties, and did not have an adverse impact on the environment.
Potential consequences: When the scaffolding topples, if people are working on the scaffold or people passing under the scaffolding, it may lead to casualties or even mass death and injury accidents.

Analysis/Comments

Investigation on the erection of scaffolding found (see Attachment 2): 1. The external scaffolding was erected as an open type (plane U-shaped), which deviated from the scaffolding plan and calculations for the enclosed circle type (plane enclosed polygon type) erection as specified in the special construction program; 2. The external scaffolding used bracing instead of tie members for reinforcement while the erection heigh achieved 8.5m, which deviated from the requirement of the special program "When erecting braces, the braces should be a through-length tube (set the tie member when erecting height below 6m)"; 3. The inclination angle of the brace on the external scaffolding and is greater than 60° related to the ground, which deviated from the requirement of the special program "the inclination of the brace related to the ground shall be within 45° - 60°", and the root of the brace is not firmly fixed. It was judged that the improper erection type of the external scaffolding (open type) and the excessive erection height without toppling prevention measures resulted in the insufficient structural stability of the scaffolding, thus finally causing the scaffolding to tilt and topple when a sudden storm occurred.
According to the analysis and summarization of the problems in project management supervision of each construction company, as well as the interview and investigation, it revealed that the construction company and supervision department personnel at all levels had a high tolerance for the practice of departure/deviation from the construction program. In fact, the owner's department had found a number of problematic facts in various inspections in the early stage that the on-site operation and personnel behavior did not strictly comply with the procedures and program requirements but only requested on-site technical and behavioral correction for specific problems, without digging deeper into the root cause of the problem management and requiring all parties involved in the project to carry out management-level rectification. This reflects that the assessment and supervision of the effectiveness of the operation of the project department and the supervision of the production safety management system is inadequate, and the way of safety management of the project has a preferential on the on-site inspection and on-site rectification of specific problems, without paying attention to the root causes of the apparent problems of infrastructure projects.
The project is the owner's key management project, and the Engineering Management Division and the Safety and Quality Division regularly carry out joint on-site safety supervision and inspection of the project, arrange special personnel to carry out on-site safety inspection every day, and record the problems found in the inspection into the industrial safety management system to track for close, however, the inspection is not carried out in conjunction with the special program and fails to identify the hidden problems related to the toppled scaffolding. This reflects the requirements for on-site safety supervision and inspection of infrastructure construction projects in the relevant procedures of the company is unclear; the actual inspection is mainly based on experience, and the inspection is not deep enough to find out the safety problems at the technical level.
In addition, in the special construction program for external scaffolding, the expression of "when erecting braces, the braces shall be a through-length tube (set the tie member when erecting height below 6m)", which was not clear enough. The program intended that when the tie members could not be installed, bracing reinforcement can be used, however, it was prohibited to erect to more than 6 meters in height, while the interviews indicated that some staff understood that after setting the bracing below 6 meters, they could continue to build upwards, and had built up to a height of 8.5 meters. At the same time, the program did not provide for some specific safety measures in the process of erection. It did specify temporary reinforcement measures at the open end of the scaffold during the erection stage, nor consider the specific measures for reinforcement by bracing when there was an obvious height difference between the scaffolding foundation and the surrounding ground.

Direct cause
The improper erection type of external scaffolding (open type) and the excessive erection height without toppling prevention measures resulted in the insufficient structural stability of the scaffolding, thus finally causing the scaffolding to tilt and topple when a sudden storm occurred.

Root causes
1. The assessment and supervision of the effectiveness of the operation of the project department and the supervision of the production safety management system was inadequate, and it had a preference on the on-site inspection and rectification of specific problems in the project safety management without paying attention to the root causes of the apparent problems of infrastructure construction projects;
2. The requirements for the on-site safety supervision and inspection of infrastructure construction projects were unclear, and the inspection was mainly based on experience, which was not deep enough to find the safety problems at the technical level.

Causal factor
The special program for external scaffolding had some defects and the enforceability of individual steps was inadequate.

Corrective Actions

1. Perform temporary tying and reinforcement measures on the west and south side of the external scaffolding.
2. Organize to establish special demolition programs to remove toppled scaffolding.
3. Quickly check the scaffolding erection of other projects of the company, and complete the rectification in time when problems are found.
4. Prepare Supervision and Management of Safety and Quality of Infrastructure Construction Projects by clarifying the requirements of the general contracting company/construction company/supervision department/company's management office and safety supervision office in each stage of the project's safety production management, further refining the supervision scope, supervision standards and requirements of each party's safety management, and establishing a supervision system of supervision at each level.
5. Organize special supervision of the effectiveness of the safety management system for each party of the EPC (Engineering Procurement Construction) consortium of the nuclear power information center project before the system takes effect;
6. Prepare and implement the Instruction for Observation of Pre-job Meeting for Infrastructure Construction Projects of Engineering Management Division by clarifying the specific requirements for project management personnel to participate in pre-job meetings for high-risk operations in the infrastructure construction projects and strengthening the requirements for risk analysis and implementation of key safety measures at pre-job meetings.
7. Upgrade the Industrial Safety Management of Owner's Infrastructure Construction Projects by specifying the requirements for inspection and supervision of high-risk operations involved in infrastructure construction projects such as working at heights & in limited space, foundation pits, formwork supported at heights, scaffolding, lifting and hoisting, demolition and blasting, specifying the inspection and supervision of important nodes, the frequency of daily inspection and supervision, and the disposal process of problems found by supervision, and proposing key requirements for the inspection of the consistency of operations and programs.
8. Establish the inspection and supervision cards for working at heights & in limited space, pit operations, operations of formwork supported at heights, scaffolding operations, lifting and hoisting operations, demolition and blasting operations in the infrastructure construction projects by clarifying content, methods and standards during the inspection for all parties participating in the high-risk operations. These cards will be treated as the attachment of Industrial Safety Management for Owner's Infrastructure Construction Projects for implementation of the procedure.
9. For each infrastructure construction project’s special construction program that has come into effect, formulate a targeted checklist as the basis for supervision of the on-site operation before the high-risk operation inspection and supervision cards come into effect.
10. Upgrade Special Construction Program of External Scaffolding for Nuclear Power Information Center Construction Project and Special Construction Safety Plan of Level 2 External Scaffolding for Nuclear Power Information Center Construction Project by clarifying the requirements of temporary reinforcement measures for external scaffolding in each phase as per the erection type and erection phases.

Attachments

- Attachment (Fangjiashan 1)

Coded Fields

| Field | Code | Description |
| --- | --- | --- |
| Category | 08 | Other events involving plant safety or reliability |
| Consequences | 10 | Non consequential or near miss |
| Systems | 000 | NONE or Unidentified |
| Components | 800 | CIVIL |
| Status | 180 | Not relevant |
| Activity | 00 | Not relevant |
| Group | 160 | Civil |
| Direct Cause | 0100 | MECHANICAL DEFICIENCY |
| Root Cause | 0801 0802 | Duties and tasks not clearly explained Progress not adequately monitored |
| Causal Factor | 0707 | Unclear or complex wording |

CONFIDENTIALITY NOTICE: Copyright © 1987-2022 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale or commercial use. This document is protected as an unpublished work under the copyright laws of all countries which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. This document and its contents are confidential and shall be treated in strictest confidence. In particular, except with the prior written consent of the WANO Coordinating Centre, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations.

LIABILITY DISCLAIMER NOTICE: This information was prepared in connection with work sponsored by the WANO. Neither WANO, WANO members, nor any person acting on the behalf of them (a) makes warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that use of any information, apparatus, method or process disclosed in this document may not infringe on privately owned rights, or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of any information, apparatus, method, or process disclosed in this document.

Конец формы