# Quick information

Penetration of active medium beyond the controlled area at Temelin NPP Unit 2

On 22 May 2014 at noon, dose rate increase in a pipeline in rooms A 016 and A 0380 (rooms of systems of emergency feeding of steam generators beyond the controlled area) was observed. Measured value was 0,75µSv/h in 0,1 meter distance from the pipeline. Dose rate measurement did not confirm penetration of the active medium beyond the valve 2TX90S04 (to the tanks of the emergency feeding of steam generators).

During subsequent investigation it was found out that the penetration of active medium to the pipelines belonging to the system of emergency feeding of steam generators (located in the reactor building at -4,2 m outside the controlled area) occurred as a consequence of the testing of the pumps of the system of unclean condensate and an internal leak of the valve which separates the systems on 18 May. The estimated volume of medium that leaked to the pipelines beyond the controlled area is around 150 l.

Low activity medium did not leak beyond pipelines of the systems, the reactor building nor to the environment, and did not endanger the personnel nor the Unit operation. Procedure for decontamination beyond the controlled area has been elaborated and implemented, and radiation monitoring of the rooms A 016 and A 0380 and their vicinity is underway.

Failure event form for this event assessed as unusual (and preliminarily assessed as INES 0) will be elaborated, and the standard investigation using operational experience feedback has been initiated.