## IGALL_Master_Table
Table number | IGALL number | Systems | Structure/ component | Ageing effect/ degradation mechanism | Critical location/ part | Material | Environment | Ageing Management Programme (AMP) | Further Action | References | Remarks | Design
101 | 1 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Class 1 piping, piping components and piping elements | Stainless steel and steel with austenitic cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 2 | Reactor pressure vessel, internals, reactor coolant system | Pump, valve | Loss of fracture toughness due to thermal ageing | Class 1 pump casings, valve bodies and bonnets | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel, AMP153 WWER Main Gate Valve, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA110 Thermal Ageing of Cast Austenitic Stainless Steels) |  |  | PWR
101 | 3 | Reactor pressure vessel, internals, reactor coolant system | Pump, valve | Cracking due to stress corrosion cracking | Class 1 pump casings, valve bodies | Steel with stainless steel cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP138 Reactor Coolant Pump, AMP153 WWER Main Gate Valve | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 4 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Closure bolting | High-strength, low alloy steel, stainless steel | Air with reactor coolant leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP115 Bolting Integrity | No |  |  | PWR
101 | 5 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Nickel alloy, stainless steel | Air with reactor coolant leakage | AMP115 Bolting Integrity | No |  |  | PWR
101 | 6 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cumulative fatigue damage due to fatigue | Pressurizer relief tank: tank shell and head, flange, nozzle | Steel with stainless steel or nickel-alloy cladding | Treated borated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 7 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
101 | 8 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cumulative fatigue damage due to fatigue | Piping and component (external surface), bolting | Steel, stainless steel | System temperature up to 340°C (644°F) | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
101 | 9 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to cyclic loading | Pressurizer: integral support | Steel, stainless steel | Air with metal temperature up to 288°C (550°F) | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 10 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer heater sheath and sleeve, heater bundle diaphragm plate | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 11 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cumulative fatigue damage due to fatigue | Reactor coolant pressure boundary components: piping, piping components, piping element, flange, nozzle and safe end, pressurizer vessel shell head, weld, heater sheath and sleeve, penetration, thermal sleeve | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Reactor coolant | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 12 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer components | Steel with stainless steel or nickel-alloy cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 13 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Reactor coolant system piping and fittings: cold leg, hot leg, surge line, spray line | Steel with stainless steel cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP153 WWER Main Gate Valve | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 14 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of fracture toughness due to thermal ageing | Class 1 piping, piping components and piping elements | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) | AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel, AMP153 WWER Main Gate Valve | No Yes, if TLAA (TLAA110 Thermal Ageing of Cast Austenitic Stainless Steels) |  |  | PWR
101 | 15 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to cyclic loading | Reactor coolant system piping and fittings: cold leg, hot leg, surge line, spray line | Steel with stainless steel cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 16 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to cyclic loading | Pressurizer components | Steel with stainless steel or nickel-alloy cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 17 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
101 | 18 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer surge and steam space nozzle, weld | Nickel alloy, Steel with stainless steel cladding | Reactor coolant, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 19 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Nickel alloy | Reactor coolant, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 20 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to general, pitting, crevice corrosion | Closure bolting | Steel | Air - indoor uncontrolled | AMP115 Bolting Integrity | No |  |  | PWR
101 | 21 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to boric acid corrosion | Closure bolting | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 22 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
101 | 23 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
101 | 24 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, flange, heater sheath and sleeve, penetration, thermal sleeve, vessel shell head, weld | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP103 Water Chemistry | No |  |  | PWR
101 | 25 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer relief tank: tank shell and head, flange, nozzle | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 26 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking (for stainless steel only), mechanical, thermal, vibratory loading | Class 1 piping, fittings and branch connections < 100mm (4 inch) | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP121 One-Time Inspection of Class 1 Small-bore piping | No |  |  | PWR
101 | 27 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Class 1 piping, piping components and piping elements | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 28 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer instrumentation penetration, heater sheath and sleeve, heater bundle diaphragm plate, manway and flange | Nickel alloy, nickel-alloy cladding, Steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 29 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Loss of material due to boric acid corrosion | External surface: reactor coolant pressure boundary piping or components adjacent to dissimilar metal (alloy 82/ 182) weld | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No |  |  | PWR
101 | 30 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer relief tank: tank shell and head, flange, nozzle | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
101 | 31 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer: spray head | Nickel alloy | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP154 WWER Pressurizer | No |  |  | PWR
101 | 32 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer: spray head | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP154 WWER Pressurizer | No |  |  | PWR
101 | 33 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
101 | 34 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel components: flange, nozzle, penetration, pressure housing, safe end, thermal sleeve, vessel shell, head, weld | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Treated borated water >60°C (>140°F) | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 35 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cumulative fatigue damage due to fatigue | Pressure vessel support skirt and attachment weld | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
101 | 36 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Closure head: vessel flange leak detection line | Stainless steel | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, a plant-specific ageing management programme | Yes, if plant- specific AMP |  | A plant-specific ageing management programme to mitigate or detect cracking | PWR
101 | 37 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of fracture toughness due to thermal ageing | Control rod drive head penetration: pressure housing | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) | AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel | No | PWR | IGALL | PWR
101 | 38 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Control rod drive head penetration: flange bolting | Stainless steel | Air with reactor coolant leakage | AMP115 Bolting Integrity | No |  |  | PWR
101 | 39 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to wear | Control rod drive head penetration: flange bolting | Stainless steel | Air with reactor coolant leakage | AMP115 Bolting Integrity | No |  |  | PWR
101 | 40 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of preload due to thermal effects, gasket creep, self-loosening | Control rod drive head penetration: flange bolting | Stainless steel | Air with reactor coolant leakage | AMP115 Bolting Integrity | No |  |  | PWR
101 | 41 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of fracture toughness due to neutron irradiation embrittlement | Nozzle: inlet, outlet, safety injection | Low alloy steel with stainless steel, nickel-alloy cladding or without cladding | Reactor coolant and neutron flux | AMP118 Reactor Vessel Surveillance, AMP152 WWER RPV Surveillance | Yes, if TLAA (TLAA102 RPV Neutron Embrittlement or/and TLAA116 Thermal Ageing of Low Alloy Steels) |  |  | PWR
101 | 42 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of fracture toughness due to neutron irradiation embrittlement | Vessel shell: upper shell, intermediate shell, lower shell (including beltline weld) | Low alloy steel with stainless steel or nickel-alloy cladding | Reactor coolant and neutron flux | AMP118 Reactor Vessel Surveillance, AMP152 WWER RPV Surveillance | Yes, if TLAA (TLAA102 RPV Neutron Embrittlement or/and TLAA116 Thermal Ageing of Low Alloy Steels) |  |  | PWR
101 | 43 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Crack growth due to cyclic loading | Vessel shell: upper shell, intermediate shell, lower shell (including beltline weld) | Low alloy steel SA508-Cl 2 forgings clad (with stainless steel) using a high-heat-input welding process | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | Yes, if TLAA (TLAA115 Fatigue and Thermal Ageing Analysis of Manufacturing Flaws) |  |  | PWR
101 | 44 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to wear | Vessel shell: vessel flange | Steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 45 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Penetration: head vent piping (top head), instrument tube (top head) | Nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 46 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Bottom-mounted instrument guide tube (external to bottom head) | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, a plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
101 | 47 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Control rod drive head penetration: nozzle weld | Nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 48 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Nozzle safe end and weld: inlet, outlet, safety injection | Stainless steel, nickel alloy weld or buttering | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 49 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to pitting, crevice corrosion | Flange, head weld, nozzle, penetration, pressure housing, safe end, vessel shell | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  |  | PWR
101 | 50 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to boric acid corrosion | External surface: reactor pressure vessel top head and bottom head | Steel | Air with reactor coolant leakage | AMP110 PWR Boric Acid Corrosion, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No |  |  | PWR
101 | 51 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Closure head: stud assembly | High-strength, low alloy steel | Air with reactor coolant leakage | AMP104 Reactor Head Closure Stud Bolting | No |  |  | PWR
101 | 52 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to general, pitting, crevice corrosion, wear | Closure head: stud assembly | High-strength, low alloy steel | Air with reactor coolant leakage | AMP104 Reactor Head Closure Stud Bolting | No |  |  | PWR
101 | 53 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cumulative fatigue damage due to fatigue | Closure head: stud assembly | High-strength, low alloy steel | Air with reactor coolant leakage | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
101 | 54 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Control rod drive head penetration: pressure housing | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 55 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Core guide lugs, core support pads | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 56 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Penetration: instrument tube (bottom head) | Nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 57 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cumulative fatigue damage due to fatigue | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 58 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 59 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 60 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Change in dimensions due to void swelling | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 61 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of preload due to thermal and irradiation enhanced stress relaxation | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 62 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 63 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 64 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 65 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Change in dimensions due to void swelling | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 66 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of preload due to thermal and irradiation enhanced stress relaxation | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 67 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 68 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to pitting, crevice corrosion | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry | No |  |  | PWR
101 | 69 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Core barrel assembly: baffle/ former assembly: accessible baffle-to-former bolts and screws, accessible locking devices (including welds) of baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 70 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of preload due to thermal and irradiation enhanced stress relaxation | Core barrel assembly: baffle/ former assembly: accessible baffle-to-former bolts and screws, accessible locking devices (including welds) of baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 71 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Core barrel assembly: baffle/ former assembly: accessible baffle-to-former bolts and screws, accessible locking devices (including welds) of baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 72 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core barrel assembly: baffle/ former assembly: accessible baffle-to-former bolts and screws, accessible locking devices (including welds) of baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 73 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to thermal ageing | Control rod guide tube (CRGT) assembly: accessible surfaces at four screw locations (every 90 degrees) for CRGT spacer castings | Cast austenitic stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 74 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Core barrel assembly: external baffle-to-baffle bolts, core barrel-to-former bolts, locking devices (including welds) of external baffle-to-baffle bolts and core barrel-to-former bolts, internal baffle-to-baffle bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 75 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of preload due to thermal and irradiation enhanced stress relaxation | Core barrel assembly: external baffle-to-baffle bolts, core barrel-to-former bolts, locking devices (including welds) of external baffle-to-baffle bolts and core barrel-to-former bolts, internal baffle-to-baffle bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 76 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Core barrel assembly: external baffle-to-baffle bolts, core barrel-to-former bolts, locking devices (including welds) of external baffle-to-baffle bolts and core barrel-to-former bolts, internal baffle-to-baffle bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 77 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to irradiation-assisted stress corrosion cracking | Core barrel assembly: external baffle-to-baffle bolts, core barrel-to-former bolts, locking devices (including welds) of external baffle-to-baffle bolts and core barrel-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 78 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Core barrel assembly: upper thermal shield bolts, surveillance specimen holder tube bolts (Davis-Besse, only), surveillance specimen tube holder studs, and nuts (Crystal River Unit 3, only) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 79 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Lower grid assembly: lower thermal shield (LTS) bolt | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 80 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Core barrel assembly: accessible lower core barrel (LCB) bolts and locking devices | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 81 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Core support shield (CSS) assembly: accessible upper core barrel (UCB) bolts and locking devices | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 82 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Core barrel assembly: baffle plate accessible surfaces within one inch around each baffle plate flow and bolt hole | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 83 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Core barrel assembly: core barrel cylinder (including vertical and circumferential seam welds), former plates | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 84 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Core support shield (CSS) assembly: CSS top flange, plenum cover assembly: plenum cover weldment rib pads and plenum cover support flange | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 85 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to thermal ageing | Core support shield (CSS) assembly: CSS vent valve disc shaft or hinge pin, CSS vent valve top retaining ring, CSS vent valve bottom retaining ring | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 86 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to thermal ageing | Core support shield (CSS) assembly: CSS cast outlet nozzles (Oconee Unit 3 and Davis-Besse, only), CSS vent valve discs | Cast austenitic stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 87 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Lower grid assembly: alloy X-750 lower grid shock pad bolt and locking device (TMI-1, only) | Nickel alloy | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 88 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Flow distributor assembly: flow distributor bolts and locking devices | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 89 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation and thermal ageing | Incore monitoring instrumentation (IMI) guide tube assembly: accessible top surfaces of IMI incore guide tube spider castings | Cast austenitic stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 90 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation and thermal ageing | Incore monitoring instrumentation (IMI) guide tube assembly: accessible top surfaces of IMI guide tube spider-to-lower grid rib sections welds | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 91 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of fracture toughness due to neutron irradiation embrittlement | Lower grid assembly: accessible pads, accessible pad-to-rib section weld, accessible alloy X-750 dowel, cap screw and locking device | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 92 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Lower grid assembly: alloy X-750 dowel-to-guide block weld | Nickel alloy | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 93 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Lower grid assembly: accessible alloy X-750 dowel-to-lower fuel assembly support pad weld | Nickel alloy | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 94 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking | Upper grid assembly: alloy X-750 dowel-to-upper fuel assembly support pad welds (all plants except Davis-Besse) | Nickel alloy | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 95 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to fatigue | Core barrel assembly: internal baffle-to-baffle bolts | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 96 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Reduction in ductility and fracture toughness due to neutron irradiation | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | Yes, if TLAA (plant-specific TLAA) |  |  | PWR
101 | 97 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking or other mechanism(s) | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 98 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 99 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to pitting, crevice corrosion | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry | No |  |  | PWR
101 | 100 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 101 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 102 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 103 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of preload due to thermal and irradiation enhanced stress relaxation | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 104 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 105 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 106 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 107 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 108 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of preload due to thermal and irradiation enhanced stress relaxation | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 109 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 110 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking and fatigue | Control element assembly (CEA): shroud assemblies: instrument guide tube in peripheral CEA assemblies | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 111 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking and fatigue | Control element assembly (CEA): shroud assemblies: remaining instrument guide tube in CEA assemblies | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 112 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Core shroud assembly (for bolted core shroud assembly): core shroud bolts (accessible) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 113 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of preload due to thermal and irradiation enhanced stress relaxation | Core shroud assembly (for bolted core shroud assembly): core shroud bolts (accessible) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 114 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core shroud assembly (for bolted core shroud assembly): core shroud bolts (accessible) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 115 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Core shroud assembly (for bolted core shroud assembly): core shroud bolts (accessible) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 116 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking | Core shroud assembly (for bolted core shroud assembly): barrel-shroud bolts with neutron exposures greater than 3 dpa | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 117 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of preload due to thermal and irradiation enhanced stress relaxation | Core shroud assembly (for bolted core shroud assembly): barrel-shroud bolts with neutron exposures greater than 3 dpa | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 118 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core shroud assembly (for bolted core shroud assembly): barrel-shroud bolts with neutron exposures greater than 3 dpa | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 119 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core shroud assembly (for bolted core shroud assembly): shroud plate, former plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 120 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Core shroud assembly (for bolted core shroud assembly): shroud plate, former plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 121 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Core shroud assembly (all plants): guide lugs and guide lug insert bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 122 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of preload due to thermal and irradiation enhanced stress relaxation | Core shroud assembly (all plants): guide lugs and guide lug insert bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 123 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to fatigue | Core shroud assembly (all plants): guide lugs and guide lug insert bolts | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 124 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking | Core shroud assembly (for welded core shrouds in two vertical sections): core shroud plate-former plate weld: the axial and horizontal weld seams at the core shroud re-entrant corners as visible from the core side of the shroud, within six inches of th | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 125 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking | Core shroud assembly (for welded core shrouds in two vertical sections): remaining axial welds in shroud plate-to-former plate | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 126 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking | Core shroud assembly (for welded core shrouds with full-height shroud plates): axial weld seams at the core shroud re-entrant corners, at the core mid-plane (+3 feet in height) as visible from the core side of the shroud | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 127 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking | Core shroud assembly (for welded core shrouds with full-height shroud plates): remaining axial welds, ribs, and rings | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 128 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Core shroud assembly (for welded core shrouds in two vertical sections): gap between the upper and lower plates | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | Yes, if TLAA (TLAA109 PWR RPV Internals Swelling) |  |  | PWR
101 | 129 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking | Core support barrel assembly: upper core support barrel flange weld (accessible surfaces) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 130 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking and fatigue | Core support barrel assembly: surfaces of the lower core barrel flange weld (accessible surfaces) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 131 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking | Core support barrel assembly: lower cylinder weld and remaining core barrel assembly weld | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 132 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Lower support structure: core support column bolt | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 133 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support structure: core support column bolt | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 134 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Core support barrel assembly: upper core barrel flange | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 135 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to fatigue | Core support barrel assembly: lower flange weld, if fatigue life cannot be demonstrated by TLAA | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | Yes, evaluate to determine the potential locations and extent of fatigue cracking, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 136 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Lower support structure: A286 fuel alignment pin (all plants with core shroud assembled with full-height shroud plates) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 137 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking and fatigue | Lower support structure: core support column weld (applicable to all plants except those assembled with full-height shroud plates) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 138 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support structure: A286 fuel alignment pin (all plants with core shroud assembled in two vertical sections) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 139 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Lower support structure: A286 fuel alignment pin (all plants with core shroud assembled in two vertical sections) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 140 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of preload due to thermal and irradiation enhanced stress relaxation | Lower support structure: A286 fuel alignment pin (all plants with core shroud assembled in two vertical sections) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 141 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Lower support structure: A286 fuel alignment pin (all plants with core shroud assembled in two vertical sections) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 142 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to fatigue | Upper internals assembly: fuel alignment plate (applicable to plants with core shrouds assembled with full height shroud plates), if fatigue life cannot be demonstrated by TLAA | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | Yes, evaluate to determine the potential locations and extent of fatigue cracking, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 143 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cumulative fatigue damage due to fatigue | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 144 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking and fatigue | Lower support structure: deep beam (applicable assembly with full height shroud plate) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 145 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to fatigue | Lower support structure: core support plate (applicable to plants with a core support plate), if fatigue life cannot be demonstrated by TLAA | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | Yes, evaluate to determine the potential locations and extent of fatigue cracking, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 146 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Incore instrumentation (ICI): ICI thimble tube - lower | Zirconium alloy (Zircaloy-4) | Reactor coolant and neutron flux | A plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
101 | 147 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to irradiation-assisted stress corrosion cracking | Core shroud assembly (for bolted core shroud assembly): shroud plate, former plate | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 148 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core shroud assembly (welded): shroud plate, former plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 149 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Change in dimensions due to void swelling | Core shroud assembly (welded): shroud plate, former plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 150 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core shroud assembly (for welded core shrouds with full-height shroud plates): axial weld seams at the core shroud re-entrant corners, at the core mid-plane (+3 feet in height) as visible from the core side of the shroud | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 151 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core shroud assembly (for welded core shrouds with full-height shroud plates): remaining axial welds, ribs, and rings | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 152 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Core support barrel assembly: lower cylinder weld | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 153 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support structure: core support column | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 154 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation and thermal ageing | Lower support structure: core support column | Cast austenitic stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 155 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support structure: core support plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 156 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support structure: deep beam (applicable assembly with full height shroud plate) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 157 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking or other mechanism(s) | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 158 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 159 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cumulative fatigue damage due to fatigue | Core support barrel assembly: lower flange weld (if fatigue analysis exists) | Stainless steel | Reactor coolant and neutron flux | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 160 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cumulative fatigue damage due to fatigue | Lower support structure: core support plate (applicable to plants with a core support plate), if fatigue analysis exists | Stainless steel | Reactor coolant and neutron flux | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 161 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cumulative fatigue damage due to fatigue | Upper internals assembly: fuel alignment plate (applicable to plants with core shrouds assembled with full height shroud plates), if fatigue analysis exists | Stainless steel | Reactor coolant and neutron flux | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 162 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to pitting, crevice corrosion | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry | No |  |  | PWR
101 | 163 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 164 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 165 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Change in dimensions due to void swelling | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 166 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 167 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Reactor pressure vessel internal components with no additional measures | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 168 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 169 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 170 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Change in dimensions due to void swelling | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 171 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 172 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Reactor pressure vessel internal components (inaccessible location) | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 173 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Change in dimensions due to void swelling | Baffle-to-former assembly: baffle and former plates | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | Yes, if TLAA (TLAA109 PWR RPV Internals Swelling) |  |  | PWR
101 | 174 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Baffle-to-former assembly: accessible baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 175 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Baffle-to-former assembly: accessible baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 176 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Change in dimensions due to void swelling | Baffle-to-former assembly: accessible baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 177 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Baffle-to-former assembly: accessible baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 178 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Baffle-to-former assembly: baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 179 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Baffle-to-former assembly: baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 180 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Change in dimensions due to void swelling | Baffle-to-former assembly: baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 181 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Baffle-to-former assembly: baffle-to-former bolts | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 182 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Baffle-to-former assembly: baffle-edge bolts (all plants with baffle-edge bolts) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 183 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core barrel assembly: upper core barrel flange weld | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 184 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking and fatigue | Core barrel assembly: core barrel outlet nozzle weld | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 185 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core barrel assembly: lower core barrel flange weld | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 186 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Core barrel assembly: lower core barrel flange weld | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 187 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking and fatigue | Core barrel assembly: core barrel flange | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel) |  |  | PWR
101 | 188 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Bottom mounted instrument: flux thimble tube | Stainless steel with or without chrome plating | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals, AMP122 PWR Flux Thimble Tube Inspection | No |  |  | PWR
101 | 189 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Lower internals assembly: clevis insert bolt | Nickel alloy | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 190 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Lower support assembly: lower support column bolt | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 191 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support assembly: lower support column bolt | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 192 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Lower support assembly: lower support column bolt | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 193 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Lower internals assembly: lower core plate, extra-long (XL) lower core plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 194 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Lower internals assembly: lower core plate, extra-long (XL) lower core plate | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 195 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking and fatigue | Lower internals assembly: lower core plate, extra-long (XL) lower core plate | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 196 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation and thermal ageing | Lower support assembly: lower support column body (cast) | Cast austenitic stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 197 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking | Lower support assembly: lower support column body (cast) | Cast austenitic stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 198 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Bottom-mounted instrumentation column bodies | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 199 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to fatigue | Bottom-mounted instrumentation column bodies | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 200 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to irradiation-assisted stress corrosion cracking | Lower support assembly: lower support column body (non-cast) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 201 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Lower support assembly: lower support column body (non-cast) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 202 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Control rod guide tube (CRGT) assemblies: CRGT guide plates (cards) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 203 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation and thermal ageing | Control rod guide tube (CRGT) assembly: CRGT lower flange weld (accessible) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 204 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking and fatigue | Control rod guide tube (CRGT) assembly: CRGT lower flange weld (accessible) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 205 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Alignment and interfacing components: upper core plate alignment pins | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 206 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Alignment and interfacing components: internals hold down spring | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 207 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Alignment and interfacing components: internals hold down spring | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 208 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking | Alignment and interfacing components: upper core plate alignment pins | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 209 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to fatigue | Thermal shield assembly: thermal shield flexure | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 210 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Thermal shield assembly: thermal shield flexure | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 211 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cumulative fatigue damage due to fatigue | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 212 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Core barrel assembly: core barrel flange | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 213 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking and fatigue | Upper internals assembly: upper support ring or skirt | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 214 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Baffle-to-former assembly: baffle-edge bolts (all plants with baffle-edge bolts) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 215 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Change in dimensions due to void swelling | Baffle-to-former assembly: baffle-edge bolts (all plants with baffle-edge bolts) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 216 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of preload due to thermal and irradiation enhanced stress relaxation | Baffle-to-former assembly: baffle-edge bolts (all plants with baffle-edge bolts) | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 217 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking and fatigue | Control rod guide tube assemblies: guide tube support pins | Nickel alloy | Reactor coolant and neutron flux | A plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
101 | 218 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Control rod guide tube assemblies: guide tube support pins | Nickel alloy | Reactor coolant and neutron flux | A plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
101 | 219 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking or other mechanism(s) | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 220 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 221 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Control rod guide tube (CRGT) assemblies: C-tube and sheath | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 222 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core barrel assembly: core barrel axial weld | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 223 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of fracture toughness due to neutron irradiation embrittlement | Core barrel assembly: core barrel axial weld | Stainless steel | Reactor coolant and neutron flux | AMP113 PWR Vessel Internals | No |  |  | PWR
101 | 224 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
101 | 225 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cumulative fatigue damage due to fatigue | Once-through steam generator components: primary side nozzle, safe end, weld | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Reactor coolant | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 226 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Change in dimensions due to corrosion of carbon steel tube support plate | Tube | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 227 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of material due to erosion | Secondary manway cover, handhole cover | Steel | Air with leaking secondary-side water and/ or steam | AMP102 In-service Inspection/ Periodic Inspection for Class 2 components | No |  |  | PWR
101 | 228 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cumulative fatigue damage due to fatigue | Steam generator components: top head, steam nozzle and safe end, upper and lower shell, feedwater (FW) and auxiliary FW nozzle and safe end, FW impingement plate and support | Steel | Secondary feed water, steam | AMP101 Fatigue Monitoring, AMP 116 Steam Generators | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 229 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Steam generator components: secondary side nozzle (vent, drain, and instrumentation) | Nickel alloy | Secondary feed water, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP 116 Steam Generators | No |  |  | PWR
101 | 230 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Steam generator components: feedwater (FW) and auxiliary FW nozzle and safe end, steam nozzle and safe end | Steel | Secondary feed water, steam | AMP114 Flow-accelerated Corrosion | No |  |  | PWR
101 | 231 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Tube plug | Nickel alloy | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 232 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Ligament cracking due to corrosion | Steam generator structural: tube support plate | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 233 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Tube and sleeve | Nickel alloy | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 234 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cumulative fatigue damage due to fatigue | Tube and sleeve | Nickel alloy | Reactor coolant, secondary feed water, steam | AMP101 Fatigue Monitoring, AMP 116 Steam Generators | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 235 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to outer diameter stress corrosion cracking | Tube and sleeve | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 236 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to intergranular attack | Tube and sleeve | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 237 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of material due to general, pitting, crevice corrosion | Steam generator components: shell assembly | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP 116 Steam Generators | No |  |  | PWR
101 | 238 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of material due to erosion, general, pitting, crevice corrosion | Steam generator: tube bundle wrapper, associated support, mounting hardware | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 239 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of material due to fretting and wear | Tube and sleeve | Nickel alloy | Secondary feed water, steam | AMP116 Steam Generators | No |  |  | PWR
101 | 240 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Instrument penetration and primary side nozzle, safe end, weld | Steel with nickel-alloy cladding, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection for Class 1 components, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components, AMP 116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 241 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | PWR
101 | 242 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Primary side components: upper and lower head and tube sheet weld exposed to reactor coolant | Steel with stainless steel or nickel-alloy cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection for Class 1 components, AMP103 Water Chemistry, AMP 116 Steam Generators | No |  |  | PWR
101 | 243 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Tube-to-tube sheet weld | Nickel alloy | Reactor coolant | AMP103 Water Chemistry, a plant-specific ageing management programme, AMP 116 Steam Generators | Yes, detection of ageing effects is to be evaluated |  | A plant-specific programme to verify effectiveness of the water chemistry | PWR
101 | 244 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Closure bolting | Steel | Air with reactor coolant leakage | AMP115 Bolting Integrity, AMP116 Steam Generators | No |  |  | PWR
101 | 245 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to boric acid corrosion | External surface | Steel | Air with reactor coolant leakage | AMP110 PWR Boric Acid Corrosion, AMP116 Steam Generators | No |  |  | PWR
101 | 246 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cumulative fatigue damage due to fatigue | Recirculating steam generator components: flange, lower head, nozzle, penetration, safe end, weld | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Reactor coolant | AMP101 Fatigue Monitoring, AMP116 Steam Generators | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 247 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cumulative fatigue damage due to fatigue | Steam generator components: top head, steam nozzle and safe end, upper and lower shell, feedwater (FW) and auxiliary FW nozzle and safe end, FW impingement plate and support | Steel | Secondary feed water, steam | AMP101 Fatigue Monitoring, AMP116 Steam Generators | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 248 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Pressure boundary and structural: steam nozzle and safe end, feedwater nozzle and safe end | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP114 Flow-accelerated Corrosion, AMP 116 Steam Generators | No |  |  | PWR
101 | 249 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to erosion | Steam generator feedwater impingement plate and support | Steel | Secondary feed water | A plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
101 | 250 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Tube plug | Nickel alloy, stainless steel, steel with stainless steel cladding | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 251 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Ligament cracking due to corrosion | Steam generator structural: tube support plate | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 252 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Change in dimensions due to corrosion of carbon steel tube support plate | Tube | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 253 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Tube and sleeve | Nickel alloy | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 254 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cumulative fatigue damage due to fatigue | Tube and sleeve | Nickel alloy | Reactor coolant, secondary feed water, steam | AMP101 Fatigue Monitoring, AMP116 Steam Generators | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 255 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to outer diameter stress corrosion cracking | Tube and sleeve | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 256 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to intergranular attack | Tube and sleeve | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 257 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to pitting corrosion, wastage | Tube and sleeve (exposed to phosphate chemistry) | Nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 258 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to erosion, general, pitting, crevice corrosion | Steam generator: tube bundle wrapper, associated support, mounting hardware | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 259 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Primary side components: divider plate | Stainless steel | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 260 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to fretting | Steam generator structural: U-bend support including anti-vibration bar | Steel, chrome plated steel, stainless steel, nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 261 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to general (steel only) pitting and crevice corrosion | Steam generator structural: U-bend support including anti-vibration bar | Steel, chrome plated steel, stainless steel, nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 262 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Steam generator: primary nozzle, nozzle to safe end weld, manway, flange | Stainless steel, steel with stainless steel cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 263 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to fretting and wear | Tube and sleeve | Nickel alloy | Secondary feed water, steam | AMP116 Steam Generators | No |  |  | PWR
101 | 264 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Instrument penetration and primary side nozzle, safe end, weld | Steel with nickel-alloy cladding, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 265 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Primary side components: divider plate | Steel with nickel-alloy cladding, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP116 Steam Generators | Yes, detection of ageing effects is to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | Supplemental examination (Alloy 600 only) | PWR
101 | 266 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to general, pitting, crevice corrosion | Steam generator components: upper and lower shell, transition cone, new transition cone closure weld | Steel | Secondary feed water, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 267 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to general, pitting, crevice corrosion | Steam generator components: shell assembly | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP116 Steam Generators | No |  |  | PWR
101 | 268 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking or other mechanism(s) | Steam generator structural: U-bend support including anti-vibration bar | Steel, chrome plated steel, stainless steel, nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 269 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity, AMP116 Steam Generators | No |  |  | PWR
101 | 270 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Wall thinning due to flow accelerated corrosion, general corrosion | Steam generator structural: tube support lattice bar | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 271 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Wall thinning due to flow accelerated corrosion | Upper assembly and separators including: feedwater inlet ring and support | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 272 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Tube-to-tube sheet weld | Nickel alloy | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators, a plant-specific ageing management programme | Yes, detection of ageing effects is to be evaluated |  | A plant-specific programme to verify effectiveness of the water chemistry | PWR
101 | 273 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Class 1 piping, piping components and piping elements | Stainless steel | Air - indoor uncontrolled (external) | A plant-specific ageing management programme | Yes, detection of ageing effects is to be evaluated |  | Supplemental examination to detect cracking | BWR, PWR
101 | 274 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant system piping (PWR) | Loss of fracture toughness due to thermal ageing | Cold leg, crossover leg, hot leg | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 275 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cumulative fatigue damage due to fatigue | RCS pump casing | Cast austenitic stainless steel | Reactor coolant | AMP101 Fatigue Monitoring, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 276 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cumulative fatigue damage due to fatigue | RCS pump flywheel | Steel | Air | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA112 Main Circulation Pump Flywheel) |  |  | PWR
101 | 277 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to boric acid corrosion | Lower head penetration, instrument nozzle | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
101 | 278 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Loss of material due to boric acid corrosion | Manway bolt | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP115 Bolting Integrity, AMP154 WWER Pressurizer | No |  |  | PWR
101 | 279 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) | Cumulative fatigue damage due to fatigue | Core barrel outlet nozzle | Stainless steel | Reactor coolant | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | PWR
101 | 280 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) | Cracking due to stress corrosion cracking | Lower core plate, lower internal assembly, lower support plate, lower support plate column, fuel alignment pin | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 281 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of fracture toughness due to thermal ageing | Control rod drive head penetration: pressure housing | Stainless steel | Reactor coolant >250°C (>482°F) | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 282 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) | Change in dimensions due to void swelling | Guide tube support pin | Nickel alloy, stainless steel | Reactor coolant | AMP113 PWR Vessel Internals | Yes, if TLAA (TLAA109 PWR RPV Internals Swelling) |  |  | PWR
101 | 283 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (PWR) | Loss of material due to general, pitting, crevice corrosion | Secondary side tube support plate | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 284 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (PWR) | Loss of material due to wear | Primary side tube, tube plug | Stainless steel, steel with stainless steel cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP116 Steam Generators | No |  |  | PWR
101 | 285 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking | Lower internals assembly: clevis insert bolt | Stainless steel (316) | Reactor coolant | AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 286 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Reduction of heat transfer due to fouling | Tube | Nickel alloy (Alloy 690 SB166 UNS N06690) | Reactor coolant | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 287 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Reduction of heat transfer due to fouling | Tube | Nickel alloy (Alloy 690 SB166 UNS N06690) | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 288 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to flow-induced vibration | Tube at tube support plate | Nickel alloy, stainless steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | NoYes, if TLAA (TLAA107 High-Cycle Fatigue For Steam Generator Tubes) |  |  | PWR
101 | 289 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Reduction of heat transfer due to fouling | Tube at tube support plate | Stainless steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 290 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Change in dimensions due to fouling at the tubesheet level | Tube at tubesheet level | Alloy 800 NG | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 291 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to crevice corrosion (caused by fouling at the tubesheet level) | Tube at tubesheet level | Alloy 800 NG | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 292 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of fracture toughness due to thermal ageing | Non irradiated weld and base metal | Low alloy steel with stainless steel cladding (WWER-1000) | Reactor coolant | AMP118 Reactor Vessel Surveillance, AMP152 WWER RPV Surveillance | Yes, if TLAA (TLAA102 RPV Neutron Embrittlement) | PWR | IGALL | PWR
101 | 293 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to erosion | Pump casing, weld | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 294 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Pump casing, weld | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 295 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Pressure cover | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 296 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Pressure cover | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 297 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to erosion | Nozzle | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 298 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to fatigue | Environments of the flanged joints of the main plane of split | Austenitic steel, Ni sealing ring, high-strength steel bolt and screw | Air with borated water leakage | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 299 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Environments of the flanged joints of the main plane of split | Austenitic steel, Ni sealing ring, high-strength steel bolt and screw | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 300 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Environments of the flanged joints of the main plane of split | Austenitic steel, Ni sealing ring, high-strength steel bolt and screw | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 301 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to fatigue | Sealing surface of the main flange | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
101 | 302 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Sealing surface of the main flange | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 303 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Sealing surface of the main flange | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 304 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Driving wheel | Cast austenitic stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 305 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to erosion | Driving wheel | Cast austenitic stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 306 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Components of the sealing-block casing | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 307 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to corrosion | Supporting frame, support holding | Steel | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 308 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to boric acid corrosion | Supporting frame, support holding | Steel | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 309 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (WWER) | Cracking due to stress corrosion cracking | Steam generator: dissimilar weld | Steel, stainless steel | Secondary water | AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 310 | Reactor pressure vessel, internals, reactor coolant system | Reactor Coolant Pump (WWER) | Cracking due to high cycle thermal fatigue | Guiding unit and fixing ring-shaped cover | Austenitic steel | Reactor coolant, treated borated water | AMP138 Reactor Coolant Pump | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
102 | 1 | Reactor pressure vessel, internals, reactor coolant system | Pump, valve | Loss of fracture toughness due to thermal ageing | Class 1 pump casings, valve bodies and bonnets | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) | AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel | No Yes, if TLAA (TLAA110 Thermal Ageing of Cast Austenitic Stainless Steels) |  |  | BWR
102 | 2 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Isolation condenser components | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | Yes, detection of ageing effects is to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 3 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Piping, piping component, piping element greater than or equal to 4 NPS | Stainless steel | Reactor coolant | AMP103 Water Chemistry, AMP107 BWR Stress Corrosion Cracking in Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 4 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Piping, piping component, piping element greater than or equal to 4 NPS | Nickel alloy | Reactor coolant | AMP103 Water Chemistry, AMP107 BWR Stress Corrosion Cracking in Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 5 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cumulative fatigue damage due to fatigue | Reactor coolant pressure boundary components: piping, piping component, piping element | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Reactor coolant | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  | Fatigue is a TLAA evaluated and for Class 1 components environmental effects on fatigue are to be addressed according to national requirements | BWR
102 | 6 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to cyclic loading | Isolation condenser components | Steel, stainless steel | Reactor coolant | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 7 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Reactor coolant | AMP114 Flow-accelerated Corrosion | No |  | Relevant to Feedwater piping and Bottom Head Drain Line | BWR
102 | 8 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of fracture toughness due to thermal ageing | Class 1 piping, piping components and piping elements | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) | AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel | No Yes, if TLAA (TLAA110 Thermal Ageing of Cast Austenitic Stainless Steels) |  |  | BWR
102 | 9 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of material due to pitting, crevice corrosion | Reactor coolant pressure boundary component | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
102 | 10 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, cyclic loading | Class 1 piping, fittings and branch connections < 100mm (4 inch) | Steel, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP121 One-Time Inspection of Class 1 Small-bore piping | No |  | ISI depending on national requirements | BWR
102 | 11 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking (for stainless steel only), mechanical, thermal, vibratory loading | Isolation condenser components | Steel, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | Checking the condition of ageing degradation with visual inspection or something during regular dismantling inspection is required. | BWR
102 | 12 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of material due to general (steel only) pitting and crevice corrosion | Closure bolting | Steel, stainless steel | Air with reactor coolant leakage | AMP115 Bolting Integrity | No |  |  | BWR
102 | 13 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of material due to general (steel only) pitting and crevice corrosion or wear | Closure bolting | Steel, stainless steel | Air | AMP115 Bolting Integrity | No |  |  | BWR
102 | 14 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of preload due to thermal effects, gasket creep, self-loosening | Pump and valve closure bolting | Steel, stainless steel | System temperature up to 288°C (550°F) | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
102 | 15 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel components: flange, nozzle, penetration, safe end, thermal sleeve, vessel shell, head, weld | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Reactor coolant | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  | Fatigue is a TLAA evaluated and for Class 1 components environmental effects on fatigue are to be addressed according to national requirements. | BWR
102 | 16 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Top head enclosure: vessel flange leak detection line | Nickel alloy, stainless steel | Air with reactor coolant leakage (internal) or reactor coolant | A plant-specific ageing management programme | Yes, if plant- specific AMP |  | A plant-specific ageing management programme is to be evaluated because existing programs may not be capable of mitigating or detecting crack initiation and growth due to SCC in the vessel flange leak detection line | BWR
102 | 17 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cumulative fatigue damage due to fatigue Loss of fracture toughness due to neutron irradiation embrittlement | Vessel shell: intermediate beltline shell, beltline weld | Low alloy steel with or without stainless steel cladding | Reactor coolant and neutron flux | AMP118 Reactor Vessel Surveillance | Yes, if TLAA (TLAA102 RPV Neutron Embrittlement) |  | This is a major issue and for AMP18 there a several national regulations | BWR
102 | 18 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of fracture toughness due to neutron irradiation embrittlement Cracking due to SCC | Vessel shell: attachment weld | Nickel alloy, stainless steel | Reactor coolant | AMP103 Water Chemistry, AMP105 BWR Vessel ID Attachment Welds, AMP107 BWR Stress Corrosion Cracking in Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 19 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to cyclic loading | Nozzle: feedwater | Steel with or without stainless steel cladding | Reactor coolant | AMP101 Fatigue Monitoring, AMP106 BWR Feedwater Nozzle | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA113 Thermal Stratification, TLAA119 High-cycle Thermal Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 20 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking Cracking due to cyclic loading | Nozzle: control rod drive return line | Steel with or without stainless steel cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP123 BWR Control Rod Drive Return Line Nozzle | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | ISI e.g. VT, UT | BWR
102 | 21 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to cyclic loading Loss of fracture toughness due to neutron irradiation embrittlement | Nozzle: low-pressure coolant injection or RHR injection mode | SteelLow alloy steel with or without stainless steel cladding | Reactor coolant and neutron flux | AMP118 Reactor Vessel Surveillance | Yes, if TLAA (TLAA102 RPV Neutron Embrittlement) |  |  | BWR
102 | 22 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of fracture toughness due to neutron irradiation embrittlement Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Nozzle safe end and weld: high-pressure core spray, low pressure core spray, control rod drive return line, recirculating water, low pressure coolant injection or RHR injection mode | Nickel alloy, stainless steel | Reactor coolant | AMP103 Water Chemistry, AMP107 BWR Stress Corrosion Cracking in Coolant Pressure Boundary Components | No |  | If applicable, the CRD return nozzle cap has to be taken into account. Cold worked area just as machine (instrumentation) nozzles (stainless steel) have to be taken into account. | BWR
102 | 23 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Pressure vessel support skirt and attachment weld | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | In many cases the inspection here is very restricted | BWR
102 | 24 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel: flange, nozzle, penetration, safe end, vessel shell, head, weld | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  |  | BWR
102 | 25 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of material due to pitting, crevice corrosion | Top head enclosure: closure stud, nut | High-strength, low alloy steel | Air with reactor coolant leakage | AMP102 In-service Inspection/ Periodic Inspection | No |  | ISI - PT, ET | BWR
102 | 26 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of material due to general, pitting, crevice corrosion, wear | Top head enclosure: closure stud, nut | High-strength, low alloy steel | Air with reactor coolant leakage | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
102 | 27 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cumulative fatigue damage due to fatigue Loss of fracture toughness due to neutron irradiation embrittlement | Vessel shell (including applicable beltline) components: shell, shell plate or forging, shell weld, nozzle plate or forging, nozzle weld | Low alloy steel with or without cladding | Reactor coolant and neutron flux | AMP118 Reactor Vessel Surveillance | Yes, if TLAA (TLAA102 RPV Neutron Embrittlement) |  |  | BWR
102 | 28 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, cyclic loading | Penetration: control rod drive stub tube, in core monitor housing, jet pump instrument, standby liquid control, flux monitor vessel instrumentation penetrations, control rod drive housing (CRDH) and incore-monitoring housing (ICMH) penetrations and standby liquid control (SLC) nozzles/Core ΔP nozzles | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP108 BWR Penetrations | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | No safety issue , see IAEA Techdoc 1470 VT may be performed during hydro- of pressure test, ISI - VT | BWR
102 | 29 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of fracture toughness due to neutron irradiation embrittlement | Penetration: drain line | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  |  | BWR
102 | 30 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Top head enclosure (without cladding): top head, nozzle (vent, top head spray or RCIC and spare) | Steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP119 One-Time Inspection | No |  | ISI - PT, VT | BWR
102 | 31 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of material due to general, pitting, crevice corrosion, wear | Top head enclosure: closure stud, nut Closure head: stud assembly | High-strength, low alloy steel | Air with reactor coolant leakage | AMP104 Reactor Head Closure Stud Bolting | No |  |  | BWR
102 | 32 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking | Closure head: stud assembly | High-strength, low alloy steel | Air with reactor coolant leakage | AMP104 Reactor Head Closure Stud Bolting | No | BWR | IGALL | BWR
102 | 33 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Jet pump assembly: thermal sleeve, inlet header, riser brace arm, holddown beam, inlet elbow, mixing assembly, diffuser casting | Nickel alloy, stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | Not applicable to certain design (internal recirculation pumps) | BWR
102 | 34 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Fuel supports and control rod drive assemblies: control rod drive housing | Stainless steel | Reactor coolant | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 35 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Instrumentation: incore neutron flux monitor guide tube, intermediate range monitor (IRM) dry tube, source range monitor (SRM) dry tube | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | Component should be replaced after e.g. 15 years | BWR
102 | 36 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  | A TLAA is not mandatory because only a few location will undergo fatigue. GE design: Special attention should be drawn to the jet pump braces. Fatigue is a TLAA evaluated and for Class 1 components environmental effects on fatigue are to be addressed acco | BWR
102 | 37 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core shroud (including repairs) and core plate: core shroud (upper, central, lower) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | IASCC: Neutron fluence analysis can be used to adjust the inspection programme | BWR
102 | 38 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core shroud and core plate: core plate and plate bolts (used in early BWRs) | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | IASCC: Neutron fluence analysis can be used to adjust the inspection programme | BWR
102 | 39 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core shroud and core plate: access hole cover (welded) | Nickel alloy | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | IASCC: Neutron fluence analysis can be used to adjust the inspection programme | BWR
102 | 40 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core shroud and core plate: access hole cover (mechanical) | Nickel alloy | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 41 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core shroud (including repairs) and core plate: shroud support structure (shroud support cylinder, shroud support plate, shroud support legs) | Nickel alloy, stainless steel, Nickel alloy (X-750), Nickel alloy (XM19) | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 42 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core shroud and core plate: LPCI coupling | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | IASCC: Neutron fluence analysis can be used to adjust the inspection programme | BWR
102 | 43 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Top guide | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | IASCC: Neutron fluence analysis can be used to adjust the inspection programme | BWR
102 | 44 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, irradiation-assisted stress corrosion cracking | Core spray lines and spargers: core spray lines (headers), spray rings, spray nozzles, thermal sleeves | Stainless steel | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA121 IASCC Fluence Limit for Stainless Steel and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | IASCC: Neutron fluence analysis can be used to adjust the inspection programme | BWR
102 | 45 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to flow-induced vibration | Steam dryer | Stainless steel | Reactor coolant | AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 46 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of fracture toughness due to neutron irradiation and thermal ageing | Reactor pressure vessel internal components | PH martensitic stainless steel (17-4PH and 15-5PH), martensitic stainless steel (SS 403, 410, 431, etc.) | Reactor coolant >250°C (>482°F) and neutron flux | AMP109 BWR Vessel Internals | No |  |  | BWR
102 | 47 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of fracture toughness due to neutron irradiation embrittlement | Reactor pressure vessel internal components | Nickel alloy (X-750) | Reactor coolant and neutron flux | AMP109 BWR Vessel Internals | No |  |  | BWR
102 | 48 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of fracture toughness due to neutron irradiation and thermal ageing | Jet pump assembly: casting | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) and neutron flux | AMP109 BWR Vessel Internals | No |  | It is an open issue whether neutron embrittlement is potential degradation mechanism or not. | BWR
102 | 49 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of material due to pitting, crevice corrosion Loss of fracture toughness due to neutron irradiation and thermal ageing embrittlement | Fuel supports and control rod drive assemblies: orificed fuel support | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) and neutron flux | AMP109 BWR Vessel Internals | No |  |  | BWR
102 | 50 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of fracture toughness due to neutron irradiation and thermal ageing | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  | ISI - VT | BWR
102 | 51 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of material due to wear | Reactor pressure vessel internals components: jet pump wedge surface | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No |  | ISI - VT | BWR
102 | 52 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cracking due to intergranular stress corrosion cracking Loss of material due to wear | Reactor pressure vessel internals components: jet pump wedge surface | Nickel alloy (X-750) | Reactor coolant and neutron flux | AMP103 Water Chemistry, AMP109 BWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
103 | 1 | Primary heat transport system | Primary coolant pump | Cumulative fatigue damage due to fatigue | Flywheel | Steel | Air | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA112 Main Circulation Pump Flywheel) |  |  | CANDU/ PHWR
103 | 2 | Primary heat transport system | Auxiliary PHT circuit piping | Cracking due to stress corrosion cracking | Cold leg, hot leg, surge line, spray line, reducing tees, dissimilar metal welds | Nickel alloy, stainless steel, steel | Primary heat transport coolant (D2O) >260°C (500°F) | AMP103 Water Chemistry, AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP146 CANDU/ PHWR In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 3 | Primary heat transport system | Auxiliary PHT circuit piping | Cumulative fatigue damage due to fatigue | Cold leg, hot leg, surge line, spray line, reducing tees, dissimilar metal welds | Nickel alloy, stainless steel, steel | Primary heat transport coolant (D2O) >260°C (500°F) | AMP101 Fatigue Monitoring, AMP103 Water Chemistry, AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue, TLAA 113 Thermal Stratification) |  |  | CANDU/ PHWR
103 | 4 | Primary heat transport system | Feeder piping | Cracking due to stress corrosion cracking | Outlet feeder piping at dissimilar metal weld for flow orifice | Alloy 600 and weld metal alloy 82 to carbon steel | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 5 | Primary heat transport system | Feeder piping | Cracking due to stress corrosion cracking or other mechanisms (hydrogen assisted stress cracking) | Outlet feeder piping at non-stress relieved tight radius bend and at field-repaired weld (location of high tensile residual stress) | Carbon steel (SA106 Gr B or C) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 6 | Primary heat transport system | Feeder piping | Cumulative fatigue damage due to fatigue | Tight radius bend and weld near or at Grayloc connection | Carbon steel (SA106 Gr B or C, SA333 Gr 6) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP101 Fatigue Monitoring, AMP103 Water Chemistry, AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
103 | 7 | Primary heat transport system | Feeder piping | Loss of fracture toughness due to dynamic strain ageing (temperature and strain rate) | Outlet feeder piping | Carbon steel (SA106 Gr B or C, SA333 Gr 6) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 8 | Primary heat transport system | Feeder piping | Loss of fracture toughness due to thermal ageing | Outlet feeder piping at location with cold-worked material and the presence of hydrogen from FAC, location with low wall thickness is more problematic | Carbon steel (SA106 Gr B or C, SA333 Gr 6) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 9 | Primary heat transport system | Feeder piping | Increased flow resistance due to fouling | Inlet feeder piping | Carbon steel (SA106 Gr B or C, SA333 Gr 6) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 10 | Primary heat transport system | Feeder piping | Loss of material due to general corrosion | Outside surface of feeder piping | Carbon steel (SA106 Gr B or C) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 11 | Primary heat transport system | Feeder piping | Loss of material due to fretting and wear | Outside surface of feeder piping (at free end of fuel channel) at low clearances between adjacent components | Carbon steel (SA106 Gr B or C) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 12 | Primary heat transport system | Feeder piping | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Outlet feeder piping at tight radius bend and weld near or at Grayloc connection | Carbon steel (SA106 Gr B or C, SA333 Gr 6) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP114 Flow-accelerated Corrosion, AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 13 | Primary heat transport system | Feeder piping | Wall thinning due to preferential weld attack | Weld in outlet feeder with high coolant velocity and located downstream of flow disturbances such as bends and reducers or coupling steels with different Cr concentration | Carbon steel (SA106 Gr B or C, SA333 Gr 6) | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP140 CANDU/ PHWR Feeder Piping, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 14 | Primary heat transport system | Fuel, coolant channel - annulus spacer | Change of material properties, including reduction in fracture toughness, due to neutron irradiation and thermal embrittlement and hydrogen/ deuterium uptake | High power fuel channel | Tight fitting: Inconel X-750 coil with zircalloy-2 girdle wire. Loose fitting: zircalloy spacers, Zr-2.5% Nb-0.5Cu | CO2 gas and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 15 | Primary heat transport system | Fuel, coolant channel - annulus spacer | Movement or shifting due to sustained vibratory loading | High power fuel channel | Tight fitting: Inconel X-750 coil with zircalloy-2 girdle wire. Loose fitting: zircalloy spacers, Zr-2.5% Nb-0.5Cu | CO2 gas and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 16 | Primary heat transport system | Fuel, coolant channel - pressure tube | Change of material properties, including reduction in fracture toughness, due to neutron irradiation embrittlement and hydrogen/ deuterium uptake | High power fuel channel | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA111 CANDU/PHWR Hydrogen Embrittlement and Delayed Hydride Cracking in Pressure Tubes) |  |  | CANDU/ PHWR
103 | 17 | Primary heat transport system | Fuel, coolant channel - pressure tube | Loss of material due to crevice corrosion | Fuel bundle bearing pad locations on inner surface of pressure tube in the outlet half | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP103 Water Chemistry, AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 18 | Primary heat transport system | Fuel, coolant channel - pressure tube | Loss of material due to corrosion | High power fuel channel | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP103 Water Chemistry, AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 19 | Primary heat transport system | Fuel, coolant channel - pressure tube | Cracking due to delayed hydride cracking (DHC) | Pressure tube at inlet and outlet rolled joints where deuterium uptake rate is high and residual tensile stresses, defect locations, if pressure tube contacts calandria tube | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP103 Water Chemistry, AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA111 CANDU/PHWR Hydrogen Embrittlement and Delayed Hydride Cracking in Pressure Tubes) |  |  | CANDU/ PHWR
103 | 20 | Primary heat transport system | Fuel, coolant channel - pressure tube | Cracking due to fatigue | Pressure tube at defect location | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP103 Water Chemistry, AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 21 | Primary heat transport system | Fuel, coolant channel - pressure tube | Increased flow resistance due to fouling | Fuel, coolant channel inlet end-fitting and inlet end of pressure tube | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP103 Water Chemistry, AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 22 | Primary heat transport system | Fuel, coolant channel - pressure tube | Change in dimensions due to irradiation-assisted deformation (pressure tube and calandria tube sag) | High power fuel channel | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA105 CANDU/ PHWR Fuel Channel Creep) |  |  | CANDU/ PHWR
103 | 23 | Primary heat transport system | Fuel, coolant channel - pressure tube | Change in dimensions due to irradiation-assisted deformation (pressure tube creep elongation) | High power fuel channel | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA105 CANDU/ PHWR Fuel Channel Creep) |  |  | CANDU/ PHWR
103 | 24 | Primary heat transport system | Fuel, coolant channel - pressure tube | Change in dimensions due to irradiation-assisted deformation (pressure tube diametral creep) | High power fuel channel | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA105 CANDU/ PHWR Fuel Channel Creep) |  |  | CANDU/ PHWR
103 | 25 | Primary heat transport system | Fuel, coolant channel - pressure tube | Loss of material due to fretting | Internal surface at fuel bundle bearing pad location | Zirconium alloy (Zr-2.5%Nb) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 26 | Primary heat transport system | Inlet and outlet headers | Cumulative fatigue damage due to fatigue | Nozzle | Carbon steel | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
103 | 27 | Primary heat transport system | Inlet and outlet headers | Cracking damage due to fatigue | Weld | Carbon steel | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 28 | Primary heat transport system | Header | Loss of material due to corrosion, erosion | Junction of piping and header | SA350 Gr LF2 | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 29 | Primary heat transport system | Piping, piping components and piping elements | Cracking due to fatigue | Weld | Carbon steel (SA106 Gr B or C) | Primary heat transport coolant (D2O), 249 - 293°C (480°F - 559°F) | AMP101 Fatigue Monitoring, AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
103 | 30 | Primary heat transport system | Pressurizer | Cracking due to stress corrosion cracking, primary water stress corrosion cracking | Pressurizer internal components | Steel with stainless steel or nickel-alloy cladding, stainless steel | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA117 Under Clad Cracking, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 31 | Primary heat transport system | Pressurizer | Cracking due to fatigue | Weld, dissimilar metal weld | Steel | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP101 Fatigue Monitoring, AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 32 | Primary heat transport system | Pressurizer | Cracking due to fatigue | Pressurizer: integral support | Steel, stainless steel | Air with metal temperature up to 288°C (550°F) | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 33 | Primary heat transport system | Pressurizer/ bleed condenser | Cracking due to fatigue | Pressurizer surge and steam space nozzle, bleed condenser heat exchanger tube | Nickel alloy | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP101 Fatigue Monitoring, AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 34 | Primary heat transport system | Bleed condenser (shell and tube type) | Loss of material due to corrosion, erosion | Internal surface | Steel, stainless steel | Primary heat transport coolant (D2O), 249 - 293°C (480°F - 559°F) | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 35 | Primary heat transport system | Pump, valve | Wall thinning due to corrosion and erosion | Internal surface | Steel | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 36 | Primary heat transport system | Primary coolant pump | Loss of fracture toughness due to thermal ageing | Casing | SA352 Gr LCB | Primary heat transport coolant (D2O), 249 - 310°C (480°F - 590°F) | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA115 Fatigue and Thermal Ageing Analysis of Manufacturing Flaws) |  |  | CANDU/ PHWR
103 | 37 | Primary heat transport system | Primary coolant pump | Cracking due to stress corrosion cracking | Casing and valve bodies | SA352 Gr LCB, SA182 Gr F304, SA182 Gr F316 | Primary heat transport coolant (D2O), 249 - 293°C (480°F - 559°F) | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 38 | Primary heat transport system | Primary coolant pump | Cracking due to fatigue | Casing | SA352 Gr LCB, SA182 Gr F304, SA182 Gr F316 | Primary heat transport coolant (D2O), 249 - 293°C (480°F - 559°F) | AMP101 Fatigue Monitoring, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA119 High-cycle Thermal Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 39 | Primary heat transport system | Primary coolant pump | Loss of material due to wear | Pump internals | SA352 Gr LCB, SA182 Gr F304, SA182 Gr F316 | Primary heat transport coolant (D2O), 249 - 293°C (480°F - 559°F) | AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 40 | Primary heat transport system | Steam generator (recirculating) | Change in dimensions due to corrosion of carbon steel tube support plate | Tube | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 41 | Primary heat transport system | Steam generator (recirculating) | Cracking due to intergranular attack | Tube and sleeve | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 42 | Primary heat transport system | Steam generator (recirculating) | Cracking due to outer diameter stress corrosion cracking | Tube and sleeve | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 43 | Primary heat transport system | Steam generator (recirculating) | Cracking due to primary water stress corrosion cracking | Tube plug weld | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Primary heat transport coolant (D2O) | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 44 | Primary heat transport system | Steam generator (recirculating) | Cracking due to primary water stress corrosion cracking | Tube and sleeve | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Primary heat transport coolant (D2O) | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 45 | Primary heat transport system | Steam generator (recirculating) | Cracking due to primary water stress corrosion cracking | Tube-to-tube sheet weld | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Primary heat transport coolant (D2O) | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
103 | 46 | Primary heat transport system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Steam generator: primary nozzle, nozzle to safe end weld, manway, flange | Stainless steel, steel with stainless steel cladding | Primary heat transport coolant (D2O) | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 47 | Primary heat transport system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Closure bolting | Steel | Air with primary heat transport coolant (D2O) leakage | AMP115 Bolting Integrity | No |  |  | CANDU/ PHWR
103 | 48 | Primary heat transport system | Steam generator (recirculating) | Cracking due to stress corrosion cracking or other mechanism(s) | Steam generator structural: U-bend support including anti-vibration bar | Steel, chrome plated steel, stainless steel, nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes, AMP114 Flow-accelerated Corrosion | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 49 | Primary heat transport system | Steam generator (recirculating) | Cracking damage due to fatigue | Steam generator components: top head, steam nozzle and safe end, upper and lower shell, feedwater (FW) and auxiliary FW nozzle and safe end, FW impingement plate and support | Steel | Secondary feed water, steam | AMP101 Fatigue Monitoring, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 50 | Primary heat transport system | Steam generator (recirculating) | Cracking due to fatigue | Tube and sleeve | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Primary heat transport coolant (D2O) coolant and secondary feed water/ steam | AMP101 Fatigue Monitoring, AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA107 High-Cycle Fatigue For Steam Generator Tubes) |  |  | CANDU/ PHWR
103 | 51 | Primary heat transport system | Steam generator (recirculating) | Increased flow resistance due to fouling (precipitation of magnetite on inner surfaces from feeder FAC) | Tube and sleeve | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Primary heat transport coolant (D2O), 260 - 310°C (480°F - 590°F) | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 52 | Primary heat transport system | Steam generator (recirculating) | Ligament cracking due to corrosion, reduction of flow due to fouling of flow holes | Steam generator structural: tube support plate | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
103 | 53 | Primary heat transport system | Steam generator (recirculating) | Loss of material due to erosion | Steam generator feedwater impingement plate and support | Steel | Secondary feed water | AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 54 | Primary heat transport system | Steam generator (recirculating) | Loss of material due to fretting and wear | Tube and sleeve | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Secondary feed water, steam | AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 55 | Primary heat transport system | Steam generator (recirculating) | Loss of material due to general (steel only) pitting and crevice corrosion | Steam generator structural: U-bend support including anti-vibration bar | Steel, chrome plated steel, stainless steel, nickel alloy | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 56 | Primary heat transport system | Steam generator (recirculating) | Loss of material due to pitting corrosion, wastage | Tube and sleeve (exposed to phosphate chemistry) | Nickel alloy (Incoloy 800, Inconel 600, Monel 400) | Secondary feed water, steam | AMP103 Water Chemistry, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
103 | 57 | Primary heat transport system | Steam generator (recirculating) | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | CANDU/ PHWR
103 | 58 | Primary heat transport system | Steam generator (recirculating) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Pressure boundary and structural: steam nozzle and safe end, feedwater nozzle and safe end | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP114 Flow-accelerated Corrosion, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 59 | Primary heat transport system | Steam generator (recirculating) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Upper assembly and separators including: feedwater inlet ring and support | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP114 Flow-accelerated Corrosion, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes, AMP114 Flow-accelerated Corrosion | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 60 | Primary heat transport system | Steam generator (recirculating) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Steam generator structural: tube support plate | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP114 Flow-accelerated Corrosion, AMP116 Steam Generators, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 61 | Primary heat transport system | Fuel, coolant channel - end fitting assembly | Loss of leak tightness due to creep | Rolled joint | Stainless steel 403 (modified) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP139 CANDU/ PHWR Fuel Coolant Channels | No |  |  | CANDU/ PHWR
103 | 62 | Primary heat transport system | Fuel, coolant channel - end fitting assembly | Cracking due to stress corrosion cracking | Rolled joint | Stainless steel 403 (modified) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP103 Water Chemistry, AMP139 CANDU/ PHWR Fuel Coolant Channels, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analysis) |  |  | CANDU/ PHWR
103 | 63 | Primary heat transport system | Fuel, coolant channel - end fitting assembly | Loss of fracture toughness due to thermal ageing | Rolled joint | Stainless steel 403 (modified) | Primary heat transport coolant (D2O) 249 - 310°C (480°F - 590°F) and neutron flux | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA122 Thermal Ageing of Martensitic Stainless Steels) |  |  | CANDU/ PHWR
103 | 64 | Primary heat transport system | PHT storage tank | Loss of material due to general corrosion | Internal surface | Carbon steel | Primary heat transport coolant (D2O) | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
103 | 65 | Primary heat transport system | Regenerative heat exchanger (shell and tube type) | Loss of material due to general corrosion, MIC and biofouling | Shell, nozzle | Steel | Secondary feed water, steam | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
104 | 1 | Engineered safety features | Containment spray system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP134 External Surfaces monitoring of Mechanical Components (for tank) | No |  |  | PWR
104 | 2 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 3 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general corrosion | Ducting, piping and components (external surfaces) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | PWR
104 | 4 | Engineered safety features | Containment spray system (PWR) | Loss of material due to boric acid corrosion | External surface (of what?) | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 5 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general corrosion | Piping and component (internal surface) | Steel | Air - indoor uncontrolled (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 6 | Engineered safety features | Containment spray system (PWR) | Loss of material due to selective leaching | Motor cooler | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 7 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 8 | Engineered safety features | Containment spray system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 9 | Engineered safety features | Containment spray system (PWR) | Loss of material due to selective leaching | Heat exchanger components | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 10 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Treated borated water | AMP103 Water Chemistry | No |  |  | PWR
104 | 11 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general, pitting, crevice corrosion | Encapsulation components | Steel | Air - indoor uncontrolled (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 12 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general, pitting, crevice, boric acid corrosion | Encapsulation components | Steel | Air with borated water leakage (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 13 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 14 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 15 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 16 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 17 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 18 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 19 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element (internal surfaces), tank | Stainless steel | Condensation (Internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 20 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general, pitting, crevice, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 21 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice, MIC, fouling that leads to corrosion | Heat exchanger components | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 22 | Engineered safety features | Containment spray system (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 23 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice corrosion | Heat exchanger components | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 24 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice, galvanic corrosion | Heat exchanger components | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 25 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 26 | Engineered safety features | Containment spray system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 27 | Engineered safety features | Containment spray system (PWR) | Loss of material due to pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 28 | Engineered safety features | Containment spray system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 29 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Partially-encased tanks with breached moisture barrier | Stainless steel | Raw water | A plant-specific ageing management programme | Yes, if plant- specific AMP |  | A plant-specific aging management programme is to be evaluated for pitting and crevice corrosion of tank bottom because moisture and water can egress under the tank due to cracking of the perimeter seal from weathering | PWR
104 | 30 | Engineered safety features | ECCS (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry | No |  |  | PWR
104 | 31 | Engineered safety features | ECCS (PWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Stainless steel | Treated borated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 32 | Engineered safety features | ECCS (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 33 | Engineered safety features | ECCS (PWR) | Loss of material due to erosion | Orifice (miniflow recirculation) | Stainless steel | Treated borated water | A plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
104 | 34 | Engineered safety features | ECCS (PWR) | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | PWR
104 | 35 | Engineered safety features | ECCS (PWR) | Cracking due to stress corrosion cracking | Safety injection tank (accumulator) | Steel with stainless steel or nickel-alloy cladding | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry | No |  |  | PWR
104 | 36 | Engineered safety features | ECCS (PWR) | Loss of material due to selective leaching | Motor cooler | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 37 | Engineered safety features | ECCS (PWR) | Loss of fracture toughness due to thermal ageing | Piping, piping component, piping element | Cast austenitic stainless steel | Treated borated water >250°C (>482°F) Reactor coolant >250°C (>482°F) | AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel | No Yes, if TLAA (TLAA110 Thermal Ageing of Cast Austenitic Stainless Steels) |  |  | PWR, BWR
104 | 38 | Engineered safety features | ECCS (PWR) | Loss of material due to boric acid corrosion | Piping, piping component, piping element | Aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 39 | Engineered safety features | ECCS (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 40 | Engineered safety features | ECCS (PWR) | Loss of material due to selective leaching | Heat exchanger components | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 41 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Treated borated water | AMP103 Water Chemistry | No |  |  | PWR
104 | 42 | Engineered safety features | ECCS (PWR) | Loss of material due to corrosion following cladding breach | Pump casing | Steel with stainless steel cladding | Treated borated water | A plant-specific ageing management programme | Yes, verify that plant-specific program addresses clad breach |  |  | PWR
104 | 43 | Engineered safety features | ECCS (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 44 | Engineered safety features | ECCS (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | PWR
104 | 45 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 46 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  |  | PWR
104 | 47 | Engineered safety features | ECCS (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 48 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 49 | Engineered safety features | ECCS (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 50 | Engineered safety features | ECCS (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 51 | Engineered safety features | ECCS (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 52 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 53 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element (internal surfaces), tank | Stainless steel | Condensation (Internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 54 | Engineered safety features | ECCS (PWR) | Loss of material due to general, pitting, crevice, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 55 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice, MIC, fouling that leads to corrosion | Heat exchanger components | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 56 | Engineered safety features | ECCS (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 57 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Heat exchanger components | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 58 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice, galvanic corrosion | Heat exchanger components | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 59 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 60 | Engineered safety features | ECCS (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 61 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 62 | Engineered safety features | ECCS (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 63 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, | No |  |  | PWR
104 | 64 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | Bolting | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 65 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Stainless steel | Treated borated water | AMP115 Bolting Integrity | No |  |  | PWR
104 | 66 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 67 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy (≤15% Zn and ≤8% Al) | Air with borated water leakage | None | No |  |  | PWR
104 | 68 | Auxiliary systems | Spent fuel storage | Reduction of neutron-absorbing capacity due to Boraflex degradation | Spent fuel storage rack: neutron-absorbing sheet (PWR) | Boraflex | Treated borated water | AMP126 Boraflex Monitoring | No |  |  | PWR, BWR, WWER
104 | 69 | Auxiliary systems | Spent fuel storage | Reduction of neutron-absorbing capacity due to effects of SFP environment | Spent fuel storage rack: neutron-absorbing sheet (PWR) | Boral®, boron steel, other materials (excluding Boraflex) | Treated borated water | AMP137 Monitoring of Neutron-Absorbing Materials Other than Boraflex | No |  |  | PWR, BWR, WWER
104 | 70 | Auxiliary systems | Spent fuel storage | Change in dimensions due to effects of SFP environment | Spent fuel storage rack: neutron-absorbing sheet (PWR) | Boral®, boron steel, other materials (excluding Boraflex) | Treated borated water | AMP137 Monitoring of Neutron-Absorbing Materials Other than Boraflex | No |  |  | PWR, BWR, WWER
104 | 71 | Auxiliary systems | Spent fuel storage | Loss of material due to effects of SFP environment | Spent fuel storage rack: neutron-absorbing sheet (PWR) | Boral®, boron steel, other materials (excluding Boraflex) | Treated borated water | AMP137 Monitoring of Neutron-Absorbing Materials Other than Boraflex | No |  |  | PWR, BWR, WWER
104 | 72 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Steel with stainless steel or nickel-alloy cladding | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry | No |  |  | PWR
104 | 73 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | PWR
104 | 74 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to boric acid corrosion | Piping, piping component, piping element | Aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 75 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Hardening and loss of strength due to elastomer degradation | Elastomer, lining | Elastomer | Treated borated water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 76 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to pitting, crevice corrosion (only for steel after lining, cladding degradation) | Piping, piping component, piping element | Steel with elastomer lining | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 77 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 78 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 79 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Steel with stainless steel cladding, stainless steel | Treated borated water | AMP103 Water Chemistry | No |  |  | PWR
104 | 80 | Auxiliary systems | Chemical and volume control system (PWR) | Cumulative fatigue damage due to fatigue | Heat exchanger components and tubes | Stainless steel | Treated borated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 81 | Auxiliary systems | Chemical and volume control system (PWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 82 | Auxiliary systems | Chemical and volume control system (PWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Stainless steel | Treated borated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 83 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to stress corrosion cracking, cyclic loading | Heat exchanger components, non-regenerative | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry | Yes, if plant- specific AMP |  | AMPs to be augmented by verifying the absence of cracking due to stress corrosion cracking and cyclic loading. An acceptable verification programme is to include temperature and radioactivity monitoring of the shell side water, and eddy current testing of | PWR
104 | 84 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | PWR
104 | 85 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to boric acid corrosion | Piping, piping component, piping element | Aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 86 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to stress corrosion cracking | High-pressure pump, casing | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 87 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to cyclic loading | High-pressure pump, casing | Stainless steel | Treated borated water | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 88 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 89 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to cyclic loading | Heat exchanger components and tubes | Stainless steel | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
104 | 90 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 91 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 92 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 93 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 94 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 95 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to selective leaching | Heat exchanger components | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 96 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Steel with stainless steel cladding, stainless steel | Treated borated water | AMP103 Water Chemistry | No |  |  | PWR
104 | 97 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry | No |  |  | PWR
104 | 98 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to corrosion following cladding breach | Pump casing | Steel with stainless steel or nickel-alloy cladding | Treated borated water | A plant-specific ageing management programme | Yes, verify that plant-specific program addresses clad cracking |  |  | PWR
104 | 99 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | Bolting | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 100 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | PWR
104 | 101 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Stainless steel | Treated borated water | AMP115 Bolting Integrity | No |  |  | PWR
104 | 102 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 103 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy (≤15% Zn and ≤8% Al) | Air with borated water leakage | None | No |  |  | PWR
104 | 104 | Steam and power conversion system | Main steam system (PWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Steam, treated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 105 | Steam and power conversion system | Main steam system (PWR) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Steam | AMP114 Flow-accelerated Corrosion | No |  |  | PWR
104 | 106 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Nickel alloy | Steam | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 107 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Air - outdoor (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 108 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Condensation (Internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 109 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Steam | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 110 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 111 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 112 | Steam and power conversion system | Main steam system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 113 | Steam and power conversion system | Main steam system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Steam | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 114 | Steam and power conversion system | Feedwater system (PWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Treated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 115 | Steam and power conversion system | Feedwater system (PWR) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Treated water | AMP114 Flow-accelerated Corrosion | No |  |  | PWR
104 | 116 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 117 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 118 | Steam and power conversion system | Feedwater system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 119 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 120 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 121 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 122 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 123 | Steam and power conversion system | Steam generator blow down system (PWR) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Treated water | AMP114 Flow-accelerated Corrosion | No |  |  | PWR
104 | 124 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 125 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | Heat exchanger components | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 126 | Steam and power conversion system | Steam generator blow down system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 127 | Steam and power conversion system | Steam generator blow down system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 128 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 129 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice, MIC, fouling that leads to corrosion | Heat exchanger components | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 130 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 131 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 132 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | PWR
104 | 133 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 134 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 135 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 136 | Steam and power conversion system | Steam generator blow down system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 137 | Steam and power conversion system | Steam generator blow down system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 138 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | PWR
104 | 139 | Steam and power conversion system | Steam generator blow down system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger components | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 140 | Steam and power conversion system | Steam generator blow down system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 141 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 142 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to general, pitting, crevice corrosion | PWR heat exchanger components | Steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 143 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 144 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | PWR heat exchanger components | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 145 | Steam and power conversion system | Steam generator blow down system (PWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel | Treated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 146 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 147 | Steam and power conversion system | Steam generator blow down system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 148 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 149 | Steam and power conversion system | Steam generator blow down system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 150 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Treated water | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
104 | 151 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Treated water | AMP114 Flow-accelerated Corrosion | No |  |  | PWR
104 | 152 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 153 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Heat exchanger components | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 154 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 155 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 156 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Tank（external surface) | Steel | Air - outdoor (External) | AMP132 Aboveground Metallic Tanks | No |  |  | PWR
104 | 157 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 158 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 159 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 160 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger components and tubes | Aluminum | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 161 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 162 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Tank（external surface) | Steel | Soil, concrete | AMP132 Aboveground Metallic Tanks | No |  |  | PWR
104 | 163 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 164 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice, galvanic, MIC, fouling that leads to corrosion | Steel piping, piping component, piping element exposed to raw water | Steel | Raw water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 165 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | PWR
104 | 166 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching, AMP 124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 167 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Raw water | AMP120 Selective Leaching, AMP 124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 168 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | PWR
104 | 169 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching, AMP 124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 170 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 171 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 172 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 173 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 174 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 175 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching, AMP 124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 176 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 177 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 178 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 179 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 180 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general (steel only) pitting and crevice corrosion | Tank（internal surface) | Steel, stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 181 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice, MIC | Heat exchanger components | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 182 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice, MIC | Heat exchanger components | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 183 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 184 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 185 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP 124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 186 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP 124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 187 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 188 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 189 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  |  | PWR
104 | 190 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 191 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | PWR
104 | 192 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | External surface | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | PWR
104 | 193 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to boric acid corrosion | Bolting | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | PWR
104 | 194 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy (≤15% Zn and ≤8% Al) | Air with borated water leakage | None | No |  |  | PWR
104 | 195 | Engineered safety features | ECCS (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 196 | Engineered safety features | ECCS (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | PWR
104 | 197 | Auxiliary systems | Spent fuel storage | Cracking due to stress corrosion cracking | Spent fuel storage rack (PWR) | Stainless steel | Treated borated water >60°C (>140°F) | AMP103 Water Chemistry | No |  |  | PWR
104 | 198 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 199 | Auxiliary systems | Spent fuel pool cooling and cleanup (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 200 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to stress corrosion cracking, cyclic loading | High-pressure pump, closure bolting | Steel, high-strength | Air with steam or water leakage | AMP115 Bolting Integrity | No |  |  | PWR
104 | 201 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 202 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 203 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | PWR
104 | 204 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 205 | Auxiliary systems | Chemical and volume control system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | PWR
104 | 206 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | PWR
104 | 207 | Steam and power conversion system | Main steam system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 208 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | PWR
104 | 209 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
104 | 210 | Steam and power conversion system | Feedwater system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 211 | Steam and power conversion system | Feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | PWR
104 | 212 | Steam and power conversion system | Steam generator blow down system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 213 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | PWR
104 | 214 | Steam and power conversion system | Steam generator blow down system (PWR) | Loss of material due to general, pitting, crevice, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
104 | 215 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 216 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | PWR
104 | 217 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice, MIC | Piping, piping component, piping element, tank | Steel with coating or wrapping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | PWR
104 | 218 | Steam and power conversion system | Auxiliary feedwater system (PWR) | Loss of material due to general, pitting, crevice, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | PWR
105 | 1 | Engineered safety features | Standby gas treatment system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, chloride is the main issue here, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 2 | Engineered safety features | Standby gas treatment system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 3 | Engineered safety features | Standby gas treatment system (BWR) | Loss of material due to general, pitting, crevice, MIC | Piping, piping component, piping element | Steel with coating or wrapping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  |  | BWR
105 | 4 | Engineered safety features | ECCS (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 5 | Engineered safety features | ECCS (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 6 | Auxiliary systems | Spent fuel pool cooling and cleanup (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 7 | Auxiliary systems | Spent fuel pool cooling and cleanup (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 8 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 9 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Stainless steel | Treated water | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 10 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 11 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Regenerative heat exchanger components | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 12 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 13 | Auxiliary systems | Reactor water cleanup system (BWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 14 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 15 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 16 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 17 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR
105 | 18 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | BWR
105 | 19 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR
105 | 20 | Auxiliary systems | Shutdown cooling system (older BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 21 | Auxiliary systems | Shutdown cooling system (older BWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 22 | Auxiliary systems | Shutdown cooling system (older BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 23 | Auxiliary systems | Shutdown cooling system (older BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 24 | Auxiliary systems | Shutdown cooling system (older BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 25 | Auxiliary systems | Shutdown cooling system (older BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 26 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR
105 | 27 | Steam and power conversion system | Main steam system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 28 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 29 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 30 | Steam and power conversion system | Feedwater system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 31 | Steam and power conversion system | Feedwater system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 32 | Engineered safety features | Standby gas treatment system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, chloride is the main issue here, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 33 | Engineered safety features | Standby gas treatment system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 34 | Engineered safety features | Standby gas treatment system (BWR) | Loss of material due to general, pitting, crevice, MIC | Piping, piping component, piping element | Steel with coating or wrapping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR
105 | 35 | Engineered safety features | ECCS (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 36 | Engineered safety features | ECCS (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 37 | Auxiliary systems | Spent fuel storage | Cracking due to stress corrosion cracking | Spent fuel storage rack (BWR) | Stainless steel | Treated water >60°C (>140°F) | AMP103 Water Chemistry | No |  |  | BWR
105 | 38 | Auxiliary systems | Spent fuel pool cooling and cleanup (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 39 | Auxiliary systems | Spent fuel pool cooling and cleanup (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 40 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 41 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Stainless steel | Treated water | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 42 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 43 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Regenerative heat exchanger components | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 44 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 45 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP103 Water Chemistry, AMP129 BWR Reactor Water Cleanup System | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 46 | Auxiliary systems | Reactor water cleanup system (BWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 47 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 48 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 49 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 50 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR
105 | 51 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | BWR
105 | 52 | Auxiliary systems | Reactor water cleanup system (BWR) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR
105 | 53 | Auxiliary systems | Shutdown cooling system (older BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 54 | Auxiliary systems | Shutdown cooling system (older BWR) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 55 | Auxiliary systems | Shutdown cooling system (older BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 56 | Auxiliary systems | Shutdown cooling system (older BWR) | Loss of material due to general, pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR
105 | 57 | Auxiliary systems | Shutdown cooling system (older BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 58 | Auxiliary systems | Shutdown cooling system (older BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 59 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR
105 | 60 | Steam and power conversion system | Main steam system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 61 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
105 | 62 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 63 | Steam and power conversion system | Feedwater system (BWR) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
105 | 64 | Steam and power conversion system | Feedwater system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR
106 | 1 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vessel | Loss of fracture toughness due to neutron irradiation embrittlement | Vessel | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 2 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vessel | Cracking due to stress corrosion cracking | Weld | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP103 Water Chemistry | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
106 | 3 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vessel | Cracking due to fatigue | Nozzle and weld region | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Evironmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 4 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator diffuser | Loss of fracture toughness due to neutron irradiation embrittlement | Diffuser | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 5 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator diffuser | Cracking due to fatigue, flow-induced vibration | Location with highest velocity | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA123 CANDU/PHWR Calandria Internals Vibrations) |  |  | CANDU/ PHWR
106 | 6 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator diffuser | Cracking due to fatigue | Region having sudden change in cross section | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue, TLAA123 CANDU/PHWR Calandria Internals Vibrations) |  |  | CANDU/ PHWR
106 | 7 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator diffuser | Loss of material due to corrosion, erosion | Diffuser | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 8 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube | Loss of fracture toughness due to neutron irradiation embrittlement | Highest fluence location | Zirconium alloy | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 9 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube | Cracking due to fatigue | Tube | Zirconium alloy | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage,TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
106 | 10 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube | Change of dimension due to irradiation induced creep | Garter spring | Zirconium alloy | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA105 CANDU/PHWR Fuel Channel Creep) |  |  | CANDU/ PHWR
106 | 11 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube | Loss of leak tightness due to stress relaxation | Near rolled joint | Zirconium alloy | Neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 12 | Reactor assemblies, moderator and moderator auxiliary systems | Annulus gas system | Loss of material due to wear | Filter, valve | Stainless steel | CO2, high neutron fluence | AMP146 CANDU/ PHWR Inspection Programmes, AMP150 CANDU/ PHWR Annulus Gas System | No |  |  | CANDU/ PHWR
106 | 13 | Reactor assemblies, moderator and moderator auxiliary systems | Annulus gas system | Cracking due to fatigue | Compressor, valve | Stainless steel | CO2, high neutron fluence | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes, AMP150 CANDU/ PHWR Annulus Gas System | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | CANDU/ PHWR
106 | 14 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube sheet | Loss of fracture toughness due to neutron irradiation embrittlement | Tube sheet | Stainless steel | Neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 15 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube sheet | Loss of material due to corrosion | Tube sheet | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 16 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria tube sheet | Cracking due to fatigue | Near rolled joint | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 17 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator manifold | Cracking due to vibrational fatigue | Weld at Nelson stud | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA123 CANDU/PHWR Calandria Internals Vibrations, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 18 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria relief duct | Cracking due to stress corrosion cracking | Weld, piping | Stainless steel | Air, helium | AMP141 CANDU/ PHWR Reactor Assembly | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 19 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria relief duct | Loss of material due to corrosion | Weld, piping | Stainless steel | Air, helium | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 20 | Reactor assemblies, moderator and moderator auxiliary systems | Dump ports, dump belows, dump tank | Cracking due to fatigue | Outlet and inlet | Stainless steel | D2O, 44-63°C (111°F - 145°F), neutron fluence | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 21 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator system piping | Cracking due to fatigue | Moderator inlet nozzle and piping, piping bend | Stainless steel | D2O, neutron fluence | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 22 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator system piping | Loss of material due to corrosion, erosion | Moderator inlet nozzle and piping, piping bend | Stainless steel | D2O, neutron fluence | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 23 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator heat exchangers (shell and tube type) | Loss of material due to general corrosion, MIC, pitting corrosion, crevice corrosion and fouling | Shell, tube | Steel, stainless steel | D2O, raw water, neutron fluence | AMP103 Water Chemistry, AMP145 CANDU/ PHWR Moderator and Moderator Purification Heat Exchangers | No |  |  | CANDU/ PHWR
106 | 24 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator heat exchangers (shell and tube type) | Reduction of heat transfer due to fouling | Shell, tube | Steel, stainless steel | D2O, raw water, neutron fluence | AMP103 Water Chemistry, AMP145 CANDU/ PHWR Moderator and Moderator Purification Heat Exchangers | No |  |  | CANDU/ PHWR
106 | 25 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator pump | Loss of material due to wear | Casing, rotating components | Stainless steel | D2O, raw water, neutron fluence | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 26 | Regulating systems and safety systems, reactivity control unit | Vertical and horizontal flux units | Cracking due to flow-induced vibration | Joint location to the locating assembly attached to calandria | Zirconium alloy | D2O, neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA123 CANDU/PHWR Calandria Internals Vibrations) |  |  | CANDU/ PHWR
106 | 27 | Regulating systems and safety systems, reactivity control unit | Vertical and horizontal flux units | Change in dimensions due to irradiation induced creep | Joint location to the locating assembly attached to calandria | Zirconium alloy | D2O, neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA123 CANDU/PHWR Calandria Internals Vibrations) |  |  | CANDU/ PHWR
106 | 28 | Regulating systems and safety systems, reactivity control unit | Vertical and horizontal flux units | Change in dimensions due to irradiation induced creep | Joint location to the locating assembly attached to calandria | Zirconium alloy | D2O, neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 29 | Regulating systems and safety systems, reactivity control unit | Ionization chamber housing assembly-pipe and pipe sub assembly | Loss of material due to corrosion | Piping, piping component, piping element | Stainless steel | Air, moist | AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 30 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator system valve | Loss of material due to erosion | Bellow seal valve, seat | Steel | D2O, neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP143 CANDU/ PHWR Auxiliary System Valves | No |  |  | CANDU/ PHWR
106 | 31 | Reactor assemblies, moderator and moderator auxiliary systems | Motorized valve | Loss of material due to erosion | Disc and body internals | Steel | D2O, neutron fluence | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 32 | Reactor assemblies, moderator and moderator auxiliary systems | Control valves | Loss of material due to erosion | Disc and body internals | Steel | D2O, neutron fluence | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 33 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator system butterfly valve | Loss of material due to flow accelerated corrosion | Disc and body internals | Steel | D2O, neutron fluence | AMP114 Flow-accelerated Corrosion, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 34 | Reactor assemblies, moderator and moderator auxiliary systems | Moderator cover gas blower | Loss of material due to wear | Blower | Steel | Helium, neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 35 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system end shield | Loss of fracture toughness due to neutron irradiation embrittlement | End shield | Stainless steel | Treated water, neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 36 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system end shield | Cracking due to stress corrosion cracking | End shield | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
106 | 37 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system end shield | Loss of material due to general corrosion | End shield | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 38 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system end shield | Cracking due to fatigue | End shield | Stainless steel | Treated water, neutron fluence | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
106 | 39 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system end shield | Loss of material due to crevice corrosion | End shield | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP141 CANDU/ PHWR Reactor Assembly | No |  |  | CANDU/ PHWR
106 | 40 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system piping | Loss of material due to corrosion, erosion, wear | Piping, piping component, piping element | Steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 41 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system pump | Loss of material due to corrosion, erosion, wear | Impeller, casing, plate gasket | Steel, stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 42 | Reactor assemblies, moderator and moderator auxiliary systems | End shield heat exchangers (plate type) | Loss of material due to corrosion, erosion | Plate, gasket | Steel, stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 43 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system motorized valve | Loss of material due to erosion | Seat, disc, body internals | Steel | Treated water, neutron fluence | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 44 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system control valve | Loss of material due to erosion | Seat, disc, body internals | Steel | Treated water, neutron fluence | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 45 | Reactor assemblies, moderator and moderator auxiliary systems | End shield cooling system expansion tank | Loss of material due to corrosion | Weld | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 46 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vault liner | Loss of material due to corrosion | Liner | Steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP141 CANDU/ PHWR Reactor Assembly | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 47 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vault cooling system expansion tank | Loss of material due to corrosion | Weld | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 48 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vault cooling system piping | Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 49 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vault cooling system plate type heat exchanger | Loss of material due to corrosion, erosion | Plate, gasket | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 50 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vault cooling system motorized valve | Loss of material due to erosion | Seat, disc | Steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 51 | Reactor assemblies, moderator and moderator auxiliary systems | Calandria vault cooling system control valve | Loss of material due to erosion | Seat, disc, body internals | Stainless steel | Treated water, neutron fluence | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 52 | Steam and Power Conversion System | Main steam lines | Cracking due to fatigue | Piping and piping component | Steel | Steam | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 53 | Steam and Power Conversion System | Main steam lines | Loss of material due to corrosion, erosion | Piping, piping component, piping element | Steel | Steam | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 54 | Steam and Power Conversion System | Support for piping and components | Cracking due to vibrational fatigue | Support component and bellow | Steel | Air | AMP146 CANDU/ PHWR Inspection Programmes, AMP147 Containment Bellows | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses) |  |  | CANDU/ PHWR
106 | 55 | Steam and Power Conversion System | Boiler feed pumps | Loss of material due to wear | Rotating parts | Steel | Treated water | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 56 | Steam and Power Conversion System | Boiler feed pumps | Loss of material due to flow accelerated corrosion | Casing | Steel | Treated water | AMP114 Flow-accelerated Corrosion, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 57 | Steam and Power Conversion System | Feed water piping | Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Treated water | AMP114 Flow-accelerated Corrosion, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 58 | Steam and Power Conversion System | Steam generator blow down line | Cracking due to fatigue | Piping, piping component, piping element | Steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 59 | Steam and Power Conversion System | Steam generator blow down line | Loss of material due to general corrosion, flow accelerated corrosion and wear | Piping, piping component, piping element | Steel | Treated water | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 60 | Steam and Power Conversion System | Air compressor | Loss of material due to wear | Moving parts | Steel | Air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 61 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Wall thinning due to cavitation, corrosion, flow accelerated corrosion | Casing, nozzle | Cast stainless steel | Treated water | AMP103 Water Chemistry, AMP114 Flow-accelerated Corrosion, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 62 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Cracking due to fatigue | Impeller | Stainless steel | Treated water | AMP101 Fatigue Monitoring, AMP144 CANDU/ PHWR Auxiliary System Pumps | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 63 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Loss of material due to corrosion, erosion | Impeller | Stainless steel | Treated water | AMP103 Water Chemistry, AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 64 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Cracking due to fatigue | Shaft | Stainless steel | Treated water | AMP101 Fatigue Monitoring, AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 65 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Cracking due to vibrational fatigue | Bearings | Steel | Treated water | AMP101 Fatigue Monitoring, AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 66 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Cracking due to vibrational fatigue | Coupling | Steel | Treated water | AMP101 Fatigue Monitoring, AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 67 | Steam and Power Conversion System | Condenser vacuum, extraction pump | Loss of material due to corrosion | Condesate storage tank | Steel | Treated water | AMP103 Water Chemistry, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 68 | Steam and Power Conversion System | Condenser | Loss of material due to erosion, corrosion, pitting and crevice corrosion | Condenser shell, condenser dump device, diffuser assembly, hot well support, impingement plate, stiffener, water box | Steel | Treated water | AMP117 Closed Treated Water Systems, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 69 | Steam and Power Conversion System | Condenser | Cracking due to fatigue | Condenser dump device | Steel | Treated water | AMP117 Closed Treated Water Systems, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 70 | Steam and Power Conversion System | Condenser | Loss of material due to corrosion | Tube | Stainless steel | Treated water | AMP117 Closed Treated Water Systems, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 71 | Steam and Power Conversion System | Condenser | Hardening and loss of strength due to elastomer degradation | Expansion joint | Elastomer | Treated water | AMP117 Closed Treated Water Systems, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 72 | Steam and Power Conversion System | De-aerator | Loss of material due to corrosion | Shell | Steel | Treated water | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 73 | Steam and Power Conversion System | De-aerator | Cracking due to fatigue, stress corrosion cracking | Shell | Steel | Treated water | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 74 | Steam and Power Conversion System | De-aerator | Loss of material due to corrosion | Tube | Stainless steel | Steam, treated water | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 75 | Steam and Power Conversion System | De-aerator | Cracking due to fatigue, flow-induced vibration | Tray | Steel | Steam, treated water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 76 | Steam and Power Conversion System | Feedwater system | Cracking due to fatigue | Piping, piping component, piping element | Steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 77 | Steam and Power Conversion System | Feedwater system | Loss of material due to general corrosion, flow accelerated corrosion, wear | Piping, piping component, piping element | Steel | Treated water | AMP114 Flow-accelerated Corrosion, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 78 | Steam and Power Conversion System | Feed water heater | Cracking due to fatigue | Tube, shell | Steel, stainless steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 79 | Steam and Power Conversion System | Feed water heater | Loss of material due to erosion, fretting and flow accelerated corrosion | Tube, shell | Steel, stainless steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes, AMP114 Flow-accelerated Corrosion | No |  |  | CANDU/ PHWR
106 | 80 | Steam and Power Conversion System | Feed water heater | Loss of material due to corrosion | Bolting | Low alloy steel | Air | AMP115 Bolting Integrity, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 81 | Regulating systems and safety systems, liquid zone control system | Liquid zone control compartment assemblies | Loss of material due to fretting | Liquid zone control compartment assembly components | Stainless steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 82 | Regulating systems and safety systems, liquid zone control system | Process equipment | Loss of material due to corrosion | Process equipment components | Steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 83 | Regulating systems and safety systems, liquid zone control system | Piping, piping components and piping elements | Loss of material due to corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 84 | Regulating systems and safety systems, liquid zone control system | Valve, flange | Loss of material due to corrosion | Valve, flange | Stainless steel, low alloy steel | Treated water | AMP115 Bolting Integrity, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 85 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Guide tube assembly (incore part) | Change in dimensions due to irradiation induced creep | Incore part | Zirconium alloy | D2O, high neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown Systems | No |  |  | CANDU/ PHWR
106 | 86 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Guide tube assembly (incore part) | Cracking due to flow-induced vibration | Incore part | Zirconium alloy | D2O, high neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown Systems | No |  |  | CANDU/ PHWR
106 | 87 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Guide tube assembly (incore part) | Loss of material due to wear | Incore part | Zirconium alloy | D2O, high neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown Systems | No |  |  | CANDU/ PHWR
106 | 88 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Locator assembly, guide tube, adjustor rod drive mechanism housing | Change in dimensions due to irradiation induced creep | Guide tube, weld | Stainless steel | D2O, high neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 89 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Locator assembly, guide tube, adjustor rod drive mechanism housing | Cracking due to flow-induced vibration | Guide tube, weld | Stainless steel | D2O, high neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown System | Yes if TLAA (TLAA123 CANDU/PHWR Calandria Internals Vibrations, TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 90 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Locator assembly, guide tube, adjustor rod drive mechanism housing | Reduction of neutron-absorbing capacity due to effects of environment | Guide tube, weld | Stainless steel | D2O, high neutron fluence | AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 91 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Drive mechanism of shut off rod | Loss of material due to corrosion, wear | Gear, shaft | Stainless steel | Air | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 92 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Drive mechanism of shut off rod | Change in dimensions due to irradiation induced creep | Drive mechanism of shut off rod | Stainless steel | Air | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 93 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Drive mechanism of shut off rod | Loss of material due to wear | Drive mechanism of shut off rod | Stainless steel | Air | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 94 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Clutch mechanism | Loss of material due to wear | Clutch mechanism | Stainless steel | Air | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 95 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Rope | Change in dimensions due to creep | Rope snap | Stainless steel | Neutron fluence | AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 96 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Rope | Loss of fracture toughness due to neutron irradiation embrittlement and thermal embrittlement | Rope snap | Stainless steel | Neutron fluence | AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 97 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Rope | Loss of material due to general corrosion | Rope snap | Stainless steel | Neutron fluence | AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 98 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Shut off rod | Cracking due to fatigue | Shut off rod | Cadmium, cadmium sandwiched in stainless steel | Neutron fluence | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 99 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Shut off rod | Reduction of neutron-absorbing capacity due to effects of environment | Shut off rod | Cadmium, cadmium sandwiched in stainless steel | Neutron fluence | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 100 | Regulating systems and safety systems, shut down system - 1 (Shut off rod) | Dash pot mechanism | Loss of material due to wear | Dash pot mechanism | Stainless steel | Lubricating oil | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 101 | Regulating systems and safety systems, shut down system - 2 | Helium tank | Loss of material due to corrosion | Weld | Stainless steel | Air, helium | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 102 | Regulating systems and safety systems, shut down system - 2 | Quick acting MOVs | Loss of material due to wear | Valve components | Stainless steel | Air, helium | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 103 | Regulating systems and safety systems, shut down system - 2 | Ball valve | Loss of material due to wear | Valve components | Stainless steel | Air, helium | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 104 | Regulating systems and safety systems, shut down system - 2 | SDS-2 tank | Loss of material due to corrosion | Weld | Stainless steel | Solution of D2O and Gadolinium | AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 105 | Regulating systems and safety systems, shut down system - 2 | SDS-2 ball | Loss of material due to wear | Ball | Polymer | Gadolinium | AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 106 | Regulating systems and safety systems, shut down system - 2 | Piping outside calandria (SS) | Cracking due to flow-induced vibration | Piping, piping component, piping element | Stainless steel | Solution of D2O and Gadolinium | AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | Yes, if TLAA (TLAA103 Crack Growth Analyses, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 107 | Regulating systems and safety systems, shut down system - 2 | Piping outside calandria (SS) | Loss of material due to corrosion | Piping, piping component, piping element | Stainless steel | Solution of D2O and Gadolinium | AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP146 CANDU/ PHWR Inspection Programmes, AMP148 CANDU/PHWR Shutdown System | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 108 | Regulating systems and safety systems, shut down system - 2 | Piping inside calandria | Cracking due to flow-induced vibration | Piping, piping component, piping element | Stainless steel, zirconium alloy | D2O, Gadolinium, neutron fluence | AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown System | Yes if TLAA (TLAA123 CANDU/PHWR Calandria Internals Vibrations) |  |  | CANDU/ PHWR
106 | 109 | Regulating systems and safety systems, shut down system - 2 | Piping inside calandria | Change in dimensions due to irradiation induced creep | Piping, piping component, piping element | Stainless steel, zirconium alloy | D2O, Gadolinium, neutron fluence | AMP121 One-Time Inspection of Class 1 Small-bore piping, AMP141 CANDU/ PHWR Reactor Assembly, AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 110 | Regulating systems and safety systems, shut down system - 2 | Poison transfer pump (canned rotor) | Loss of material due to corrosion, erosion | Pump components | Cast stainless steel | Solution of D2O and Gadolinium | AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 111 | Regulating systems and safety systems, shut down system - 2 | SDS-2 diaphragm valve | Loss of material due to wear | Body, stem | Steel | Solution of D2O and Gadolinium | AMP148 CANDU/PHWR Shutdown System | No |  |  | CANDU/ PHWR
106 | 112 | Regulating systems and safety systems, emergency core cooling system | ECCS strainer | Loss of material due to corrosion | Strainer | Stainless steel | treated water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 113 | Regulating systems and safety systems, emergency core cooling system | ECCS (H2O), (D2O) accumulator | Loss of material due to corrosion | Weld | Steel | Treated water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 114 | Regulating systems and safety systems, emergency core cooling system | ECCS air accumulator | Loss of material due to corrosion | Weld | Steel | Air | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 115 | Regulating systems and safety systems, emergency core cooling system | ECCS air compressor | Loss of material due to corrosion, erosion, wear | Moving parts | Steel | air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 116 | Regulating systems and safety systems, emergency core cooling system | ECCS pump | Loss of material due to corrosion, erosion, wear | Casing, impeller | Cast stainless steel | Treated water | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 117 | Regulating systems and safety systems, emergency core cooling system | ECCS piping | Loss of material due to corrosion, erosion, wear, MIC, pitting | Piping, piping component, piping element | Steel | Treated water | AMP125 Buried and Underground Piping and Tanks, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 118 | Regulating systems and safety systems, emergency core cooling system | ECCS MOVs, valves | Loss of material due to corrosion, erosion, wear | Body, stem | Stainless steel | Treated water | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 119 | Regulating systems and safety systems, emergency core cooling system | ECCS rupture disk | Loss of material due to wear | Disk | Nickel alloy | Treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 120 | Regulating systems and safety systems, emergency core cooling system | ECCS plate type heat exchanger | Loss of material due to corrosion, erosion, crevice corrosion, fouling, MIC, pitting | Plate | Stainless steel | Treated water | AMP103 Water Chemistry, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 121 | Regulating systems and safety systems, emergency core cooling system | ECCS tanks RVs | Loss of material due to corrosion, erosion | Weld | Steel | Treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 122 | Steam and power conversion system, high pressure low pressure turbine system | HP/ LP stop/ governor valve, steam chest | Denting, erosion, wear | Sliding surfaces | Steel | Steam | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 123 | Steam and power conversion system, high pressure low pressure turbine system | HP/ LP stop/ governor valve actuator (i.e. receiver amplifier unit) | Loss of material due to wear | Sliding surfaces | Steel | Steam | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 124 | Steam and power conversion system, high pressure low pressure turbine system | HP outer casing to bearing pedestal keys and push-pull arrangements | Loss of material due to wear | Sliding surfaces | Steel | Steam | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 125 | Steam and power conversion system, high pressure low pressure turbine system | LP turbine | Loss of material due to erosion | Blades (last rows) | Steel | Steam, treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No | AERB/ NPP/ SG/ O-14: Life management of Nuclear Power plants |  | CANDU/ PHWR
106 | 126 | Steam and power conversion system, high pressure low pressure turbine system | LP turbine | Cracking due to vibrational fatigue | Blades (last rows) | Steel | Steam, treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No | AERB/ NPP/ SG/ O-14: Life management of Nuclear Power plants |  | CANDU/ PHWR
106 | 127 | Steam and power conversion system, high pressure low pressure turbine system | Turbine governor, governing system | Loss of material due to wear | Sliding surfaces | Steel | air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 128 | Steam and power conversion system, high pressure low pressure turbine system | Bearing pedestal, bearing | Cracking due to fatigue and vibration | Bearings | Steel | Lubricating oil | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 129 | Steam and power conversion system, high pressure low pressure turbine system | HP & LP turbines | Loss of material due to erosion | Blades (last rows) | Steel | Steam, treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 130 | Steam and power conversion system, high pressure low pressure turbine system | HP & LP turbines | Vibration due to loosening | Blades (last rows) | Steel | Steam, treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 131 | Steam and power conversion system, high pressure low pressure turbine system | Rotor | Cracking due to fatigue | Rotating parts | Steel | Steam, treated water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 132 | Steam and power conversion system, high pressure low pressure turbine system | Casing | Loss of material due to corrosion, erosion | Casing | Steel | Steam, treated water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 133 | Steam and power conversion system, high pressure low pressure turbine system | Internal steam pipe, G48 | Loss of material due to erosion | Piping, piping component, piping element | Steel | Steam | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 134 | Steam and power conversion system, high pressure low pressure turbine system | Internal steam pipe, G48 | Cracking due to vibrational fatigue | Piping, piping component, piping element | Steel | Steam | AMP146 CANDU/ PHWR Inspection Programmes | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 135 | Steam and power conversion system, high pressure low pressure turbine system | LP gland bellows and bellows connected reheat pipes | Cracking due to fatigue | Piping, piping component, piping element | Steel | Steam, treated water | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 136 | Steam and power conversion system, high pressure low pressure turbine system | Support for piping and components | Cracking due to fatigue | Spring | Steel | Air | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 137 | Steam and power conversion system, high pressure low pressure turbine system | Bolts and studs | Cracking due to fatigue | Bolting | Low alloy steel | Air | AMP115 Bolting Integrity | No |  |  | CANDU/ PHWR
106 | 138 | Auxiliary system, lubrication oil storage and purification system | Oil pump | Loss of material due to wear | Pump components | Steel | Air, lubricating oil | AMP136 Lubricating Oil Analysis | No |  |  | CANDU/ PHWR
106 | 139 | Auxiliary system, lubrication oil storage and purification system | Lubricating oil cooler | Loss of material due to corrosion | Cooler components | Steel | Oil, water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 140 | Auxiliary system, lubrication oil storage and purification system | Purification system | Loss of material due to wear | Valve | Steel | Air, lubricating oil | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 141 | Auxiliary system, fire water system | Fire water pump, valve casing and bowl | Loss of material due to general corrosion, MIC, pitting corrosion, crevice corrosion and wear | Piping, piping component, piping element | Steel | Raw water | AMP131 Fire Water System, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 142 | Auxiliary system, fire water system | Fire water pump, valve casing and bowl | Increased flow resistance due to fouling | Piping, piping component, piping element | Steel | Raw water | AMP131 Fire Water System, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 143 | Auxiliary system, fire water system | Fire water pump-impeller | Cracking due to fatigue | Impeller | Copper alloy, stainless steel | Raw water | AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 144 | Auxiliary system, fire water system | Fire water pump-impeller | Loss of material due to wear | Impeller | Copper alloy, stainless steel | Raw water | AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 145 | Auxiliary system, fire water system | Fire water pump-shaft | Cracking due to fatigue | Shaft | Stainless steel | Raw water | AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 146 | Auxiliary system, fire water system | Fire water pump-shaft | Loss of material due to wear | Shaft | Stainless steel | Raw water | AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 147 | Auxiliary system, fire water system | Fire water piping | Loss of material due to general corrosion, MIC, pitting corrosion, crevice corrosion | Piping, piping component, piping element | Steel | Raw water | AMP131 Fire Water System, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 148 | Auxiliary system, fire water system | Fire water piping | Increased flow resistance due to fouling | Piping, piping component, piping element | Steel | Raw water | AMP131 Fire Water System, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 149 | Auxiliary system, non active water process system | Pump | Loss of material due to corrosion, wear | Casing, impeller | Cast carbon steel, stainless steel | Raw water | AMP144 CANDU/ PHWR Auxiliary System Pumps | No |  |  | CANDU/ PHWR
106 | 150 | Auxiliary system, non active water process system | Valve | Loss of material due to erosion | Body, stem | Cast carbon steel, stainless steel | Raw water | AMP143 CANDU/ PHWR Auxiliary System Valves | No |  |  | CANDU/ PHWR
106 | 151 | Auxiliary system, non active water process system | Heat exchanger | Loss of material due to corrosion | Plate, gasket, frame | Elastomers, steel, titanium | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 152 | Auxiliary system, non active water process system | Heat exchanger | Cracking due to fatigue | Plate, gasket, frame | Elastomers, steel, titanium | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 153 | Auxiliary system, non active water process system | Feeding tank | Loss of material due to corrosion | Tank body, nozzle | Steel | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 154 | Auxiliary system, non active water process system | Piping, piping components and piping elements | Loss of material due to corrosion | Piping, piping component, piping element | Steel | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 155 | Auxiliary system, service water system | Pump | Loss of material due to cavitation, corrosion, erosion, wear | Casing, impeller, shaft | Steel | Raw water | AMP143 CANDU/ PHWR Auxiliary System Valves, AMP144 CANDU/ PHWR Auxiliary System Pumps, AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 156 | Auxiliary system, service water system | Header, piping | Loss of material due to general corrosion, MIC, pitting corrosion, crevice corrosion, wear and erosion | Piping, piping component, piping element | Steel | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 157 | Auxiliary system, service water system | Header, piping | Increased flow resistance due to fouling | Piping, piping component, piping element | Steel | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 158 | Auxiliary system, service water system | Heat exchanger | Loss of material due to corrosion, erosion, crevice corrosion, fouling, MIC, pitting | Plate, gasket, frame | Steel | Raw water | AMP146 CANDU/ PHWR Inspection Programmes | No |  |  | CANDU/ PHWR
106 | 159 | Auxiliary system, fuel handling system | Fueling machine head sub assemblies (ram assembly, separator, magazine) | Cracking due to fatigue | Ram assembly, separator, magazine | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA103 Crack Growth Analyses for Flaws Detected Inservice, TLAA106 Environmentally Assisted Fatigue) |  |  | CANDU/ PHWR
106 | 160 | Auxiliary system, fuel handling system | Fueling machine head sub assemblies (ram assembly, separator, magazine) | Loss of material due to wear, erosion | Ram assembly, separator, magazine | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | Yes, functional and preventive maintenance (PM) checks. Assemblies/ components are replaced depending on the requirement |  |  | CANDU/ PHWR
106 | 161 | Auxiliary system, fuel handling system | Fueling machine head sub assemblies (ram assembly, separator, magazine) | Change in dimensions due to creep | Ram assembly, separator, magazine | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | Yes, functional and preventive maintenance (PM) checks. Assemblies/ components are replaced depending on the requirement |  |  | CANDU/ PHWR
106 | 162 | Auxiliary system, fuel handling system | Fueling machine head sub assemblies (ram assembly, separator, magazine) | Loss of preload due to stress relaxation | Ram assembly, separator, magazine | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | Yes, functional and preventive maintenance (PM) checks. Assemblies/ components are replaced depending on the requirement |  |  | CANDU/ PHWR
106 | 163 | Auxiliary system, fuel handling system | Fueling machine head sub assemblies (ram assembly, separator, magazine) | Loss of material due to erosion, wear | Housing | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | Yes, functional and preventive maintenance (PM) checks to replace degraded components if required |  |  | CANDU/ PHWR
106 | 164 | Auxiliary system, fuel handling system | Reactor channel seal plug | Loss of material due to erosion, wear | Seal plug | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | Yes, once in five years, 5 seal plugs are to be removed and subjected to ISI |  |  | CANDU/ PHWR
106 | 165 | Auxiliary system, fuel handling system | Shielding cum sealing door | Cracking due to thermal fatigue | Seal | Glass | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 166 | Auxiliary system, fuel handling system | Shielding cum sealing door | Loss of toughness due to radiation damage | Seal | Glass | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 167 | Auxiliary system, fuel handling system | Shielding cum sealing door | Loss of material due to wear and tear | Seal | Glass | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 168 | Auxiliary system, fuel handling system | Fueling machine D2O system pump | Loss of material due to wear | Casing, impeller | Steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 169 | Auxiliary system, fuel handling system | Fueling machine D2O system pipe and tubing | Loss of material due to corrosion, erosion, wear | Piping, piping component, piping element | Stainless steel | Primary heat transport coolant (D2O) | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 170 | Auxiliary system, fuel handling system | Fueling machine D2O system pipe and tubing | Cracking due to vibrational fatigue | Piping, piping component, piping element | Stainless steel | Primary heat transport coolant (D2O) | AMP142 CANDU/ PHWR Fuel Handling | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 171 | Auxiliary system, fuel handling system | Fueling machine D2O system support structure | Loss of material due to corrosion | Support | Steel | Primary heat transport coolant (D2O) | AMP142 CANDU/ PHWR Fuel Handling | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 172 | Auxiliary system, fuel handling system | Fueling machine D2O system heat exchanger | Loss of material due to flow accelerated corrosion | Plate, gasket, frame | Steel | Primary heat transport coolant (D2O) | AMP114 Flow-accelerated Corrosion, AMP143 CANDU/ PHWR Auxiliary System Valves, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 173 | Auxiliary system, fuel handling system | Fueling machine oil-hydraulic system | Loss of fracture toughness due to neutron irradiation embrittlement | Moving parts | Steel | Hydraulic oil | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 174 | Auxiliary system, fuel handling system | Fueling machine oil-hydraulic system | Loss of material due to wear | Moving parts | Steel | Hydraulic oil | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 175 | Auxiliary system, fuel handling system | Fueling machine oil-hydraulic system - piping and tubing | Cracking due to vibrational fatigue | Piping, piping component, piping element | Stainless steel | Hydraulic oil | AMP142 CANDU/ PHWR Fuel Handling | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 176 | Auxiliary system, fuel handling system | Fueling machine carriage | Loss of material due to wear | Moving parts | Steel | Air | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 177 | Auxiliary system, fuel handling system | Fueling machine guide column | Loss of material due to wear | Moving parts | Steel | Air | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 178 | Auxiliary system, fuel handling system | Fueling machine bridge | Loss of material due to wear | Moving parts | Steel | Air | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 179 | Auxiliary system, fuel handling system | Ball screw assembly | Loss of material due to wear | Moving parts | Steel | Air | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 180 | Auxiliary system, fuel handling system | Fuel transfer port, transfer magazine, shuttle tranfer station, new fuel magazine | Loss of material due to wear | Port, transfer magazine | Stainless steel | D2O, 65°C, neutron fluence | AMP142 CANDU/ PHWR Fuel Handling | No |  |  | CANDU/ PHWR
106 | 181 | Auxiliary system, air conditioning and ventilation system | Centrifugal fans | Loss of material due to wear | Rotating parts | Steel | Air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 182 | Auxiliary system, air conditioning and ventilation system | Air ducting, grills and diffuser | Loss of material due to corrosion | Air ducting, grills, diffuser | Steel | Air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 183 | Auxiliary system, air conditioning and ventilation system | Filter | Increased flow resistance due to fouling | Filter | Steel | Air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 184 | Auxiliary system, air conditioning and ventilation system | Chiller | Loss of material due to corrosion | Chiller | Steel | Raw water | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 185 | Auxiliary systems | Crane | Loss of material due to wear | Moving parts | Steel | Air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 186 | Auxiliary systems | Crane | Loss of material due to corrosion | Carbon steel components | Steel | Air | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 187 | Auxiliary system, air conditioning and ventilation system | D2O dryer damper | Loss of material due to wear | Damper | Steel | Air, moist | Ageing management is accomplished through routine plant maintenance or preventive maintenance activities | No |  |  | CANDU/ PHWR
106 | 188 | Auxiliary system, service water system | Buried pipings | Loss of material due to corrosion | Piping, piping component, piping element | Steel | Raw water | AMP125 Buried and Underground Piping and Tanks | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 189 | Auxiliary system, service water system | Piping in trenches | Loss of material due to corrosion | Piping support | Steel | Air, water | AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 190 | Steam and power conversion system | Emergency water pipe line | Loss of material due to corrosion | Piping, piping component, piping element | Stainless steel | Raw water | AMP103 Water Chemistry, AMP146 CANDU/ PHWR Inspection Programmes | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | CANDU/ PHWR
106 | 191 | Steam and power conversion system | Emergency water pipe line | Cracking due to fatigue | Piping, piping component, piping element | Stainless steel | Raw water | AMP101 Fatigue Monitoring, AMP146 CANDU/ PHWR Inspection Programmes | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | CANDU/ PHWR
106 | 192 | Steam and power conversion system | Emergency water pipe line | Loss of material due to wear | Lube oil pump | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | CANDU/ PHWR
106 | 193 | Auxiliary system, instrument air system | Piping, piping components and piping elements | Loss of material due to corrosion, pitting corrosion | Piping, piping component, piping element | Steel | Air | AMP128 Compressed Air Monitoring | No |  |  | CANDU/ PHWR
106 | 194 | Auxiliary system, instrument air system | Vessel, tank | Loss of material due to general corrosion, pitting corrosion, crevice corrosion | Vessel, tank | Steel | Air | AMP128 Compressed Air Monitoring | No |  |  | CANDU/ PHWR
106 | 195 | Auxiliary system, instrument air system | Piping, piping components and piping elements | Loss of material due to wear | Piping, piping component, piping element | Steel | Air | AMP128 Compressed Air Monitoring | No |  |  | CANDU/ PHWR
106 | 196 | Auxiliary system, instrument air system | Valve | Cracking due to fatigue | Parts | Steel | Air | AMP128 Compressed Air Monitoring | No |  |  | CANDU/ PHWR
106 | 197 | Auxiliary system, spent fuel pool cooling system | Heat exchanger | Loss of material due to general corrosion, pitting corrosion, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | CANDU/ PHWR
106 | 198 | Auxiliary system, spent fuel pool cooling system | Piping, piping components and piping elements | Loss of material due to general corrosion, pitting corrosion, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | CANDU/ PHWR
106 | 199 | Reactor assemblies, moderator and moderator auxiliary systems | Annulus gas system (heat exchanger, piping, valve) | Loss of material due to corrosion | Heat exchanger tubing, piping, valve | Stainless steel | CO2 with small concentration of O2 and D2O | AMP150 CANDU/ PHWR Annulus Gas System | No |  |  | CANDU/ PHWR
106 | 200 | Reactor assemblies, moderator and moderator auxiliary systems | Failed Fuel Detection System (piping) | Loss of material due to wear | Sample tubing | Stainless steel | Primary coolant (D2O) | AMP151 CANDU/ PHWR Failed Fuel Detection System | No |  |  | CANDU/ PHWR
106 | 201 | Primary heat transport auxilliary systems | D2O leakage collection system (piping, pump, tank) | Loss of material due to corrosion | Internal surface | Stainless steel | Primary coolant (D2O), 121°C | AMP149 CANDU/ PHWR Heavy Water Management | No |  |  | CANDU/ PHWR
106 | 202 | Primary heat transport auxilliary systems | D2O supply system (piping) | Loss of material due to corrosion | Inlet and outlet | Stainless steel | Primary coolant (D2O), 94°C | AMP149 CANDU/ PHWR Heavy Water Management | No |  |  | CANDU/ PHWR
106 | 203 | Primary heat transport auxilliary systems | D2O vapour recovery system (dryer, piping) | Loss of material due to corrosion | Internal surface | Carbon steel | Air/Treat water, 38.8°C | AMP149 CANDU/ PHWR Heavy Water Management | No |  |  | CANDU/ PHWR
106 | 204 | Primary heat transport auxilliary systems | D2O clean-up system (drum, filter, Ion heat-exchanger, pump, tank) | Loss of material due to corrosion | Internal surface | Stainless steel | Primary coolant(D2O), 40°C | AMP149 CANDU/ PHWR Heavy Water Management | No |  |  | CANDU/ PHWR
107 | 1 | Containment structures | Common components | Cumulative fatigue damage due to fatigue | Penetration bellow, penetration sleeve | Dissimilar metal weld, stainless steel, steel | Air - indoor uncontrolled, air - outdoor | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR, CANDU/ PHWR, PWR
107 | 2 | Containment structures | Common components | Cracking due to stress corrosion cracking | Penetration bellow, penetration sleeve | Stainless steel, dissimilar metal weld | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Containment Leak Rate Testing, AMP147 Containment Bellows | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 3 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to general and pitting corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 4 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of material due to general and pitting corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 5 | Structures and component supports | Support for piping and components - BWR containment support | Loss of material due to general and pitting corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 6 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 7 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 8 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 9 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 10 | Structures and component supports | Support for piping and components - class 1 | Cumulative fatigue damage due to fatigue | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR, CANDU/ PHWR, PWR
107 | 11 | Structures and component supports | Support for piping and components - class 2 and 3 | Cumulative fatigue damage due to fatigue | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR, CANDU/ PHWR, PWR
107 | 12 | Structures and component supports | Support for piping and components - BWR containment support | Cumulative fatigue damage due to fatigue | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
107 | 13 | Structures and component supports | Support for piping and components - class 1 | Loss of mechanical function due to corrosion, dirt, distortion, overload | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 14 | Structures and component supports | Support for piping and components - class 1 | Fatigue due to vibratory and cyclic thermal loads | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 15 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of mechanical function due to corrosion, dirt, distortion, overload | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 16 | Structures and component supports | Support for piping and components - class 2 and 3 | Fatigue due to vibratory and cyclic thermal loads | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 17 | Structures and component supports | Support for piping and components - BWR containment support | Loss of mechanical function due to corrosion, dirt, distortion, overload | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 18 | Structures and component supports | Support for piping and components - BWR containment support | Fatigue due to vibratory and cyclic thermal loads | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 19 | Structures and component supports | Support for piping and components - class 1 | Reduction or loss of isolation function due to humidity, radiation hardening, sustained vibratory loading, temperature | Vibration isolation element | Non-metallic (e.g. rubber) | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 20 | Structures and component supports | Support for piping and components - class 2 and 3 | Reduction or loss of isolation function due to humidity, radiation hardening, sustained vibratory loading, temperature | Vibration isolation element | Non-metallic (e.g. rubber) | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 21 | Structures and component supports | Support for piping and components - BWR containment support | Reduction or loss of isolation function due to humidity, radiation hardening, sustained vibratory loading, temperature | Vibration isolation element | Non-metallic (e.g. rubber) | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 22 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to general (steel only) pitting and crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel, stainless steel | Treated water <60°C (<140°F) | AMP103 Water Chemistry, AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 23 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No
107 | 24 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No
107 | 25 | Structures and component supports | Support for piping and components - BWR containment support | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 26 | Structures and component supports | Support for piping and components - class 1 | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No
107 | 27 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No
107 | 28 | Structures and component supports | Support for piping and components - BWR containment support | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 29 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to pitting, crevice corrosion | Structural bolting | Stainless steel | Treated water | AMP103 Water Chemistry, AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 30 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of material due to pitting, crevice corrosion | Structural bolting | Stainless steel | Treated water | AMP103 Water Chemistry, AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 31 | Structures and component supports | Support for piping and components - BWR containment support | Loss of material due to pitting, crevice corrosion | Structural bolting | Stainless steel | Treated water | AMP103 Water Chemistry, AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 32 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 33 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of material due to pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 34 | Structures and component supports | Support for piping and components - BWR containment support | Loss of material due to pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR
107 | 35 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 36 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 37 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 38 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 39 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 40 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 41 | Structures and component supports | Support for piping and components - class 1 | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 42 | Structures and component supports | Support for piping and components - BWR containment support | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR
107 | 43 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 44 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 45 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 46 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
107 | 47 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
107 | 48 | Structures and component supports | Support for piping and components - class 1 | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 49 | Structures and component supports | Support for piping and components - class 1 | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 50 | Structures and component supports | Support for piping and components - class 2 and 3 | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 51 | Structures and component supports | Support for piping and components - BWR containment support | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
107 | 52 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 53 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 54 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general and pitting corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 55 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to general and pitting corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 56 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Reduction or loss of isolation function due to humidity, radiation hardening, sustained vibratory loading, temperature | Vibration isolation element | Non-metallic (e.g. rubber) | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 57 | Structures and component supports | Support for piping and components - class 1 | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding surfaces | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 58 | Structures and component supports | Support for piping and components - class 2 and 3 | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding surfaces | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 59 | Structures and component supports | Support for piping and components - BWR containment support | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding surfaces | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 60 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding support bearing, sliding support surface | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 61 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding support bearing, sliding support surface | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 62 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum, stainless steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 63 | Structures and component supports | Support for piping and components - class 1 | None | Support member, weld, bolted connection, support anchorage to building structure | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 64 | Structures and component supports | Support for piping and components - class 1 | None | Support member, weld, bolted connection, support anchorage to building structure | Aluminum, galvanized steel, stainless steel | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 65 | Structures and component supports | Support for piping and components - class 2 and 3 | None | Support member, weld, bolted connection, support anchorage to building structure | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 66 | Structures and component supports | Support for piping and components - class 2 and 3 | None | Support member, weld, bolted connection, support anchorage to building structure | Aluminum, galvanized steel, stainless steel | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 67 | Structures and component supports | Support for piping and components - BWR containment support | None | Support member, weld, bolted connection, support anchorage to building structure | Stainless steel | Air with borated water leakage | None | No |  |  | BWR
107 | 68 | Structures and component supports | Support for piping and components - BWR containment support | None | Support member, weld, bolted connection, support anchorage to building structure | Aluminum, galvanized steel, stainless steel | Air - indoor uncontrolled | None | No |  |  | BWR
107 | 69 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | None | Support member, weld, bolted connection, support anchorage to building structure | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 70 | Structures and component supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | None | Support member, weld, bolted connection, support anchorage to building structure | Aluminum, galvanized steel, stainless steel | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 71 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | None | Support member, weld, bolted connection, support anchorage to building structure | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
107 | 72 | Structures and component supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | None | Support member, weld, bolted connection, support anchorage to building structure | Aluminum, galvanized steel, stainless steel | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 1 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 2 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 3 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 4 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Concrete | None - see remarks | No |  | Provided concrete has low chloride content. | BWR, CANDU/ PHWR, PWR
108 | 5 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 6 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Concrete | None - see remarks | No |  | Provided 1) attributes of the concrete are consistent with ACI 318 or ACI 349 (low water-to-cement ratio, low permeability, and adequate air entrainment) as cited in NUREG-1557, and 2) plant OE indicates no degradation of the concrete | BWR, CANDU/ PHWR, PWR
108 | 7 | Reactor pressure vessel, internals, reactor coolant system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 8 | Engineered safety features | Containment isolation components | Loss of material due to general, pitting, crevice, MIC, fouling that leads to corrosion | Containment isolation piping and components (internal surfaces) | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 9 | Engineered safety features | Containment isolation components | Loss of material due to general corrosion | Containment isolation piping and components (external surfaces) | Steel | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 10 | Engineered safety features | Containment isolation components | Loss of material due to pitting, crevice, MIC, fouling that leads to corrosion | Containment isolation piping and components (internal surfaces) | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 11 | Engineered safety features | Containment isolation components | Loss of material due to general corrosion | Containment isolation piping and components (external surfaces) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 12 | Engineered safety features | Containment isolation components | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 13 | Engineered safety features | Containment isolation components | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 14 | Engineered safety features | Containment isolation components | Loss of material due to general, pitting, crevice corrosion | Containment isolation piping and components (internal surfaces) | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 15 | Engineered safety features | Containment isolation components | Loss of material due to pitting, crevice corrosion | Containment isolation piping and components (internal surfaces) | Stainless steel | Treated water | AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 16 | Engineered safety features | Containment isolation components | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 17 | Engineered safety features | Containment isolation components | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 18 | Engineered safety features | Containment isolation components | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 19 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | Closure bolting | Steel | Air with steam or water leakage | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 20 | Engineered safety features | External surface of components and miscellaneous bolting | Cracking due to cyclic loading, stress corrosion cracking | Closure bolting | Steel, high-strength | Air with steam or water leakage | AMP115 Bolting Integrity | Yes, if TLAA (TLAA115 Fatigue and Thermal Ageing Analysis of Manufacturing Flaws) |  |  | BWR, CANDU/ PHWR, PWR
108 | 21 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 22 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 23 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 24 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 25 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Copper alloy | Any | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 26 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Nickel alloy | Any | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 27 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Air - outdoor (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 28 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Raw water | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 29 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Fuel oil | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 30 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Treated water | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 31 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Underground piping, piping component, piping element | Steel, stainless steel | Air - indoor uncontrolled (external) or condensation (external) | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 32 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Bolting | Steel, stainless steel | Air - outdoor (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 33 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 34 | Engineered safety features | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 35 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 36 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Concrete | None - see remarks | No |  | Provided 1) attributes of the concrete are consistent with ACI 318 or ACI 349 (low water-to-cement ratio, low permeability, and adequate air entrainment) as cited in NUREG-1557, and 2) plant OE indicates no degradation of the concrete | BWR, CANDU/ PHWR, PWR
108 | 37 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 38 | Engineered safety features | Common miscellaneous material, environment combinations | None | Ducting, piping and components | Galvanized steel | Air - indoor controlled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 39 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 40 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Lubricating oil | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 41 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 42 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 43 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 44 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Concrete | None - see remarks | No |  | Provided concrete has low chloride content | BWR, CANDU/ PHWR, PWR
108 | 45 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 46 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Raw water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 47 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Treated water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 48 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Air - indoor uncontrolled (external, internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 49 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Treated borated water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 50 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Air - indoor controlled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 51 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 52 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Condensation (internal, external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 53 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 54 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Closed cycle cooling water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 55 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 56 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 57 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air - outdoor | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 58 | Engineered safety features | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 59 | Auxiliary systems | New fuel storage | Loss of material due to general, pitting, crevice corrosion | Structural steel | Steel | Air - indoor uncontrolled (external) | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 60 | Auxiliary systems | Spent fuel storage | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Steel with stainless steel cladding, stainless steel | Treated borated water | AMP103 Water Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 61 | Auxiliary systems | Overhead heavy load and light load (related to refueling) handling systems | Loss of material due to wear | Crane: rail | Steel | Air - indoor uncontrolled (external), Air - Outdoor | AMP127 Inspection of Overhead Heavy Load and Light Load (Related to Refueling) Handling Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 62 | Auxiliary systems | Overhead heavy load and light load (related to refueling) handling systems | Cumulative fatigue damage due to fatigue | Crane: structural girder | Steel | Air - indoor uncontrolled (external), Air - Outdoor | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection, AMP127 Inspection of Overhead Heavy Load And Light Load (Related To Refueling) Handling Systems A plant-specific ageing management programme | Yes, if TLAA (TLAA108 Fatigue of Cranes) |  |  | BWR, CANDU/ PHWR, PWR
108 | 63 | Auxiliary systems | Overhead heavy load and light load (related to refueling) handling systems | Loss of material due to general corrosion | Crane: rail and structural girder | Steel | Air - indoor uncontrolled (external), Air - Outdoor | AMP127 Inspection of Overhead Heavy Load and Light Load (Related to Refueling) Handling Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 64 | Auxiliary systems | Overhead heavy load and light load (related to refueling) handling systems | Loss of preload due to self-loosening | Crane: structural bolting | Steel | Air - indoor uncontrolled (external), Air - Outdoor | AMP127 Inspection of Overhead Heavy Load and Light Load (Related to Refueling) Handling Systems | No | BWR, CANDU/ PHWR, PWR | IGALL | BWR, CANDU/ PHWR, PWR
108 | 65 | Auxiliary systems | Overhead heavy load and light load (related to refueling) handling systems | Cracking due to stress corrosion cracking | Crane: structural bolting | Steel, high-strength | Air - indoor uncontrolled (external), Air - Outdoor | AMP127 Inspection of Overhead Heavy Load and Light Load (Related to Refueling) Handling Systems | No | BWR, CANDU/ PHWR, PWR | IGALL | BWR, CANDU/ PHWR, PWR
108 | 66 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 67 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 68 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 69 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion, fouling that leads to corrosion | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 70 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to selective leaching | Heat exchanger components | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 71 | Auxiliary systems | Open-cycle cooling water system (service water system) | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 72 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 73 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 74 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 75 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 76 | Auxiliary systems | Open-cycle cooling water system (service water system) | None | Heat exchanger components other than tubes | Titanium (ASTM Grades 1, 2, 7, 11, or 12 that contains > 5% aluminum or more than 0.20% oxygen or any amount of tin) | Raw water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 77 | Auxiliary systems | Open-cycle cooling water system (service water system) | Reduction of heat transfer due to fouling | Heat exchanger tube | Titanium | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 78 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to aggressive chemical attack and leaching | Piping, piping component, piping element | Asbestos cement, reinforced concrete | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 79 | Auxiliary systems | Open-cycle cooling water system (service water system) | Changes in material properties due to aggressive chemical attack | Piping, piping component, piping element | Asbestos cement, reinforced concrete | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 80 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to aggressive chemical attack and leaching | Piping, piping component, piping element | Asbestos cement, reinforced concrete | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 81 | Auxiliary systems | Open-cycle cooling water system (service water system) | Changes in material properties due to aggressive chemical attack | Piping, piping component, piping element | Asbestos cement, reinforced concrete | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 82 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to aggressive chemical attack and leaching | Piping, piping component, piping element | Asbestos cement, reinforced concrete | Soil, concrete | AMP125 Buried and Underground Piping and Tanks, AMP 120 Selective Leaching | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 83 | Auxiliary systems | Open-cycle cooling water system (service water system) | Changes in material properties due to aggressive chemical attack | Piping, piping component, piping element | Asbestos cement, reinforced concrete | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 84 | Auxiliary systems | Open-cycle cooling water system (service water system) | None | Piping, piping component, piping element | Titanium (ASTM Grades 1, 2, 7, 11, or 12 that contains > 5% aluminum or more than 0.20% oxygen or any amount of tin) | Raw water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 85 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Titanium | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 86 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Super austenitic | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 87 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 88 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 89 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to water absorption | Piping, piping component, piping element | HDPE | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 90 | Auxiliary systems | Open-cycle cooling water system (service water system) | Blistering due to water absorption | Piping, piping component, piping element | HDPE | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 91 | Auxiliary systems | Open-cycle cooling water system (service water system) | Change in color due to water absorption | Piping, piping component, piping element | HDPE | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 92 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to water absorption | Piping, piping component, piping element | Fiberglass | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 93 | Auxiliary systems | Open-cycle cooling water system (service water system) | Blistering due to water absorption | Piping, piping component, piping element | Fiberglass | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 94 | Auxiliary systems | Open-cycle cooling water system (service water system) | Change in color due to water absorption | Piping, piping component, piping element | Fiberglass | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 95 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to exposure of rebar - Cracking due to corrosion of embedded steel in concrete | Piping, piping component, piping element | Concrete cylinder piping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 96 | Auxiliary systems | Open-cycle cooling water system (service water system) | Spalling due to exposure of rebar - loss of material (spalling, scaling) due to embedded steel in concrete | Piping, piping component, piping element | Concrete cylinder piping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 97 | Auxiliary systems | Open-cycle cooling water system (service water system) | Corrosion of rebar due to exposure of rebar - Corrosion of rebar due to embedded steel in concrete | Piping, piping component, piping element | Concrete cylinder piping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 98 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to exposure of rebar - Cracking due to corrosion of embedded steel in concrete | Piping, piping component, piping element | Concrete | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 99 | Auxiliary systems | Open-cycle cooling water system (service water system) | Spalling due to exposure of rebar - loss of material (spalling, scaling) due to embedded steel in concrete | Piping, piping component, piping element | Concrete | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 100 | Auxiliary systems | Open-cycle cooling water system (service water system) | Corrosion of rebar due to exposure of rebar - Corrosion of rebar due to embedded steel in concrete | Piping, piping component, piping element | Concrete | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 101 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 102 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 103 | Auxiliary systems | Open-cycle cooling water system (service water system) | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 104 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion, lining, coating degradation | Piping, piping component, piping element | Steel with coating or lining | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 105 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 106 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion, MIC | Piping, piping component, piping element | Steel with coating or wrapping | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 107 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Nickel alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 108 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 109 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 110 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to exposure of rebar - Cracking due to corrosion of embedded steel in concrete | Piping, piping component, piping element | Asbestos cement pipe | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 111 | Auxiliary systems | Open-cycle cooling water system (service water system) | Spalling due to exposure of rebar - loss of material (spalling, scaling) due to embedded steel in concrete | Piping, piping component, piping element | Asbestos cement pipe | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 112 | Auxiliary systems | Open-cycle cooling water system (service water system) | Corrosion of rebar due to exposure of rebar - Corrosion of rebar due to embedded steel in concrete | Piping, piping component, piping element | Asbestos cement pipe | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 113 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to water absorption | Piping, piping component, piping element | Fiberglass | Raw water (internal) | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 114 | Auxiliary systems | Open-cycle cooling water system (service water system) | Blistering due to water absorption | Piping, piping component, piping element | Fiberglass | Raw water (internal) | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 115 | Auxiliary systems | Open-cycle cooling water system (service water system) | Change in color due to water absorption | Piping, piping component, piping element | Fiberglass | Raw water (internal) | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 116 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to water absorption | Piping, piping component, piping element | HDPE | Raw water (internal) | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 117 | Auxiliary systems | Open-cycle cooling water system (service water system) | Blistering to water absorption | Piping, piping component, piping element | HDPE | Raw water (internal) | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 118 | Auxiliary systems | Open-cycle cooling water system (service water system) | Change in color due to water absorption | Piping, piping component, piping element | HDPE | Raw water (internal) | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 119 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to settling | Piping, piping component, piping element | Concrete, cementitious material | Raw Water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 120 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to abrasion, aggressive chemical attack, cavitation, leaching | Piping, piping component, piping element | Concrete, cementitious material | Raw Water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 121 | Auxiliary systems | Open-cycle cooling water system (service water system) | Changes in material properties due to aggressive chemical attack | Piping, piping component, piping element | Concrete, cementitious material | Raw Water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 122 | Auxiliary systems | Open-cycle cooling water system (service water system) | Cracking due to settling | Piping, piping component, piping element | Concrete, cementitious material | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 123 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to abrasion, aggressive chemical attack, cavitation, leaching | Piping, piping component, piping element | Concrete, cementitious material | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components, AMP 120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 124 | Auxiliary systems | Open-cycle cooling water system (service water system) | Changes in material properties due to aggressive chemical attack | Piping, piping component, piping element | Concrete, cementitious material | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 125 | Auxiliary systems | Open-cycle cooling water system (service water system) | Hardening and loss of strength due to elastomer degradation | Elastomer: seal and components | Elastomer | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 126 | Auxiliary systems | Open-cycle cooling water system (service water system) | Loss of material due to erosion | Elastomer: seal and components | Elastomer | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 127 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 128 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 129 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 130 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 131 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 132 | Auxiliary systems | Closed-cycle cooling water system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 133 | Auxiliary systems | Closed-cycle cooling water system | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 134 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 135 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 136 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element, tank | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 137 | Auxiliary systems | Closed-cycle cooling water system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 138 | Auxiliary systems | Closed-cycle cooling water system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 139 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 140 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 141 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  | See ID No.17 | BWR, CANDU/ PHWR, PWR
108 | 142 | Auxiliary systems | Closed-cycle cooling water system | Hardening and loss of strength due to elastomer degradation | Elastomer: seal and components | Elastomer | Closed cycle cooling water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 143 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 144 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 145 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 146 | Auxiliary systems | Closed-cycle cooling water system | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No | BWR, CANDU/ PHWR, PWR | IGALL | BWR, CANDU/ PHWR, PWR
108 | 147 | Auxiliary systems | Ultimate heat sink | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 148 | Auxiliary systems | Ultimate heat sink | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 149 | Auxiliary systems | Ultimate heat sink | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 150 | Auxiliary systems | Ultimate heat sink | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 151 | Auxiliary systems | Ultimate heat sink | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 152 | Auxiliary systems | Ultimate heat sink | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 153 | Auxiliary systems | Ultimate heat sink | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion, lining, coating degradation | Piping, piping component, piping element | Steel with coating or lining | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 154 | Auxiliary systems | Ultimate heat sink | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 155 | Auxiliary systems | Ultimate heat sink | Loss of material due to general, pitting, crevice corrosion, MIC | Piping, piping component, piping element | Steel with coating or wrapping | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 156 | Auxiliary systems | Ultimate heat sink | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Nickel alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 157 | Auxiliary systems | Ultimate heat sink | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 158 | Auxiliary systems | Ultimate heat sink | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 159 | Auxiliary systems | Compressed air system | Loss of material due to general and pitting corrosion | Piping, piping component, piping element | Steel | Condensation (internal) | AMP128 Compressed Air Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 160 | Auxiliary systems | Compressed air system | Loss of material due to general corrosion | Piping and component (external surface) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 161 | Auxiliary systems | Compressed air system | Loss of material due to general (steel only) pitting and crevice corrosion | Closure bolting | Steel, stainless steel | Condensation | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 162 | Auxiliary systems | Compressed air system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 163 | Auxiliary systems | Compressed air system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 164 | Auxiliary systems | Compressed air system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Condensation | AMP128 Compressed Air Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 165 | Auxiliary systems | Compressed air system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Condensation (internal) | AMP128 Compressed Air Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 166 | Auxiliary systems | Waste water system | Loss of material due to general (steel only) pitting and crevice corrosion | Piping, piping component, piping element | Steel, stainless steel | Raw water (potable) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 167 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Raw water (potable) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 168 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Copper alloy | Waste water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 169 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 170 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Nickel alloy | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 171 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Heat exchanger components | Stainless steel | Waste Water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 172 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Heat exchanger components | Nickel alloy | Waste Water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 173 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element, tank | Stainless steel | Waste Water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 174 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element, tank | Nickel alloy | Waste Water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 175 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element, tank | Steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 176 | Auxiliary systems | Waste water system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element, tank | Steel | Waste Water | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 177 | Auxiliary systems | Control room area ventilation system | Loss of material due to general, pitting, crevice corrosion for drip pans and drain lines, MIC | Ducting and components (internal surfaces) | Steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 178 | Auxiliary systems | Control room area ventilation system | Loss of material due to general corrosion | Ducting and components (external surfaces) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 179 | Auxiliary systems | Control room area ventilation system | Loss of material due to general corrosion | Closure bolting, ducting | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 180 | Auxiliary systems | Control room area ventilation system | Hardening and loss of strength due to elastomer degradation | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external, internal) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 181 | Auxiliary systems | Control room area ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 182 | Auxiliary systems | Control room area ventilation system | Loss of material due to general corrosion, pitting, crevice | Piping, piping component, piping element | Copper alloy | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 183 | Auxiliary systems | Control room area ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 184 | Auxiliary systems | Control room area ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 185 | Auxiliary systems | Control room area ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 186 | Auxiliary systems | Control room area ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 187 | Auxiliary systems | Control room area ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 188 | Auxiliary systems | Control room area ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element, tank | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 189 | Auxiliary systems | Control room area ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 190 | Auxiliary systems | Control room area ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 191 | Auxiliary systems | Control room area ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 192 | Auxiliary systems | Control room area ventilation system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 193 | Auxiliary systems | Control room area ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 194 | Auxiliary systems | Control room area ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 195 | Auxiliary systems | Control room area ventilation system | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 196 | Auxiliary systems | Control room area ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 197 | Auxiliary systems | Control room area ventilation system | Loss of material due to selective leaching | Heat exchanger components | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 198 | Auxiliary systems | Control room area ventilation system | Loss of material due to pitting, crevice corrosion | Ducting and components | Stainless steel | Condensation | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 199 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general, pitting, crevice corrosion for drip pans and drain lines, MIC | Ducting and components (internal surfaces) | Steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 200 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general corrosion | Ducting and components (external surfaces) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 201 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general corrosion | Closure bolting, ducting | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 202 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Hardening and loss of strength due to elastomer degradation | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external, internal) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 203 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 204 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general corrosion, pitting, crevice | Piping, piping component, piping element | Copper alloy | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 205 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 206 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 207 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 208 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 209 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 210 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element, tank | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 211 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 212 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 213 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 214 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 215 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 216 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 217 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 218 | Auxiliary systems | Auxiliary and radwaste area ventilation system | Loss of material due to pitting, crevice corrosion | Ducting and components | Stainless steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 219 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general, pitting, crevice corrosion for drip pans and drain lines, MIC | Ducting and components (internal surfaces) | Steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 220 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general corrosion | Ducting and components (external surfaces) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 221 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general corrosion | Closure bolting, ducting | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 222 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 223 | Auxiliary systems | Primary containment heating and ventilation system | Hardening and loss of strength due to elastomer degradation | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external, internal) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 224 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 225 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general corrosion, pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 226 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 227 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 228 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 229 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 230 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 231 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element, tank | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 232 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 233 | Auxiliary systems | Primary containment heating and ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 234 | Auxiliary systems | Primary containment heating and ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 235 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 236 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 237 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to selective leaching | Heat exchanger components | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 238 | Auxiliary systems | Primary containment heating and ventilation system | Loss of material due to pitting, crevice corrosion | Ducting and components | Stainless steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 239 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general, pitting, crevice corrosion for drip pans and drain lines, MIC | Ducting and components (internal surfaces) | Steel | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 240 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general corrosion | Ducting and components (external surfaces) | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 241 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general corrosion | Closure bolting, ducting | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 242 | Auxiliary systems | Diesel generator building ventilation system | Hardening and loss of strength due to elastomer degradation | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external, internal) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 243 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 244 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general corrosion, pitting, crevice | Piping, piping component, piping element | Copper alloy | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 245 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to wear | Elastomer: seal and components | Elastomer | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 246 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 247 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 248 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 249 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 250 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element, tank | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 251 | Auxiliary systems | Diesel generator building ventilation system | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 252 | Auxiliary systems | Diesel generator building ventilation system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 253 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 254 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 255 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 256 | Auxiliary systems | Diesel generator building ventilation system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 257 | Auxiliary systems | Fire protection | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 258 | Auxiliary systems | Fire protection | Hardening and loss of strength, change in dimensions due to weathering | Fire barrier penetration seal | Elastomer | Air - indoor uncontrolled | AMP130 Fire Protection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 259 | Auxiliary systems | Fire protection | Hardening and loss of strength, change in dimensions due to weathering | Fire barrier penetration seal | Elastomer | Air - outdoor | AMP130 Fire Protection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 260 | Auxiliary systems | Fire protection | Loss of material due to wear | Fire rated door | Steel | Air - indoor uncontrolled | AMP130 Fire Protection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 261 | Auxiliary systems | Fire protection | Loss of material due to wear | Fire rated door | Steel | Air - outdoor | AMP130 Fire Protection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 262 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Condensation (internal), moist air | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 263 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion | Piping, piping component, piping element | Steel | Raw water | AMP131 Fire Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 264 | Auxiliary systems | Fire protection | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 265 | Auxiliary systems | Fire protection | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 266 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice corrosion, fouling that leads to corrosion | Piping, piping component, piping element | Stainless steel | Raw water | AMP131 Fire Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 267 | Auxiliary systems | Fire protection | Concrete cracking and spalling due to aggressive chemical attack and reaction with aggregates | Structural fire barrier: wall, ceiling, floor | Reinforced concrete | Air - indoor uncontrolled | AMP130 Fire Protection, AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 268 | Auxiliary systems | Fire protection | Loss of material due to corrosion of embedded steel | Structural fire barrier: wall, ceiling, floor | Reinforced concrete | Air - indoor uncontrolled | AMP130 Fire Protection, AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 269 | Auxiliary systems | Fire protection | Cracking, loss of material due to freeze-thaw, aggressive chemical attack, reaction with aggregates | Structural fire barrier: wall, ceiling, floor | Reinforced concrete | Air - outdoor | AMP130 Fire Protection, AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 270 | Auxiliary systems | Fire protection | Loss of material due to corrosion of embedded steel | Structural fire barrier: wall, ceiling, floor | Reinforced concrete | Air - outdoor | AMP130 Fire Protection, AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 271 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Reactor coolant pump oil collection system: tank | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 272 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Reactor coolant pump oil collection system: piping, tubing, valve body | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 273 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 274 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion, MIC | Piping, piping component, piping element | Copper alloy | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 275 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 276 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 277 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 278 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 279 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Condensation (internal) | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 280 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Fire hydrant | Steel | Air - outdoor | AMP131 Fire Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 281 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Halon, carbon dioxide fire suppression system piping, piping components, piping elements | Steel | Air - indoor uncontrolled (external) | AMP130 Fire Protection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 282 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Raw water | AMP131 Fire Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 283 | Auxiliary systems | Fire protection | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 284 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion | Piping, piping component, piping element | Copper alloy | Raw water | AMP131 Fire Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 285 | Auxiliary systems | Fire protection | Loss of material due to general corrosion, pitting, crevice , MIC | Piping, piping component, piping element | Steel with coating or wrapping | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 286 | Auxiliary systems | Fire protection | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 287 | Auxiliary systems | Fire protection | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 288 | Auxiliary systems | Fire protection | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 289 | Auxiliary systems | Fire protection | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 290 | Auxiliary systems | Fire protection | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 291 | Auxiliary systems | Fire protection | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 292 | Auxiliary systems | Diesel fuel oil system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 293 | Auxiliary systems | Diesel fuel oil system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 294 | Auxiliary systems | Diesel fuel oil system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Steel | Air - outdoor (external) | AMP132 Aboveground Metallic Tanks or AMP134 External Surfaces Monitoring of Mechanical Components if it is visible from outside | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 295 | Auxiliary systems | Diesel fuel oil system | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion | Piping, piping component, piping element, tank | Steel | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 296 | Auxiliary systems | Diesel fuel oil system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Aluminum | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 297 | Auxiliary systems | Diesel fuel oil system | Loss of material due to general, pitting, crevice corrosion, MIC | Piping, piping component, piping element | Copper alloy | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 298 | Auxiliary systems | Diesel fuel oil system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 299 | Auxiliary systems | Diesel fuel oil system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 300 | Auxiliary systems | Diesel fuel oil system | Loss of material due to general corrosion, pitting, crevice , MIC | Piping, piping component, piping element | Steel with coating or wrapping | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 301 | Auxiliary systems | Diesel fuel oil system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 302 | Auxiliary systems | Diesel fuel oil system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 303 | Auxiliary systems | Diesel fuel oil system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 304 | Auxiliary systems | Diesel fuel oil system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 305 | Auxiliary systems | Emergency diesel generator system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 306 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Condensation (internal), moist air | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 307 | Auxiliary systems | Emergency diesel generator system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 308 | Auxiliary systems | Emergency diesel generator system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 309 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general (steel only) pitting and crevice corrosion | Piping, piping component, piping element, diesel engine exhaust | Steel, stainless steel | Diesel exhaust | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 310 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion | Piping, piping component, piping element, tank | Steel | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 311 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 312 | Auxiliary systems | Emergency diesel generator system | Cracking due to stress corrosion cracking | Diesel engine exhaust piping, piping components, piping elements | Stainless steel | Diesel exhaust | AMP135 Inspection of Internal Surfaces in Miscellaneous Piping and Ducting Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 313 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Aluminum | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 314 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 315 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion, MIC | Piping, piping component, piping element | Copper alloy | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 316 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 317 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Fuel oil | AMP119 One-Time Inspection, AMP133 Fuel Oil Chemistry | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 318 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Soil | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 319 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 320 | Auxiliary systems | Emergency diesel generator system | Reduction of heat transfer due to fouling | Heat exchanger tube | Aluminum | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 321 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 322 | Auxiliary systems | Emergency diesel generator system | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 323 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion, MIC | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 324 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion, MIC, fouling that leads to corrosion, lining, coating degradation | Piping, piping component, piping element | Steel with coating or lining | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 325 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 326 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element, tank | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 327 | Auxiliary systems | Emergency diesel generator system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 328 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 329 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 330 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 331 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 332 | Auxiliary systems | Emergency diesel generator system | Loss of material due to general corrosion, pitting, crevice | Heat exchanger components | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 333 | Auxiliary systems | Emergency diesel generator system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 334 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 335 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | Closure bolting | Steel | Air with steam or water leakage | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 336 | Auxiliary systems | External surface of components and miscellaneous bolting | Cracking due to stress corrosion cracking, cyclic loading | Closure bolting | Steel, high-strength | Air with steam or water leakage | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 337 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | Closure bolting, ducting | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 338 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 339 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 340 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 341 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 342 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 343 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Bolting | Steel, stainless steel | Air - outdoor (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 344 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 345 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general corrosion, pitting, crevice | Bolting | Steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks, AMP 134 external surfaces monitoring of mechanical components | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 346 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to self-loosening | Bolting | Steel | Soil | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 347 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to pitting, crevice corrosion | Bolting | Stainless steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks, AMP 134 external surfaces monitoring of mechanical components | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 348 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to self-loosening | Bolting | Stainless steel | Soil | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 349 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 350 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Copper alloy | Any | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 351 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Nickel alloy | Any | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 352 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Air - outdoor (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 353 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Raw water | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 354 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Fuel oil | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 355 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Treated water | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 356 | Auxiliary systems | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Underground piping, piping component, piping element | Aluminum, copper alloy, stainless steel, steel | Air - indoor uncontrolled, condensation (external) | AMP125 Buried and Underground Piping and Tanks, AMP 134 external surfaces monitoring of mechanical components | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 357 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (external, internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 358 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Galvanized steel | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 359 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Air - dry (external, internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 360 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Air - indoor uncontrolled (external, internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 361 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 362 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Air - indoor uncontrolled (external, internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 363 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Lubricating oil | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 364 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Heat exchanger components | Titanium | Air - indoor uncontrolled, air - outdoor | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 365 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 366 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Titanium | Air - indoor uncontrolled, air - outdoor | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 367 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Closed cycle cooling water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 368 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air - outdoor | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 369 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 370 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 371 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Concrete | None - see remarks | No |  | Provided concrete has low chloride content | BWR, CANDU/ PHWR, PWR
108 | 372 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Air - indoor controlled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 373 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - dry | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 374 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 375 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 376 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | PVC | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 377 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | PVC | Condensation (internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 378 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Glass | Waste Water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 379 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Concrete | None - see remarks | No |  | Provided 1) attributes of the concrete are consistent with ACI 318 or ACI 349 (low water-to-cement ratio, low permeability, and adequate air entrainment) as cited in NUREG-1557, and 2) plant OE indicates no degradation of the concrete | BWR, CANDU/ PHWR, PWR
108 | 380 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Air - indoor controlled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 381 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 382 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Air - dry | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 383 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 384 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Fuel oil | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 385 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Raw water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 386 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Treated water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 387 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Treated borated water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 388 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 389 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Air - dry | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 390 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 391 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 392 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Condensation (internal, external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 393 | Auxiliary systems | Common miscellaneous material, environment combinations | None | Piping element | Glass | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 394 | Auxiliary systems | Steam turbine system | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Steam | AMP114 Flow-accelerated Corrosion | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | BWR, CANDU/ PHWR, PWR
108 | 395 | Auxiliary systems | Steam turbine system | Loss of material due to general, pitting, crevice corrosion, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 396 | Auxiliary systems | Steam turbine system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 397 | Steam and power conversion system | Steam turbine system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 398 | Steam and power conversion system | Steam turbine system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 399 | Steam and power conversion system | Steam turbine system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 400 | Steam and power conversion system | Steam turbine system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 401 | Steam and power conversion system | Steam turbine system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 402 | Steam and power conversion system | Steam turbine system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 403 | Steam and power conversion system | Steam turbine system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 404 | Steam and power conversion system | Steam turbine system | Reduction of heat transfer due to fouling | Heat exchanger components and tubes | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 405 | Steam and power conversion system | Steam turbine system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 406 | Steam and power conversion system | Steam turbine system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 407 | Steam and power conversion system | Steam turbine system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 408 | Steam and power conversion system | Steam turbine system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 409 | Steam and power conversion system | Steam turbine system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 410 | Steam and power conversion system | Extraction steam system | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Steam | AMP114 Flow-accelerated Corrosion | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | BWR, CANDU/ PHWR, PWR
108 | 411 | Steam and power conversion system | Extraction steam system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 412 | Steam and power conversion system | Extraction steam system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 413 | Steam and power conversion system | Extraction steam system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 414 | Steam and power conversion system | Extraction steam system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 415 | Steam and power conversion system | Extraction steam system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 416 | Steam and power conversion system | Extraction steam system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 417 | Steam and power conversion system | Condensate system | Wall thinning due to flow accelerated corrosion Loss of material due to flow accelerated corrosion | Piping, piping component, piping element | Steel | Treated water | AMP114 Flow-accelerated Corrosion | Yes, if TLAA (TLAA104 Corrosion Allowances) |  |  | BWR, CANDU/ PHWR, PWR
108 | 418 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 419 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Heat exchanger components | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 420 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 421 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Steel | Air - outdoor (external) | AMP132 Aboveground Metallic Tanks or AMP134 External Surfaces Monitoring of Mechanical Components if it is visible from outside | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 422 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 423 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Steel | Soil, concrete | AMP132 Aboveground Metallic Tanks or AMP134 External Surfaces Monitoring of Mechanical Components if it is visible from outside | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 424 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 425 | Steam and power conversion system | Condensate system | Cracking due to stress corrosion cracking | Piping, piping component, piping element, tank |  | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 426 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Piping, piping component, piping element, tank | Stainless steel | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | Yes, environmental conditions need to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
108 | 427 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Stainless steel | Soil, concrete | AMP132 Aboveground Metallic Tanks | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 428 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Stainless steel | Air - outdoor (external) | AMP132 Aboveground Metallic Tanks or AMP134 External Surfaces Monitoring of Mechanical Components if it is visible from outside | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 429 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Aluminum | Soil, concrete | AMP132 Aboveground Metallic Tanks or AMP134 External Surfaces Monitoring of Mechanical Components if it is visible from outside | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 430 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Tank（external surface) | Aluminum | Air - outdoor (external) | AMP132 Aboveground Metallic Tanks or AMP134 External Surfaces Monitoring of Mechanical Components if it is visible from outside | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 431 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice, MIC | Piping, piping component, piping element, tank | Steel with coating or wrapping | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 432 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice, galvanic, MIC, fouling that leads to corrosion | Heat exchanger components | Steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 433 | Steam and power conversion system | Condensate system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Soil | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 434 | Steam and power conversion system | Condensate system | Loss of material due to selective leaching | Piping, piping component, piping element | Grey cast iron | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 435 | Steam and power conversion system | Condensate system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Closed cycle cooling water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 436 | Steam and power conversion system | Condensate system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Raw water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 437 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 438 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 439 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 440 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 441 | Steam and power conversion system | Condensate system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Closed cycle cooling water >60°C (>140°F) | AMP117 Closed Treated Water Systems | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR, CANDU/ PHWR, PWR
108 | 442 | Steam and power conversion system | Condensate system | Loss of material due to selective leaching | Piping, piping component, piping element | Copper alloy (>15% Zn or >8% Al) | Treated water | AMP120 Selective Leaching | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 443 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Raw water | AMP124 Open-Cycle Cooling Water System | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 444 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 445 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Steel | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 446 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 447 | Steam and power conversion system | Condensate system | Loss of material due to general (steel only) pitting and crevice corrosion | Tank（internal surface) | Steel, stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 448 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 449 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice corrosion | PWR heat exchanger components | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 450 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice, galvanic corrosion | Piping, piping component, piping element | Copper alloy | Closed cycle cooling water | AMP117 Closed Treated Water Systems | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 451 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Heat exchanger components and tubes | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 452 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | PWR heat exchanger components | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 453 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 454 | Steam and power conversion system | Condensate system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 455 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 456 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 457 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 458 | Steam and power conversion system | Condensate system | Loss of material due to general corrosion, pitting, crevice | Piping, piping component, piping element | Stainless steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 459 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice, MIC | Piping, piping component, piping element | Stainless steel | Lubricating oil | AMP119 One-Time Inspection, AMP136 Lubricating Oil Analysis | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 460 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 461 | Steam and power conversion system | Condensate system | Cracking due to stress corrosion cracking | Tank（internal surface) | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 462 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | Closure bolting | Steel | Air with steam or water leakage | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 463 | Steam and power conversion system | External surface of components and miscellaneous bolting | Cracking due to cyclic loading, stress corrosion cracking | Closure bolting | High-strength steel | Air with steam or water leakage | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 464 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Air - indoor uncontrolled (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 465 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Air - outdoor (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 466 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion | External surface | Steel | Condensation (external) | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 467 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion, pitting, crevice | Bolting | Steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks, AMP 134 external surfaces monitoring of mechanical components | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 468 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of preload due to self-loosening | Bolting | Steel | Soil | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 469 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion, pitting, crevice | Bolting | Stainless steel | Soil, concrete | AMP125 Buried and Underground Piping and Tanks, AMP 134 external surfaces monitoring of mechanical components | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 470 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of preload due to self-loosening | Bolting | Stainless steel | Soil | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 471 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion, pitting, crevice | Piping, piping component, piping element | Aluminum | Air - outdoor | AMP134 External Surfaces Monitoring of Mechanical Components | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 472 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Copper alloy | Any | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 473 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Nickel alloy | Any | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 474 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Bolting | Steel, stainless steel | Air - outdoor (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 475 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general corrosion(steel only) pitting and crevice | Underground piping, piping component, piping element | Aluminum, copper alloy, stainless steel, steel | Air - indoor uncontrolled, condensation (external) | AMP125 Buried and Underground Piping and Tanks, AMP 134 external surfaces monitoring of mechanical components | No |  | Buried Steel | BWR, CANDU/ PHWR, PWR
108 | 476 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Bolting | Steel, stainless steel | Air - outdoor (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 477 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of preload due to thermal effects, gasket creep, self-loosening | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 478 | Steam and power conversion system | External surface of components and miscellaneous bolting | Loss of material due to general (steel only) pitting and crevice corrosion | Closure bolting | Steel, stainless steel | Air - indoor uncontrolled (external) | AMP115 Bolting Integrity | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 479 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Air - indoor controlled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 480 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Lubricating oil | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 481 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air - outdoor | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 482 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 483 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Condensation (internal, external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 484 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 485 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Concrete | None - see remarks | No |  | Provided concrete has low chloride content | BWR, CANDU/ PHWR, PWR
108 | 486 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Nickel alloy | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 487 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 488 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | PVC | Air - indoor uncontrolled | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 489 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | PVC | Condensation (internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 490 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Concrete | None - see remarks | No |  | Provided 1) attributes of the concrete are consistent with ACI 318 or ACI 349 (low water-to-cement ratio, low permeability, and adequate air entrainment) as cited in NUREG-1557, and 2) plant OE indicates no degradation of the concrete | BWR, CANDU/ PHWR, PWR
108 | 491 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 492 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 493 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Raw water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 494 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Treated water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 495 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Steel | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 496 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 497 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Copper alloy | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 498 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air with borated water leakage | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 499 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Condensation | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 500 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Gas | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 501 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Closed cycle cooling water | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 502 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 503 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping element | Glass | Air - indoor uncontrolled (external) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 504 | Steam and power conversion system | Common miscellaneous material, environment combinations | None | Piping, piping component, piping element | Aluminum | Air - indoor uncontrolled (external, internal) | None | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 505 | All non-Class 1 | External surface of piping, piping components and piping elements | Cracking due to stress corrosion cracking | External surface of piping, piping component, piping element | Stainless steel | Air - indoor uncontrolled (external, with possibility of exposure to air-borne chlorides or other aggressive species) | A plant-specific ageing management programme | Yes, detection of ageing effects is to be evaluated |  | Supplemental examination to detect cracking | BWR, PWR
201 | 1 | Components environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to thermal degradation of organic materials | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 2 | Components environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to radiation-induced oxidation | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 3 | Components environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to moisture intrusion | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 4 | Components environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to water trees | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 5 | Components environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to chemical contamination | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 6 | Components environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to volatilization of plasticizers | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 7 | Components environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to thermal degradation of organic materials | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 8 | Components environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to radiation-induced oxidation | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 9 | Components environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to volatilization of plasticizers | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 10 | Components environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to chemical contamination | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 11 | Components environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to wear | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 12 | Components environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to thermal degradation of organic materials | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 13 | Components environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to radiation-induced oxidation | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 14 | Components environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to moisture intrusion | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 15 | Components environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to chemical contamination | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 16 | Components environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to volatilization of plasticizers | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 17 | Components environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to thermal degradation of organic materials | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 18 | Components environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to radiation-induced oxidation | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 19 | Components environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to volatilization of plasticizers | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 20 | Components environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to chemical contamination | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 21 | Components environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to wear | Jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 22 | Components environmentally qualified | Wire | Reduced insulation resistance due to thermal degradation of organic materials | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 23 | Components environmentally qualified | Wire | Reduced insulation resistance due to radiation-induced oxidation | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 24 | Components environmentally qualified | Electrical penetration | Loss of sealing; leakage through containment due to thermal degradation of organic materials | Sealing material | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 25 | Components environmentally qualified | Electrical penetration | Loss of sealing; leakage through containment due to radiation-induced oxidation | Sealing material | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 26 | Components environmentally qualified | Electrical penetration | Reduced insulation resistance due to thermal degradation of organic materials | Electric wire/ cable | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 27 | Components environmentally qualified | Electrical penetration | Reduced insulation resistance due to radiation-induced oxidation | Electric wire/ cable | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 28 | Components environmentally qualified | Electrical penetration | Reduced insulation resistance due to moisture intrusion | Electric wire/ cable | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 29 | Components environmentally qualified | Motor (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 30 | Components environmentally qualified | Motor (AC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 31 | Components environmentally qualified | Motor (AC) | Reduced insulation resistance due to mechanical loading | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 32 | Components environmentally qualified | Motor (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 33 | Components environmentally qualified | Motor (AC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 34 | Components environmentally qualified | Motor (AC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 35 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 36 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 37 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to mechanical loading | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 38 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 39 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 40 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 41 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Rotor coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 42 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to radiation-induced oxidation | Rotor coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 43 | Components environmentally qualified | Motor (DC) | Reduced insulation resistance due to mechanical loading | Rotor coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 44 | Components environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 45 | Components environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 46 | Components environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to mechanical loading | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 47 | Components environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 48 | Components environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 49 | Components environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 50 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 51 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 52 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to mechanical loading | Stator coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 53 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 54 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 55 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 56 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Rotor coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 57 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to radiation-induced oxidation | Rotor coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 58 | Components environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to mechanical loading | Rotor coil | Copper, polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 59 | Components environmentally qualified | Terminal and junction box | Increased resistance of connection due to ohmic heating/ sustained vibratory loading/ electrical transients/ chemical contamination/ corrosion/ oxidation | Metalic parts of connection (screw, etc.) | Metal | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 60 | Components environmentally qualified | Terminal and junction box | Loss of sealing function due to thermal degradation of organic materials | Sealing (O ring, LC mold) | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 61 | Components environmentally qualified | Terminal and junction box | Loss of sealing function due to radiation-induced oxidation | Sealing (O ring, LC mold) | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 62 | Components environmentally qualified | Terminal and junction box | Reduced insulation resistance due to thermal degradation of organic materials | Insulation of terminal block | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 63 | Components environmentally qualified | Terminal and junction box | Reduced insulation resistance due to radiation-induced oxidation | Insulation of terminal block | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 64 | Components environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to thermal degradation of organic materials | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 65 | Components environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to radiation-induced oxidation | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 66 | Components environmentally qualified | Cable connection (cable splice, connector, terminal block) | Increased resistance of connection due to ohmic heating/ sustained vibratory loading/ electrical transients/ chemical contamination/ corrosion/ oxidation | Metallic parts | Metal | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 67 | Components environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of sealing function due to thermal degradation of organic materials | Sealing material (O-ring, sealing bush, etc.) | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 68 | Components environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of sealing function due to radiation-induced oxidation | Sealing material (O-ring, sealing bush, etc.) | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
201 | 69 | Components environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of sealing function due to moisture intrusion | Sealing material (O-ring, sealing bush, etc.) | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
202 | 1 | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 2 | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to radiation-induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 3 | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 4 | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to water trees | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP203 Inaccessible Power Cables not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 5 | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 6 | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 6a | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 6b | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 6c | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to significant moisture | jacket / Insulation | Various organic polymers | Adverse localized environment caused by significant moisture | AMP203 Inaccessible Power Cables not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 6d | Components not environmentally qualified | Power cable (Medium voltage) | Reduced insulation resistance due to water trees | jacket / Insulation | Various organic polymers | Adverse localized environment caused by significant moisture | AMP203 Inaccessible Power Cables not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 7 | Components not environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 7a | Components not environmentally qualified | Power cable (Medium voltage) | Loss of mechanical or dielectric strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 8 | Components not environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 8a | Components not environmentally qualified | Power cable (Medium voltage) | Loss of mechanical or dielectric strength due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 9 | Components not environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 9a | Components not environmentally qualified | Power cable (Medium voltage) | Loss of mechanical or dielectric strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 10 | Components not environmentally qualified | Power cable (Medium voltage) | Hardening and loss of strength due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 10a | Components not environmentally qualified | Power cable (Medium voltage) | Loss of mechanical or dielectric strength due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 11 | Components not environmentally qualified | Power cable (Medium voltage) | Loss of mechanical or dielectric strength due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 11a | Components not environmentally qualified | Power cable (Medium voltage) | Hardening due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 11b | Components not environmentally qualified | Power cable (Medium voltage) | Loss of mechanical or dielectric strength due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 12 | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 13 | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to radiation-induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 14 | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 15 | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 16 | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 16a | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 16b | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 16c | Components not environmentally qualified | Power cable (Low voltage) | Reduced insulation resistance due to significant moisture | jacket / Insulation | Various organic polymers | Adverse localized environment caused by significant moisture | AMP203 Inaccessible Power Cables not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 17 | Components not environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 17a | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 18 | Components not environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 18a | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 18b | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 19 | Components not environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 19a | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 20 | Components not environmentally qualified | Power cable (Low voltage) | Hardening and loss of strength due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 20a | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 21 | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 21a | Components not environmentally qualified | Power cable (Low voltage) | Hardening due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 21b | Components not environmentally qualified | Power cable (Low voltage) | Loss of mechanical or dielectric strength due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 22 | Components not environmentally qualified | Wire | Reduced insulation resistance due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 23 | Components not environmentally qualified | Wire | Reduced insulation resistance due to radiation-induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 24 | Components not environmentally qualified | Enclosed bus | Reduced insulation resistance due to surface contamination | Insulation or Insulating supports | Porcelain, Polymer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 25 | Components not environmentally qualified | Enclosed bus | Reduced insulation resistance due to thermal degradation of organic materials | Insulation or Insulating supports | Polymer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 25a | Components not environmentally qualified | Enclosed bus | Reduced insulation resistance due to radiation-induced oxidation | Insulation or Insulating supports | Polymer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 25b | Components not environmentally qualified | Enclosed bus | Reduced insulation resistance due to moisture intrusion | Insulation or Insulating supports | Polymer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 25c | Components not environmentally qualified | Enclosed bus | Reduced insulation resistance due to ohmic heating | Insulation or Insulating supports | Polymer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 26 | Components not environmentally qualified | Enclosed bus | Increased resistance of connection due to loosening connection caused by ohmic heating, thermal cycling | Bus connections | Steel Various metallic materials | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 27 | Components not environmentally qualified | Enclosed bus | Loss of material due to corrosion | Bus conductor | Copper | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 28 | Components not environmentally qualified | Enclosed bus | Loss of material due to corrosion | Housing (enclosure assemblies) | Steel, Aluminum | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 29 | Components not environmentally qualified | Enclosed bus | Hardening and loss of elastomeric material strength due to thermal degradation of organic materials | Enclosure assemblies (gaskets, boots and sealants) | Elastomer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 29a | Components not environmentally qualified | Enclosed bus | Hardening and loss of elastomeric material strength due to radiation-induced oxidation | Enclosure assemblies (gaskets, boots and sealants) | Elastomer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 29b | Components not environmentally qualified | Enclosed bus | Loss of elastomeric material strength due to moisture intrusion | Enclosure assemblies (gaskets, boots and sealants) | Elastomer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 29c | Components not environmentally qualified | Enclosed bus | Hardening and loss of elastomeric material strength due to surface contamination | Enclosure assemblies (gaskets, boots and sealants) | Elastomer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 29d | Components not environmentally qualified | Enclosed bus | Loss of mechanical or dielectric strength due to wear | Bus connections, Insulation or Insulating supports | Various metallic materials, Porcelain, Polymer | Any | AMP204 Metal Enclosed Bus | No |  |  | BWR CANDU/PHWR PWR
202 | 30 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 31 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 32 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to mechanical loading | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 33 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 34 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 35 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 36 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to moisture intrusion | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 37 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to moisture intrusion | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 38 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to moisture intrusion | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 39 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to moisture intrusion | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 40 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to moisture intrusion | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 41 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to oil-mist | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 42 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to oil-mist | Winding | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 43 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to oil-mist | Lead wire | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 44 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to oil-mist | Connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 45 | Components not environmentally qualified | Motor (AC) | Reduced insulation resistance due to oil-mist | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 46 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 47 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 48 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to mechanical loading | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 49 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 50 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 51 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 52 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 53 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to radiation-induced oxidation | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 54 | Components not environmentally qualified | Motor (DC) | Reduced insulation resistance due to mechanical loading | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 55 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 56 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 57 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to mechanical loading | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 58 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 59 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 60 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 61 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to moisture intrusion | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 62 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to oil-mist | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 63 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to oil-mist | Winding | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 64 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to oil-mist | Lead wire | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 65 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to oil-mist | Connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 66 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 67 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to radiation-induced oxidation | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 68 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to mechanical loading | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 69 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 70 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to radiation-induced oxidation | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 71 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to mechanical loading | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 72 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to thermal degradation of organic materials | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 73 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to radiation-induced oxidation | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 74 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to mechanical loading | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 75 | Components not environmentally qualified | MOV actuator (AC) | Reduced insulation resistance due to oil-mist | Rotor coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 76 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to moisture intrusion | Stator coil (insulation) | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 77 | Components not environmentally qualified | MOV actuator (DC) | Reduced insulation resistance due to moisture intrusion | Lead wire, connecting piece | Copper, polymer | Adverse localized environment | AMP214 Motors/ Motor Operated Valves Actuators/ Generators | No |  |  | BWR CANDU/PHWR PWR
202 | 78 | Components not environmentally qualified | Terminal and junction box | Increased resistance of connection due to loosening connection caused by ohmic heating, thermal cycling/ loosening connection, bolt, or mechanical assembly caused by sustained vibration loading/ chemical contamination/ corrosion/ oxidation | Metalic parts of connection(screw, etc.) | Metal | Air-indoor controlled/ air-indoor uncontrolled | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 79 | Components not environmentally qualified | Terminal and junction box | Reduced insulation resistance due to thermal degradation of organic materials | Insulation of terminal block | Polymer | Air-indoor controlled/ air-indoor uncontrolled | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 80 | Components not environmentally qualified | Terminal and junction box | Reduced insulation resistance due to radiation-induced oxidation | Insulation of terminal block | Polymer | Air-indoor controlled/ air-indoor uncontrolled | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 81 | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 82 | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to radiation-induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83 | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83a | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83b | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83c | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83d | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Reduced insulation resistance due to significant moisture | jacket / Insulation | Various organic polymers | Adverse localized environment caused by significant moisture | AMP203 Inaccessible Power Cables not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83e | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Hardening due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83f | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83g | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Hardening due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83h | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83i | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83j | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Hardening due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83k | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83l | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Hardening due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83m | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83n | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83o | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Hardening due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 83p | Components not environmentally qualified | Cable connection (cable splice, connector, terminal block) | Loss of mechanical or dielectric strength due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84 | Components not environmentally qualified | Cable connection (metallic parts cable splice, connector, terminal block) | Increased resistance of connection due to loosening connection caused by ohmic heating, thermal cycling/ loosening connection, bolt, or mechanical assembly caused by sustained vibration loading/ chemical contamination/ corrosion/ oxidation | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84a | Components not environmentally qualified | Cable connection (metallic parts) | Increased resistance of connection due to thermal cycling/loosening connection | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84b | Components not environmentally qualified | Cable connection (metallic parts) | Increased resistance of connection due to electrical transients | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84c | Components not environmentally qualified | Cable connection (metallic parts) | Increased resistance of connection due to wear (vibrations) | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84d | Components not environmentally qualified | Cable connection (metallic parts) | Increased resistance of connection due to surface contamination | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84e | Components not environmentally qualified | Cable connection (metallic parts) | Increased resistance of connection due to corrosion | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 84f | Components not environmentally qualified | Cable connection (metallic parts) | Increased resistance of connection due to oxidation | Metallic parts | Various Metals | Air-indoor controlled/ air-indoor uncontrolled/ air-outdoor | AMP206 Electrical Cable Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 85 | Components not environmentally qualified | Switchgear | Reduced insulation resistance due to thermal degradation of organic materials | Current transformer, potential transformer | Copper, polymer | Adverse localized environment | AMP204 Metal Enclosed Bus, AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 86 | Components not environmentally qualified | Switchgear Electrical Enclosures | Loss of material due to corrosion | Internal supports and cases Housing | Metal | Air-indoor controlled or uncontrolled or Outdoor Adverse localized environment | AMP212 Panels, Distribution Cabinets and Local Control Boxes | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
202 | 86a | Components not environmentally qualified | Electrical Enclosures | Loss of material due to wear | Housing (enclosure assembly moving parts (e.g., hinges, latches, handles, etc.) ) | Metal | Air-indoor controlled or uncontrolled or Outdoor | AMP212 Panels, Distribution Cabinets and Local Control Boxes | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
202 | 86b | Components not environmentally qualified | Electrical Enclosures | Loss of preload due to self-loosening | Fasteners and bolting | Metal | Air-indoor controlled or uncontrolled or Outdoor | AMP212 Panels, Distribution Cabinets and Local Control Boxes | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
202 | 86c | Components not environmentally qualified | Electrical Enclosures | Loss of sealing function due to deterioration of Elastomers | Enclosure assemblies (gaskets, boots and sealants) | Elastomer | Air-indoor controlled or uncontrolled or Outdoor | AMP212 Panels, Distribution Cabinets and Local Control Boxes | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
202 | 87 | Components not environmentally qualified | Circuit breaker | Loss of mechanical function (electrical components) due to gumming of lubricant | Rotation axis | Grease | Adverse localized environment | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 88 | Components not environmentally qualified | Circuit breaker | Reduced insulation resistance due to thermal degradation of organic materials | Coil | Polymer | Adverse localized environment | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 89 | Components not environmentally qualified | Circuit breaker | Loss of mechanical function due to plastic deformation | Spring | Steel | Adverse localized environment | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 90 | Components not environmentally qualified | Circuit breaker | Loss of electrical function due to ohmic heating | Economy resistor | Polymer | Adverse localized environment | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 91 | Components not environmentally qualified | Circuit breaker | Loss of material due to wear | Moving contacts | Copper alloy | Adverse localized environment | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 92 | Components not environmentally qualified | Battery charger/ Inverters/ UPS | Loss of electrical function due to dry out | Capacitor/ PCB | Electrolyte, silver, tin | Air-indoor controlled | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
202 | 93 | Components not environmentally qualified | Battery | Loss of electrical function due to corrosion | Electrode | Lead | Air-indoor controlled | AMP216 Batteries | No |  |  | BWR CANDU/PHWR PWR
202 | 94 | Components not environmentally qualified | Battery | Loss of electrical function due to carbonation and metalizing of the separators | Separator | Polymer | Air-indoor controlled | AMP216 Batteries | No |  |  | BWR CANDU/PHWR PWR
202 | 95 | Components not environmentally qualified | Battery | Decreased battery capacity due to corrosion | Poles, Connections, Electrodes | Lead | Air-indoor controlled | AMP216 Batteries | No |  |  | BWR CANDU/PHWR PWR
202 | 96 | Components not environmentally qualified | Battery | Decreased battery capacity due to chemical processes | Battery parts and the electrolyte | Lead, electrolyte | Air-indoor controlled | AMP216 Batteries | No |  |  | BWR CANDU/PHWR PWR
202 | 97 | Components not environmentally qualified | Battery | Leakage due to cracking | Battery vessel | Polymer | Air-indoor controlled | AMP216 Batteries | No |  |  | BWR CANDU/PHWR PWR
202 | 98 | Components not environmentally qualified | Distribution panel | Loss of material due to corrosion | Housing | Metal | Air-indoor controlled | AMP212 Panels, Distribution Cabinets and Local Control Boxes | No |  |  | BWR CANDU/PHWR PWR
202 | 99 | Components not environmentally qualified | Transformer | Reduced insulation resistance due to thermal degradation of organic materials | Insulation paper of coil | Paper | Air - outdoor | AMP211 Power Transformers not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 100 | Components not environmentally qualified | Transformer | Reduced insulation resistance due to thermal degradation of organic materials | Varnish of coils | Polymer | Air - outdoor | AMP211 Power Transformers not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 101 | Components not environmentally qualified | Transformer | Reduced insulation resistance due to surface contamination | Bushing | Porcelain | Air - outdoor | AMP211 Power Transformers not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 102 | Components not environmentally qualified | Contactor | Increased resistance of connection due to wear/ corrosion | Moving contacts | Copper alloy | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 103 | Components not environmentally qualified | Contactor | Reduced insulation resistance due to thermal degradation of organic materials | Coil wiring of electromagnetic contact | Copper, Polymer | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 104 | Components not environmentally qualified | Fuse holder | Increased resistance of connection due to chemical contamination/ Loosening connection caused by ohmic heating, thermal cycling/ frequent manipulation | Metallic clamp | Copper alloy | Air-indoor controlled/ air-indoor uncontrolled | AMP205 Fuse Holders not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
202 | 105 | Components not environmentally qualified | Transmission conductors | Loss of conductor strength due to corrosion | Transmission conductors | Aluminum/ steel | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 106 | Components not environmentally qualified | Transmission conductors | Loss of material due to wear | Transmission conductors | Aluminum/ steel | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 107 | Components not environmentally qualified | Transmission conductors | Increased resistance of connection due to oxidation/ loss of preload | Connection of transmission conductors | Aluminum/ steel | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 108 | Components not environmentally qualified | Relay, protection relay | Reduced insulation resistance due to thermal degradation of organic materials | Insulation of coil | Polymer | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 109 | Components not environmentally qualified | Relay, protection relay | Loss of electrical function due to wear | Contact | Silver | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  |  | BWR CANDU/PHWR PWR
202 | 110 | Components not environmentally qualified | Relay, protection relay | Loss of electrical function due to emergence of whiskers | Electronic/ PCB | Tin, zinc | Air-indoor controlled | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
202 | 111 | Components not environmentally qualified | Relay, contactor, breaker | Contact sticking due to surge or voltage spike | Moving Contact | Metal | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays |  |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
202 | 112 | Components not environmentally qualified | Relay, contactor, breaker | Increased friction due to soaking corrosion | Moving parts | Metal, Polymer | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays |  |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
202 | 113 | Components not environmentally qualified | High voltage insulator | Reduced insulation resistance due to surface contamination | Surface of the insulators | Glass, polymer, porcelain | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 114 | Components not environmentally qualified | High voltage insulator | Reduced insulation resistance due to ohmic heating | Insulation | Porcelain | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 115 | Components not environmentally qualified | High voltage insulator | Loss of material due to wear | Surface of the insulators | Glass, polymer, porcelain | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 116 | Components not environmentally qualified | High voltage insulator | Loss of material due to corrosion | Cable clamp | Galvanized steel | Air - outdoor | AMP208 High Voltage Insulators and Transmission Conductors | No |  |  | BWR CANDU/PHWR PWR
202 | 117 | Components not environmentally qualified | Fuse holder | Increased resistance of connection due to corrosion, oxidation, fatigue, ohmic heating, thermal cycling, electrical transients, frequent manipulation or vibration | Metallic clamp | Copper alloy | Air-indoor controlled/ air-indoor uncontrolled | AMP205 Fuse Holders not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
203 | 1 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to thermal degradation of organic materials | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 2 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to radiation-induced oxidation | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 3 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to chemical contamination | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 4 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to radiolysis | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 5 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to moisture intrusion | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 6 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to wear | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 7 | Components environmentally qualified | I&C cable | Reduced insulation resistance due to volatilization of plasticizers | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 8 | Components environmentally qualified | I&C cable | Hardening and loss of strength due to thermal degradation of organic materials | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 9 | Components environmentally qualified | I&C cable | Hardening and loss of strength due to radiation-induced oxidation | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 10 | Components environmentally qualified | I&C cable | Hardening and loss of strength due to volatilization of plasticizers | Insulation, jacket | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification, AMP210 Condition Monitoring of Electrical and I&C Cables Subject to Environmental Qualification Requirements | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 11 | Components environmentally qualified | Transmitter | Loss of sealing function due to thermal degradation of organic materials | Gasket, O-ring | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 12 | Components environmentally qualified | Transmitter | Loss of sealing function due to radiation-induced oxidation | Gasket, O-ring | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 13 | Components environmentally qualified | Transmitter | Calibration drift and deviation of setpoint due to thermal fatigue/ wear/ corrosion/ erosion-corrosion/ vibrational fatigue/ hydraulic shockhydraulic pressure fluctuations | Diaphragm | Metal | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 14 | Components environmentally qualified | Transmitter | Characteristic change due to material depletion/ changing material properties | Printed circuit board | Electronic components | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 15 | Components environmentally qualified | Transmitter | Degradation of electronic components due to thermal degradation of organic materials/ radiation damage/ moisture instrusion | Printed circuit board | Electronic components | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 16 | Components environmentally qualified | Transmitter | Characteristic change due to thermal fatigue/ wear/ corrosion/ erosion | Sensor module | Metal | Adverse Localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 17 | Components environmentally qualified | Sensor | Hardening and loss of strength due to thermal degradation of organic materials | Cable, conector | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 18 | Components environmentally qualified | Sensor | Reduced insulation resistance due to thermal degradation of organic materials | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 19 | Components environmentally qualified | Sensor | Reduced insulation resistance due to radiation-induced oxidation | Insulation | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 20 | Components environmentally qualified | Sensor | Hardening and loss of strength due to radiation-induced oxidation | Cable, conector | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 21 | Components environmentally qualified | Sensor | Characteristic change | Printed circuit board | Electronic components | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 22 | Components environmentally qualified | Sensor | Calibration drift and deviation of setpoint due to material depletion/ changing material properties/ vibrational fatigue/ hydraulic shock hydraulic pressure fluctuations | Electrical components and printed circuits | Metal | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 23 | Components environmentally qualified | Sensor | Characteristic change due to material depletion/ changing material properties | Sensor | Boron | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 24 | Components environmentally qualified | Sensor | Increased resistance of connection due to corrosion | Connector | Contact material | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 25 | Components environmentally qualified | Sensor | Reduced insulation resistance due to moisture intrusion | Cable, conector | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 26 | Components environmentally qualified | Sensor | Winding/ coil failure due to sustained vibratory loading/ mechanical loading/ ohmic heating | Sensor element | Platinum | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 27 | Components environmentally qualified | Switches | Reduced insulation resistance due to thermal degradation of organic materials | Gasket, seal | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 28 | Components environmentally qualified | Switches | Characteristic change due to fatigue | Diaphragm | Stainless Steel | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 29 | Components environmentally qualified | Switches | Increased resistance of connection due to corrosion | Microswitch | Contact material | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 30 | Components environmentally qualified | Switches | Increased resistance of connection due to wear | Contact | Contact material | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 31 | Components environmentally qualified | Switches | Loss of sealing function due to thermal degradation of organic materials | Gasket, seal | Polymer | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 32 | Components environmentally qualified | Amplifier | Characteristic change | Printed circuit board | Electronic components | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
203 | 33 | Components environmentally qualified | Electronics | Characteristic change due to dry out | Printed circuit board | Electronic components | Adverse localized environment | AMP207 Environmental Qualification of Electrical and I&C Equipment, AMP209 Re-assessment Qualification of Electrical and I&C Equipment Relevant to an Environmental Qualification | TLAA201 Environmental Qualification of Electrical and I&C Components |  |  | BWR CANDU/PHWR PWR
204 | 1 | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 2 | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to radiation-induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 3 | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 3a | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 4 | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 5 | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 6 | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 6a | Components not environmentally qualified | I&C cable | Reduced insulation resistance due to significant moisture | jacket / Insulation | Various organic polymers | Adverse localized environment caused by significant moisture | AMP203 Inaccessible Power Cables not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 7 | Components not environmentally qualified | I&C cable | Hardening and loss of strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 7a | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength due to thermal degradation of organic materials | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 8 | Components not environmentally qualified | I&C cable | Hardening and loss of strength due to radiation-induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 8a | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength due to radiation induced oxidation | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 9 | Components not environmentally qualified | I&C cable | Hardening and loss of strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 9a | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength due to volatilization of plasticizers | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 9b | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength or shield integrity due to moisture intrusion | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 9c | Components not environmentally qualified | I&C cable | Hardening due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 9d | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength due to surface contamination | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 9e | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength or shield integrity due to wear | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 9f | Components not environmentally qualified | I&C cable | Hardening due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements, AMP202 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements uised in Instrumentation Circuits | No |  |  | BWR CANDU/PHWR PWR
204 | 9g | Components not environmentally qualified | I&C cable | Loss of mechanical or dielectric strength due to radiolysis | jacket / Insulation | Polymer | Adverse localized environment | AMP201 Insulation Materials for Electrical Cables and Connections not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 10 | Components not environmentally qualified | Transmitter | Loss of sealing function due to thermal degradation of organic materials | Gasket, O-ring | Polymer | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 11 | Components not environmentally qualified | Transmitter | Loss of sealing function due to radiation-induced oxidation | Gasket, O-ring | Polymer | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 12 | Components not environmentally qualified | Transmitter | Characteristic change due to thermal fatigue/ wear/ corrosion/ erosion-corrosion/ vibrational fatigue/ hydraulic shockhydraulic pressure fluctuations | Diaphragm | Metal | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 13 | Components not environmentally qualified | Transmitter | Characteristic change due to material depletion/ changing material properties | Printed circuit board | Electronic components | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 14 | Components not environmentally qualified | Transmitter | Degradation of electronic components due to thermal and mechanical loading/ radiation damage/ moisture instrusion | Printed circuit board | Electronic components | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 15 | Components not environmentally qualified | Transmitter | Characteristic change due to thermal fatigue/ wear/ corrosion/ erosion | Sensor module | Metal | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 16 | Components not environmentally qualified | Sensor | Characteristic change | Printed circuit board | Electronic components | Adverse localized environment | AMP213 Whiskers and Capacitors with Liquid Electrolyte, AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 17 | Components not environmentally qualified | Sensor | Characteristic change due to material depletion/ changing material properties/ vibration | Sensor | Various materials | Adverse localized environment | AMP213 Whiskers and Capacitors with Liquid Electrolyte, AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 18 | Components not environmentally qualified | Sensor | Reduced insulation resistance due to moisture intrusion | RTD and thermocouple seals | Various insulation materials | Adverse localized environment | AMP217 Sensors and Transmitters not Subject to Environmental Qualification Requirements | No |  |  | BWR CANDU/PHWR PWR
204 | 19 | Components not environmentally qualified | Amplifier | Calibration drift and deviation of setpoint due to degradation of electronic components | Printed circuit board | Electronic components | Air-indoor controlled | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
204 | 20 | Components not environmentally qualified | Amplifier | Increased resistance of connection due to electrostatic discharge | Connection, insulation | Metal | Air-indoor controlled | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
204 | 21 | Components not environmentally qualified | Panel | Increased resistance of connection due to corrosion | Internal parts | Metal | Adverse localized environment (only for local control box)/ air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 22 | Components not environmentally qualified | Panel | Reduced insulation resistance due to thermal and mechanical loading | Permanent magnetic generator set | Polymer | Adverse localized environment (only for local control box)/ air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 23 | Components not environmentally qualified | Panel | Reduced insulation resistance due to moisture intrusion | Bus duct, insulation support plate | Polymer | Adverse localized environment (only for local control box)/ air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 24 | Components not environmentally qualified | Panel | Reduced insulation resistance due to thermal degradation of organic materials | Coil | Elastomer | Adverse localized environment (only for local control box)/ air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 25 | Components not environmentally qualified | Panel | Reduced insulation resistance due to dry out | Timer | Electronic components | Adverse localized environment (only for local control box)/ air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 26 | Components not environmentally qualified | Panel | Characteristic change due to material depletion/ changing material properties | Indicator, voltage regulator, instrument, resistor | Electronic components | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 27 | Components not environmentally qualified | Panel | Characteristic change due to dry out | Power supply equipment, signal convertor, protection relay | Electronic components | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 28 | Components not environmentally qualified | Panel | Loss of mechanical function due to corrosion | Supports and cases | Steel | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 29 | Components not environmentally qualified | Panel | Loss of mechanical function due to wear | Mechanical parts | Metal | Air-indoor controlled | AMP212 Panels, Distribution Cabinets and Local Control Boxes, AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 30 | Components not environmentally qualified | Panel | Loss of mechanical function due to hardening of the lubricant inducing gumming or gumming of the lubricant | Operating mechanism of field relay | Grease | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 31 | Components not environmentally qualified | Panel | Increased resistance of connection due to fouling | Operation switch | Contact material | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 32 | Components not environmentally qualified | Panel | Increased resistance of connection due to corrosion | Internal parts | Metal | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 33 | Components not environmentally qualified | Panel | Characteristic change due to material depletion/ changing material properties | Printed circuit board | Electronic components | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 34 | Components not environmentally qualified | Panel | Increased resistance of connection due to moisture intrusion | Relay | Metal | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 35 | Components not environmentally qualified | Panel | Reduced insulation resistance due to thermal degradation of organic materials | Relay | Polymer | Air-indoor controlled | AMP215 Switchgears/ Breakers/ Distribution Panels/ Contactors/ Protection Relays/ Relays | No |  | Adverse localized environment is only for local control box | BWR CANDU/PHWR PWR
204 | 36 | Components not environmentally qualified | Electronics | Loss of material due to dry out | Electrolytic capacitors | Electronic components | Adverse localized environment | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
204 | 37 | Components not environmentally qualified | Electronics | Characteristic change due to dry out | Electrolytic capacitors | Electronic components | Adverse localized environment | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
204 | 38 | Components not environmentally qualified | Electronics | Characteristic change | Printed circuit board | Electronic components | Adverse localized environment | AMP213 Whiskers and Capacitors with Liquid Electrolyte | No |  |  | BWR CANDU/PHWR PWR
301 | 1 | Containment structures | Common components | Cumulative fatigue damage due to fatigue | Penetration bellow, penetration sleeve | Dissimilar metal weld, stainless steel, steel | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if TLAA (TLAA303 Cumulative Fatigue Damage of Containment Liners and Penetrations) |  |  | BWR, CANDU/ PHWR, PWR
301 | 2 | Containment structures | Common components | Loss of material due to general, pitting, crevice corrosion | Personnel airlock, equipment hatch, crd hatch | Steel | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 3 | Containment structures | Common components | Loss of material due to general, pitting, crevice corrosion | Pressure-retaining bolting | Steel | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 4 | Containment structures | Common components | Loss of preload due to self-loosening | Pressure-retaining bolting | Any | Any | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 5 | Containment structures | Common components | Loss of coating integrity due to blistering, cracking, flaking, peeling, physical damage | Service level 1 coating | Coating | Air - indoor uncontrolled | AMP308 Protective Coating Monitoring and Maintenance Programme | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 6 | Containment structures | Common components | Loss of material due to general, pitting, crevice corrosion | Penetration sleeve | Steel, dissimilar metal welds | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 7 | Containment structures | Common components | Cracking due to cyclic loading | Penetration bellow, penetration sleeve | Dissimilar metal weld, stainless steel, steel | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 8 | Containment structures | Common components | Cracking due to stress corrosion cracking | Penetration bellow, penetration sleeve | Stainless steel, dissimilar metal weld | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, detection of ageing effects is to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
301 | 9 | Containment structures | Common components | Loss of material due to general, pitting, crevice corrosion | Penetration bellow, penetration sleeve | Stainless steel, dissimilar metal weld | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, detection of ageing effects is to be evaluated |  |  | BWR, CANDU/ PHWR, PWR
301 | 10 | Containment structures | Common components | Loss of leak tightness due to mechanical wear of locks, hinges and closure mechanisms | Personnel airlock, equipment hatch, CRD hatch: lock, hinge, and closure mechanism | Steel | Air - indoor uncontrolled, air - outdoor | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 11 | Containment structures | Common components | Loss of sealing function due to damage, erosion, surface cracks, tear, wear or other defects | Moisture barrier (caulking, flashing, and other sealants) | Elastomer, rubber, other similar materials | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 12 | Containment structures | Common components | Loss of sealing function due to damage, erosion, surface cracks, tear, wear or other defects | Gasket, seal | Elastomer, rubber, other similar materials | Air - indoor uncontrolled, air - outdoor | AMP304 Containment Leak Rate Testing | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 13 | Containment structures | Common components | Loss of material due to general, pitting, crevice corrosion | Active drains | Austenitic steel | Air - indoor uncontrolled, air - outdoor | None - see remarks | No |  | For WWER Design: Slovakia performs leak detection, in-service inspection and thickness measurement. | PWR
301 | 14 | Containment structures | Common components | Loss of material due to general, pitting, crevice corrosion | Active drains | Austenitic steel | Borated water | None - see remarks | No |  | For WWER Design: Slovakia performs leak detection, in-service inspection and thickness measurement. | PWR
301 | 15 | Containment structures | Common components | Loss of sealing function due to deterioration of gaskets, moisture barriers, seals (caulking, flashing, and other sealants) | Low, high voltage electrical penetration | Elastomer, rubber, other similar materials | Air-indoor controlled | AMP304 Containment Leak Rate Testing | No |  |  | PWR
301 | 16 | Containment structures | Concrete containments (reinforced and prestressed) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | CANDU/ PHWR, PWR
301 | 17 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to corrosion | Prestressing system: tendon, anchorage component | Steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR, CANDU/ PHWR, PWR
301 | 18 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of prestress due to creep, elevated temperature, relaxation, shrinkage | Prestressing system: tendon | Steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP313 Containment Prestressing System, AMP311 Containment Monitoring System | Yes, if TLAA (TLAA301 Concrete Containment Tendon Prestress) |  |  | CANDU/ PHWR, PWR
301 | 19 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): dome, wall, basemat, ring girders, buttresses | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | CANDU/ PHWR, PWR
301 | 20 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking and distortion due to increased stress levels from settlement | Concrete: dome, wall, basemat, ring girders, buttresses | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  |  | CANDU/ PHWR, PWR
301 | 21 | Containment structures | Concrete containments (reinforced and prestressed) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): dome, wall, basemat, ring girders, buttresses | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | CANDU/ PHWR, PWR
301 | 22 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): dome, wall, basemat, ring girders, buttresses | Concrete | Air - outdoor, ground water, soil | None - see remarks | Yes, for plants located in moderate to severe weathering conditions |  | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | CANDU/ PHWR, PWR
301 | 23 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): basemat, buttresses, dome, ring girders, wall | Concrete | Air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | CANDU/ PHWR, PWR
301 | 24 | Containment structures | Concrete containments (reinforced and prestressed) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat, buttresses, dome, ring girders, wall | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | CANDU/ PHWR, PWR
301 | 25 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat, buttresses, dome, ring girders, wall | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | CANDU/ PHWR, PWR
301 | 26 | Containment structures | Concrete containments (reinforced and prestressed) | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: dome, wall, basemat, ring girders, buttresses | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | CANDU/ PHWR, PWR
301 | 27 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | CANDU/ PHWR, PWR
301 | 28 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): dome, wall, basemat, ring girders, buttresses | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | CANDU/ PHWR, PWR
301 | 29 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, buttresses, dome, ring girders, reinforcing steel, wall | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | CANDU/ PHWR, PWR
301 | 30 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (accessible areas): basemat, buttresses, dome, ring girders, wall | Concrete | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | CANDU/ PHWR, PWR
301 | 31 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): dome, wall, basemat, ring girders, buttresses, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring | No |  | For WWER and CANDU plants use plant specific aging management program approved by the national nuclear regulatory agency | CANDU/ PHWR, PWR
301 | 32 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to general, pitting, crevice corrosion | Steel elements (inaccessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR, CANDU/ PHWR, PWR
301 | 33 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of sealing function, cracks, abrasion due to wear and tear | Liner on interior containment surface | Non-metallic liner | Air-indoor controlled | AMP309 Non-metallic Liner | No |  |  | CANDU/ PHWR, PWR
301 | 34 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of mechanical function due to exposure to environment | Liner on interior containment surface | Non-metallic liner | Air-indoor controlled | AMP309 Non-metallic Liner | No |  |  | CANDU/ PHWR, PWR
301 | 35 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of strength due to irradiation | Concrete: dome, wall, basemat, ring girders, buttresses | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, see remarks |  | Further evaluation required if the estimated irradiation dose (neutron and gamma ray) at the time of end of plant operation (40-80 years) by analysis will reach the level that may degrade concrete strength. 6.The radiation limits (neutron:app.1x10^20n/c | PWR
301 | 36 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of strength due to creep and shrinkage | All concrete elements | Concrete | Any | AMP306 Structures Monitoring | Yes, if TLAA (TLAA302 CANDU/PHWR Concrete Strength Reduction due to Creep and Shrinkage) |  |  | CANDU/ PHWR
301 | 37 | Containment structures | Concrete containments (reinforced and prestressed) | Vibrating wire or pressure or temperature sensors failure or recorder obsolescence installed in concrete structures due to lack of electrical continuity, mechanical dislocation, corrosion, component rupture or excess concrete strain | Concrete: basemat, containment, wall | Sensor | Air - indoor uncontrolled, concrete | AMP311 Containment Monitoring System | No |  |  | PWR
301 | 38 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking due to restraint shrinkage, creep and aggressive environment | Concrete (accessible areas): basemat, containment, wall | Concrete | Air - outdoor | None - see remarks | No |  | In France, visual inspection every 5 years for sea sites or every 10 years for river sites - visual inspection before and after pressure test (every 10 years) | PWR
301 | 39 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to general, pitting, crevice corrosion | Liner | Austenitic steel | Borated water | None - see remarks | No |  | For WWER Design: Slovakia uses ageing management program of reactor building. | PWR
301 | 40 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to general, pitting, crevice corrosion | Liner | Steel | Borated water | None - see remarks | No |  | For WWER Design: Slovakia and Czech Rep. perform local leak rate test, visual inspection, thickness measurement (UT) | PWR
301 | 41 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to corrosion, defects of material surface layer due to chemical attack | Liner | Austenitic steel | Borated water | None - see remarks | No |  | For WWER Design: Slovakia and Czech Rep. perform local leak rate test, visual inspection, thickness measurement (UT) | PWR
301 | 42 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to corrosion, defects of material surface layer due to chemical attack | Liner | Steel | Borated water | None - see remarks | No |  | For WWER Design: Slovakia and Czech Rep. perform local leak rate test, visual inspection, thickness measurement (UT) | PWR
301 | 43 | Containment structures | Concrete containments (reinforced and prestressed) | Loss of material due to general, pitting, crevice corrosion | Liner | Austenitic steel | Air - indoor uncontrolled, air - outdoor | None - see remarks | No |  | For WWER Design: Slovakia and Czech Rep. use visual inspection | PWR
301 | 44 | Containment structures | Concrete containments (reinforced and prestressed) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, buttresses, dome, ring girders, reinforcing steel, wall | Concrete, steel | Water | None - see remarks | No |  | For WWER Design: Slovakia and Czech Rep. use visual inspection | PWR
301 | 45 | Containment structures | Concrete containments (reinforced and prestressed) | Defects of coating, corrosion of reinforcement, liner and concrete, increased porosity and permeability of reinforced concrete due to chemical attack | All walls | Reinforced concrete | Acid, hydroxide | None - see remarks | No |  | For WWER Design: Slovakia and Czech Rep. use visual inspection | PWR
301 | 46 | Containment structures | Concrete containments (reinforced and prestressed) | Plate bulging of containment liners due to temperature and concrete creep | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled, concrete | AMP306 Structures Monitoring | No |  | In France, visual inspection every 10 years before and after full pressure test geometric contrôle every 10 years every on 5 typical plate | PWR
301 | 47 | Containment structures | Mark I concrete containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
301 | 48 | Containment structures | Mark I concrete containment | Fretting or lockup due to mechanical wear | Steel elements: drywell head, downcomer | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 49 | Containment structures | Mark I concrete containment | Loss of material due to general (steel only) pitting and crevice corrosion | Steel elements: suppression chamber (torus) liner (interior surface) | Steel, stainless steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 50 | Containment structures | Mark I concrete containment | Cracking and distortion due to increased stress levels from settlement | Concrete elements, all | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  |  | BWR
301 | 51 | Containment structures | Mark I concrete containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: basemat, containment, wall | Concrete | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 52 | Containment structures | Mark I concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): containment, wall, basemat | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR
301 | 53 | Containment structures | Mark I concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: downcomer piping | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 54 | Containment structures | Mark I concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): suppression chamber, drywell, drywell head, embedded shell, region shielded by diaphragm floor (as applicable) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 55 | Containment structures | Mark I concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat, containment, wall | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 56 | Containment structures | Mark I concrete containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: basemat, containment, wall | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
301 | 57 | Containment structures | Mark I concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat, containment, wall | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 58 | Containment structures | Mark I concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): suppression chamber, drywell, drywell head, embedded shell, region shielded by diaphragm floor (as applicable) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  | Additional plant-specific activities are warranted if loss of material due to corrosion is significant for inaccessible areas (embedded containment steel shell or liner). | BWR
301 | 59 | Containment structures | Mark I concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 60 | Containment structures | Mark I concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
301 | 61 | Containment structures | Mark I concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): containment, wall, basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 62 | Containment structures | Mark II concrete containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
301 | 63 | Containment structures | Mark II concrete containment | Loss of material due to corrosion | Prestressing system: tendon, anchorage component | Steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 64 | Containment structures | Mark II concrete containment | Loss of prestress due to creep, elevated temperature, relaxation, shrinkage | Prestressing system: tendon | Steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP313 Containment Prestressing System, AMP311 Containment Monitoring System | Yes, if TLAA (TLAA301 Concrete Containment Tendon Prestress) |  |  | BWR
301 | 65 | Containment structures | Mark II concrete containment | Fretting or lockup due to mechanical wear | Steel elements: drywell head, downcomer | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 66 | Containment structures | Mark II concrete containment | Cumulative fatigue damage due to fatigue | Steel elements: vent header, downcomer | Steel, stainless steel | Air - indoor uncontrolled, treated water | None - see remarks | Yes, if TLAA (TLAA303 Cumulative Fatigue Damage of Containment Liners and Penetrations) |  |  | BWR
301 | 67 | Containment structures | Mark II concrete containment | Loss of material due to general (steel only) pitting and crevice corrosion | Steel elements: suppression chamber (torus) liner (interior surface) | Steel, stainless steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 68 | Containment structures | Mark II concrete containment | Cracking and distortion due to increased stress levels from settlement | Concrete elements, all | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR
301 | 69 | Containment structures | Mark II concrete containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: basemat, containment, wall | Concrete | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 70 | Containment structures | Mark II concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): containment, wall, basemat | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. | BWR
301 | 71 | Containment structures | Mark II concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: downcomer piping | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 72 | Containment structures | Mark II concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): suppression chamber, drywell, drywell head, embedded shell, region shielded by diaphragm floor (as applicable) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 73 | Containment structures | Mark II concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat, containment, wall | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 74 | Containment structures | Mark II concrete containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: basemat, containment, wall | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
301 | 75 | Containment structures | Mark II concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat, containment, wall | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 76 | Containment structures | Mark II concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): suppression chamber, drywell, drywell head, embedded shell, region shielded by diaphragm floor (as applicable) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  | Additional plant-specific activities are warranted if loss of material due to corrosion is significant for inaccessible areas (embedded containment steel shell or liner). | BWR
301 | 77 | Containment structures | Mark II concrete containment | Cracking due to cyclic loading | Steel elements: vent header, downcomer | Steel, stainless steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 78 | Containment structures | Mark II concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 79 | Containment structures | Mark II concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
301 | 80 | Containment structures | Mark II concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): containment, wall, basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 81 | Containment structures | Mark III concrete containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
301 | 82 | Containment structures | Mark III concrete containment | Cracking due to stress corrosion cracking | Steel elements: suppression chamber shell (interior surface) | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 83 | Containment structures | Mark III concrete containment | Loss of material due to general, pitting and crevice corrosion | Steel elements: suppression chamber shell (interior surface) | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 84 | Containment structures | Mark III concrete containment | Cracking and distortion due to increased stress levels from settlement | Concrete elements, all | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR
301 | 85 | Containment structures | Mark III concrete containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: basemat, dome, wall | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
301 | 86 | Containment structures | Mark III concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 87 | Containment structures | Mark III concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR
301 | 88 | Containment structures | Mark III concrete containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Air - outdoor, ground water, soil | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR
301 | 89 | Containment structures | Mark III concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 90 | Containment structures | Mark III concrete containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): basemat, dome, wall | Concrete | Air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 91 | Containment structures | Mark III concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat, dome, wall | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 92 | Containment structures | Mark III concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat, dome, wall | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 93 | Containment structures | Mark III concrete containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 94 | Containment structures | Mark III concrete containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (accessible areas): basemat, dome, wall | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 95 | Containment structures | Mark III concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, dome, reinforcing steel, wall | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 96 | Containment structures | Mark III concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): dome, wall, basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring | No |  |  | BWR
301 | 97 | Containment structures | Mark III concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR
301 | 98 | Containment structures | A-BWR concrete containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
301 | 99 | Containment structures | A-BWR concrete containment | Cracking due to stress corrosion cracking | Steel elements: suppression chamber shell (interior surface) | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 100 | Containment structures | A-BWR concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: suppression chamber shell (interior surface) | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 101 | Containment structures | A-BWR concrete containment | Cracking and distortion due to increased stress levels from settlement | Concrete elements, all | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR
301 | 102 | Containment structures | A-BWR concrete containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: dome, wall, basemat, ring girders, buttresses | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
301 | 103 | Containment structures | A-BWR concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 104 | Containment structures | A-BWR concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR
301 | 105 | Containment structures | A-BWR concrete containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Air - outdoor, ground water, soil | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR
301 | 106 | Containment structures | A-BWR concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 107 | Containment structures | A-BWR concrete containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): basemat, dome, wall | Concrete | Air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 108 | Containment structures | A-BWR concrete containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat, dome, wall | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 109 | Containment structures | A-BWR concrete containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat, dome, wall | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 110 | Containment structures | A-BWR concrete containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): dome, wall, basemat | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 111 | Containment structures | A-BWR concrete containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (accessible areas): basemat, dome, wall | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 112 | Containment structures | A-BWR concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, dome, reinforcing steel, wall | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR
301 | 113 | Containment structures | A-BWR concrete containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): dome, wall, basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR
301 | 114 | Containment structures | A-BWR concrete containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  |  | BWR
301 | 115 | Containment structures | A-BWR concrete containment | Loss of strength due to irradiation | Concrete: basemat, containment, wall | Concrete | Any | None - see remarks | Yes, see remarks |  | Further evaluation required if the estimated irradiation dose (neutron and gamma ray) at the time of end of plant operation (40-80 years) by analysis will reach the level that may degrade concrete strength. The radiation limits (neutron:app.1x10^20n/cm2 | BWR
301 | 116 | Containment structures | PWR steel containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | PWR
301 | 117 | Containment structures | PWR steel containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | PWR
301 | 118 | Containment structures | PWR steel containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | PWR
301 | 119 | Containment structures | PWR steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | PWR
301 | 120 | Containment structures | PWR steel containment | Cracking due to cyclic loading | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  | The steel elements are not subject to significant transients. The only tramsients are small temperature changes during operation, and associated changes in pressure | PWR
301 | 121 | Containment structures | PWR steel containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): basemat | Concrete | Air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | PWR
301 | 122 | Containment structures | PWR steel containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): basemat | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | PWR
301 | 123 | Containment structures | PWR steel containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | PWR
301 | 124 | Containment structures | PWR steel containment | Cracking and distortion due to increased stress levels from settlement | Concrete: basemat | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | PWR
301 | 125 | Containment structures | PWR steel containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): basemat | Concrete | Air - outdoor, ground water, soil | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | PWR
301 | 126 | Containment structures | PWR steel containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): basemat | Concrete | Ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | PWR
301 | 127 | Containment structures | PWR steel containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (accessible areas): basemat | Concrete | Ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | PWR
301 | 128 | Containment structures | PWR steel containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | PWR
301 | 129 | Containment structures | PWR steel containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring | No |  |  | PWR
301 | 130 | Containment structures | PWR steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | PWR
301 | 131 | Containment structures | PWR steel containment | Cracking due to cyclic loading | Steel elements (accessible area): liner, liner anchor, integral attachment | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  | The steel elements are not subject to significant transients. The only tramsients are small temperature changes during operation, and associated changes in pressure | PWR
301 | 132 | Containment structures | PWR steel containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: basemat | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | PWR
301 | 133 | Containment structures | PWR steel containment | Loss of strength due to irradiation | Concrete: basemat | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, see remarks |  | Further evaluation required if the estimated irradiation dose (neutron and gamma ray) at the time of end of plant operation (40-80 years) by analysis will reach the level that may degrade concrete strength. 6.The radiation limits (neutron:app.1x10^20n/c | PWR
301 | 134 | Containment structures | Mark I steel containment | Cumulative fatigue damage due to fatigue | Steel elements: torus, vent line, vent header, vent line bellow, downcomer | Steel, stainless steel | Air - indoor uncontrolled | None - see remarks | Yes, if TLAA (TLAA303 Cumulative Fatigue Damage of Containment Liners and Penetrations) |  |  | BWR
301 | 135 | Containment structures | Mark I steel containment | Fretting or lockup due to mechanical wear | Steel elements: drywell head, downcomer | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 136 | Containment structures | Mark I steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: torus ring girder, downcomer | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements | Yes, if corrosion is significant |  |  | BWR
301 | 137 | Containment structures | Mark I steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): drywell shell, drywell head, drywell shell in sand pocket region | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is significant |  |  | BWR
301 | 138 | Containment structures | Mark I steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: torus shell | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is significant |  |  | BWR
301 | 139 | Containment structures | Mark I steel containment | Cracking due to cyclic loading | Steel elements: torus, vent line, vent header, vent line bellow, downcomer | Steel, stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 140 | Containment structures | Mark I steel containment | Cracking due to stress corrosion cracking | Steel elements: vent line bellow | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 141 | Containment structures | Mark I steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: vent line bellow | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 142 | Containment structures | Mark II steel containment | Fretting or lockup due to mechanical wear | Steel elements: drywell head, downcomer | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 143 | Containment structures | Mark II steel containment | Cumulative fatigue damage due to fatigue | Suppression pool shell, unbraced downcomer | Dissimilar metal weld, stainless steel, steel | Air - indoor uncontrolled | None - see remarks | Yes, if TLAA (TLAA303 Cumulative Fatigue Damage of Containment Liners and Penetrations) |  |  | BWR
301 | 144 | Containment structures | Mark II steel containment | Cracking due to cyclic loading | Suppression pool shell | Dissimilar metal weld, stainless steel, steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 145 | Containment structures | Mark II steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: downcomer piping | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements | No |  |  | BWR
301 | 146 | Containment structures | Mark II steel containment | Cracking due to cyclic loading | Unbraced downcomer | Dissimilar metal weld, stainless steel, steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 147 | Containment structures | Mark II steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): suppression chamber, drywell, drywell head, embedded shell, region shielded by diaphragm floor (as applicable) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 148 | Containment structures | Mark II steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): suppression chamber, drywell, drywell head, embedded shell, region shielded by diaphragm floor (as applicable) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  |  | BWR
301 | 149 | Containment structures | Mark II steel containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
301 | 150 | Containment structures | Mark II steel containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: basemat | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
301 | 151 | Containment structures | Mark II steel containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 152 | Containment structures | Mark II steel containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): basemat | Concrete | Ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 153 | Containment structures | Mark II steel containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (accessible areas): basemat | Concrete | Ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 154 | Containment structures | Mark II steel containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 155 | Containment structures | Mark II steel containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring | No |  |  | BWR
301 | 156 | Containment structures | Mark II steel containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): basemat | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 157 | Containment structures | Mark II steel containment | Loss of strength due to irradiation | Concrete: basemat | Concrete | Any | None - see remarks | Yes, see remarks |  | Further evaluation required if the estimated irradiation dose (neutron and gamma ray) at the time of end of plant operation (40-80 years) by analysis will reach the level that may degrade concrete strength. 6.The radiation limits (neutron:app.1x10^20n/c | BWR
301 | 158 | Containment structures | Mark II steel containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): basemat | Concrete | Air - outdoor, ground water, soil | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR
301 | 159 | Containment structures | Mark II steel containment | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): basemat | Concrete | Air - outdoor, ground water, soil | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 160 | Containment structures | Mark III steel containment | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
301 | 161 | Containment structures | Mark III steel containment | Cracking due to stress corrosion cracking | Steel elements: suppression chamber shell (interior surface) | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 162 | Containment structures | Mark III steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: suppression chamber shell (interior surface) | Stainless steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 163 | Containment structures | Mark III steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (inaccessible area): drywell shell, drywell head, drywell shell | Steel | Air - indoor uncontrolled, concrete | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | Yes, if corrosion is indicated from the IWE examination |  |  | BWR
301 | 164 | Containment structures | Mark III steel containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): basemat | Concrete | Water - flowing | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 165 | Containment structures | Mark III steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements: suppression chamber shell (interior surface) | Steel | Air - indoor uncontrolled, treated water | AMP301 In-service Inspection for Containment Steel Elements | Yes, if corrosion is significant |  |  | BWR
301 | 166 | Containment structures | Mark III steel containment | Loss of material due to general, pitting, crevice corrosion | Steel elements (accessible area): drywell shell, drywell head | Steel | Air - indoor uncontrolled | AMP301 In-service Inspection for Containment Steel Elements, AMP304 Leak rate test | No |  |  | BWR
301 | 167 | Containment structures | Mark III steel containment | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): basemat | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR
301 | 168 | Containment structures | Mark III steel containment | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete: basemat, concrete fill-in annulus | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
301 | 169 | Containment structures | Mark III steel containment | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): basemat, concrete fill-in annulus | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
301 | 170 | Containment structures | Mark III steel containment | Cracking and distortion due to increased stress levels from settlement | Concrete: basemat | Concrete | Soil | AMP302 In-service Inspection for Concrete Containment, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  |  | BWR
301 | 171 | Containment structures | Mark III steel containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): basemat | Concrete | Ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 172 | Containment structures | Mark III steel containment | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (accessible areas): basemat | Concrete | Ground water, soil | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
301 | 173 | Containment structures | Mark III steel containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment | No |  |  | BWR
301 | 174 | Containment structures | Mark III steel containment | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): basemat, reinforcing steel | Concrete, steel | Air - indoor uncontrolled, air - outdoor | AMP302 In-service Inspection for Concrete Containment, AMP306 Structures Monitoring | No |  |  | BWR
301 | 175 | Containment structures | Mark III steel containment | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): basemat, concrete fill-in annulus | Concrete | Any | AMP302 In-service Inspection for Concrete Containment, AMP312 Concrete expansion | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
302 | 1 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking due to restraint shrinkage, creep and aggressive environment | Masonry walls: all | Concrete block | Air - indoor uncontrolled, air - outdoor | AMP305 Masonry Walls | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 2 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): foundation | Concrete | Air - outdoor | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR, CANDU/ PHWR, PWR
302 | 3 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete | Concrete | Air - indoor uncontrolled | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR, CANDU/ PHWR, PWR
302 | 4 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
302 | 5 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR, CANDU/ PHWR, PWR
302 | 6 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 7 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 8 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 9 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR, PWR
302 | 10 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 11 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 12 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 13 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 14 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 15 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 16 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR, CANDU/ PHWR, PWR
302 | 17 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 18 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 19 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 20 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
302 | 21 | Structures and Component Supports | Group 1 structures (BWR reactor bldg., PWR shield bldg., control room/ bldg.) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR, CANDU/ PHWR, PWR
302 | 22 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking due to restraint shrinkage, creep and aggressive environment | Masonry walls: all | Concrete block | Air - indoor uncontrolled, air - outdoor | AMP305 Masonry Walls | No |  |  | BWR
302 | 23 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): foundation | Concrete | Air - outdoor | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR
302 | 24 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete | Concrete | Air - indoor uncontrolled | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR
302 | 25 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR
302 | 26 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR
302 | 27 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
302 | 28 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR
302 | 29 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR
302 | 30 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
302 | 31 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
302 | 32 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR
302 | 33 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  |  | BWR
302 | 34 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
302 | 35 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
302 | 36 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR
302 | 37 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR
302 | 38 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
302 | 39 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
302 | 40 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | If protective coatings are relied upon to manage the effects of aging, the structures monitoring program is to include provisions to address protective coating monitoring and maintenance. | BWR
302 | 41 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
302 | 42 | Structures and Component Supports | Group 2 Structures (BWR reactor bldg. with steel superstructure) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR
302 | 43 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking due to restraint shrinkage, creep and aggressive environment | Masonry walls: all | Concrete block | Air - indoor uncontrolled, air - outdoor | AMP305 Masonry Walls | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 44 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): foundation | Concrete | Air - outdoor | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR, CANDU/ PHWR, PWR
302 | 45 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete | Concrete | Air - indoor uncontrolled | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR, CANDU/ PHWR, PWR
302 | 46 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
302 | 47 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR, CANDU/ PHWR, PWR
302 | 48 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material due to corrosion | Steel components: pile | Steel | Ground water, soil | AMP306 Structures Monitoring | No |  |  | BWR, PWR
302 | 49 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 50 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 51 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 52 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
302 | 53 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 54 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 55 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 56 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 57 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 58 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR, CANDU/ PHWR, PWR
302 | 59 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR, CANDU/ PHWR, PWR
302 | 60 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 61 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 62 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
302 | 63 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
302 | 64 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR, CANDU/ PHWR, PWR
302 | 65 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Reduction of strength and modulus due to mechanical vibration | Concrete (inaccessible areas): turbine pedestal | Concrete | Air - indoor uncontrolled | AMP306 Structures Monitoring | No | 1. ACI 349.3R 2. AESJ-SC-P005:2008 3. JNES-SS-0512-04 4. Guidelines of AIJ:2008 |  | BWR, PWR
302 | 66 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of material properties due to irradiation | Adverse localized environment, high radiation | Elastomer | Air - indoor | AMP306 Structures Monitoring | No |  |  | BWR, PWR
302 | 67 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of material properties due to thermal exposure | Seal, gasket, moisture barrier (caulking, flashing, and other sealants) | Elastomer | Air >35°C (>95°F) | AMP306 Structures Monitoring | No |  |  | BWR, PWR
302 | 68 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of material properties due to thermal exposure | Seal, gasket, moisture barrier (caulking, flashing, and other sealants) | Elastomer | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, PWR
302 | 69 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Cracking, loss of material properties due to thermal exposure | Seal, gasket, moisture barrier (caulking, flashing, and other sealants) | Elastomer | Air >35°C (>95°F) | AMP306 Structures Monitoring | No |  |  | BWR, PWR
302 | 70 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Movement or shifting due to sustained vibratory loading | Concrete: roof, wall | Water-proofing membrane | Air - outdoor | AMP306 Structures Monitoring | Yes, if signs of degradation or water leakage are present |  |  | BWR, PWR
302 | 71 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of tightness due to material degradation | Concrete (inaccessible areas): exterior above- and below- grade | Water-proofing membrane | Concrete | AMP306 Structures Monitoring | Yes, if signs of degradation or water leakage are present in below-grade concrete surfaces that are designed to be protected by waterproofing membrane |  |  | BWR, PWR
302 | 72 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of tightness due to material degradation | Concrete (inaccessible areas): under foundation | Water-proofing membrane | Ground water, soil | AMP306 Structures Monitoring | Yes, if signs of degradation or water leakage are present in below-grade concrete surfaces that are designed to be protected by waterproofing membrane |  |  | BWR, PWR
302 | 73 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of tightness due to material degradation | Caulking, flashing and other sealants on the buildings terrace | Water-proofing membrane | Air - outdoor | AMP306 Structures Monitoring | Yes, if signs of degradation or water leakage are present in below-grade concrete surfaces that are designed to be protected by waterproofing membrane |  |  | BWR, PWR
302 | 74 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of sealing function due to deterioration of gaskets, moisture barriers, seals (caulking, flashing, and other sealants) | Gasket, seal | Elastomer, rubber, other similar materials | Any | AMP306 Structures Monitoring | No |  |  | PWR
302 | 75 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Concrete expansion due to delayed ettringite formation | Concrete which has been submitted to high temperature during its early age | Concrete | Any | AMP312 Concrete Expansion Detection and Monitoring System Detection | No |  |  | PWR
302 | 76 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Increase in rigidity of antivibration seismic bearing supports due to polymer ageing | Antiseismic devices | Elastomer, rubber, other similar materials | Air - outdoor | AMP306 Structures Monitoring | No |  |  | PWR
302 | 77 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Loss of material due to corrosion of steel plates of anti-seismic bearing | Antiseismic devices | Steel | Air - outdoor | None - see remarks | Yes, perform periodic compression and shear tests on representative samples of the bearings that are exposed to same environment as the one that are located in the structure |  |  | PWR
302 | 78 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Change in dimensions due to polymer creep of elastomers | Antiseismic devices | Elastomer, rubber, other similar materials | Air - outdoor | None - see remarks | Yes, perform periodic compression and shear tests on representative samples of the bearings that are exposed to same environment as the one that are located in the structure |  | In France, periodic test is performed on samples which have been designed in oder to be representative of the real ones. The tests are tests where specimen are submitted to both compression and shear as in the actual situation. Some samples are submitted | PWR
302 | 79 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Ageing of composite material (polymer degradation) due to environment | Masonry walls reinforced with polymer material | Concrete block | Air-indoor controlled | AMP305 Masonry Walls | No |  |  | PWR
302 | 80 | Structures and Component Supports | Group 3 structures (auxiliary, diesel generator, radwaste, turbine, switchgear, AFW pumphouse, utility/piping, such as AFW pumphouse, security/lighting poles, manholes, duct banks, SBO, such as transmission towers, startup towers circuit breaker foundatio | Ageing of composite material (polymer degradation) due to environment | Chimney made of fiber reinforced polymer | Fiber reinforced polymer | Air - outdoor | AMP306 Structures Monitoring | No |  |  | PWR
303 | 1 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete | Concrete | Air - indoor uncontrolled | None - see remarks | Yes, if temperature limits are exceeded |  | Subsection CC-3400 of ASME Section III, Division 2, and Appendix A of ACI 349 specifies the concrete temperature limits for normal operation or any other long-term period. The temperatures shall not exceed 150°F except for local areas, such as around pene | BWR, CANDU/ PHWR, PWR
303 | 2 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 3 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 4 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 5 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR, CANDU/ PHWR, PWR
303 | 6 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 7 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 8 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 9 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking due to stress corrosion cracking, loss of material due to general, pitting and crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 10 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of coating integrity due to blistering, cracking, flaking, peeling, physical damage | Service level 1 coating | Coating | Air - indoor uncontrolled | AMP308 Protective Coating Monitoring and Maintenance Programme | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 11 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | If protective coatings are relied upon to manage the effects of aging, the structures monitoring program is to include provisions to address protective coating monitoring and maintenance. | BWR, CANDU/ PHWR, PWR
303 | 12 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 13 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific ag | BWR, CANDU/ PHWR, PWR
303 | 14 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding surfaces: radial beam seats in bwr drywell | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, PWR
303 | 15 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of strength due to irradiation | Concrete | Concrete | Air - indoor uncontrolled, air - outdoor | None - see remarks | Yes, see remarks |  | Further evaluation required if the estimated irradiation dose (neutron and gamma ray) at the time of end of plant operation (40-80 years) by analysis will reach the level that may degrade concrete strength. The radiation limits (neutron:app.1x10^20n/cm2 | BWR, PWR
303 | 16 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Cracking, loss of material properties due to thermal exposure | Adverse localized environment, high radiation | Elastomer | Air - indoor | AMP306 Structures Monitoring | No |  |  | BWR, PWR
303 | 17 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Tilt mechanism (differential settlement, heave effect) due to expansive soil | Concrete (inaccessible areas) | Concrete, steel | Soil (expansive clays) | AMP310 Ground Movement Surveillance | Yes, if TLAA (TLAA304 Foundation Settlement due to Soil Movement) |  |  | BWR, PWR
303 | 18 | Structures and Component Supports | Group 4 structures (containment internal structure, excluding refueling canal) | Loss of sealing function due to deterioration of gaskets, moisture barriers, seals (caulking, flashing, and other sealants) | Seal, gasket, moisture barrier (caulking, flashing, other sealants) | Elastomer (such as epdm rubber) | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | PWR
303 | 19 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking due to restraint shrinkage, creep and aggressive environment | Masonry walls: all | Concrete block | Air - indoor uncontrolled, air - outdoor | AMP305 Masonry Walls | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 20 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking due to stress corrosion cracking | Steel components: fuel pool liner | Stainless steel | Treated water, treated borated water | AMP103 Water Chemistry | No, unless leakages have been detected through the SFP liner that cannot be accounted for from the leak chase channels |  |  | BWR, PWR
303 | 21 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to general, pitting, crevice corrosion | Steel components: fuel pool liner | Stainless steel | Treated water, treated borated water | AMP103 Water Chemistry | No, unless leakages have been detected through the SFP liner that cannot be accounted for from the leak chase channels |  |  | BWR, PWR
303 | 22 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): foundation | Concrete | Air - outdoor | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR, CANDU/ PHWR, PWR
303 | 23 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Reduction of strength and modulus due to elevated temperature (>65°C general, >90°C local) | Concrete | Concrete | Air - indoor uncontrolled | None - see remarks | Yes, if temperature limits are exceeded |  | Plant-specific aging management program shall be developed to identify the reduction of strength and modulus of elasticity for any portions of Concrete Containment that exceeds 65°C except for local areas, such as around penetrations, which exceeds 90°C. | BWR, CANDU/ PHWR, PWR
303 | 24 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 25 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR, CANDU/ PHWR, PWR
303 | 26 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 27 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 28 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 29 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 30 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR, CANDU/ PHWR, PWR
303 | 31 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 32 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR, CANDU/ PHWR, PWR
303 | 33 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 34 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 35 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR, CANDU/ PHWR, PWR
303 | 36 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 37 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 38 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 39 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | If protective coatings are relied upon to manage the effects of aging, the structures monitoring program is to include provisions to address protective coating monitoring and maintenance. | BWR, CANDU/ PHWR, PWR
303 | 40 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 41 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Masonry walls: all | Concrete block | Air - outdoor | AMP305 Masonry Walls | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 42 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific ag | BWR, CANDU/ PHWR, PWR
303 | 43 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of tightness due to material degradation | Concrete: roof, wall | Water-proofing membrane | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, PWR
303 | 44 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of tightness due to material degradation | Concrete (inaccessible areas): exterior above- and below- grade | Water-proofing membrane | Concrete | AMP306 Structures Monitoring | No |  |  | BWR, PWR
303 | 45 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of tightness due to material degradation | Caulking, flashing and other sealants on the buildings terrace | Water-proofing membrane | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, PWR
303 | 46 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Welding defect propagation due to environment | Steel components: fuel pool liner | Stainless steel | Treated water, treated borated water | AMP306 Structures Monitoring | Yes, see remarks |  | If leakage is detected thru the concrete walls or floor, source of water leakage should be found and stopped | PWR
303 | 47 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to general, pitting, crevice corrosion | Steel components: fuel pool liner | Stainless steel | Treated water, treated borated water | AMP306 Structures Monitoring | Yes, see remarks |  | If leakage is detected thru the concrete walls or floor, source of water leakage should be found and stopped | PWR
303 | 48 | Structures and Component Supports | Group 5 Structures (fuel storage facility, refueling canal) | Loss of material due to general, pitting, crevice corrosion | Concrete (accessible areas): interior and above-grade exterior | Concrete, steel | Treated water, treated borated water | AMP306 Structures Monitoring | No |  |  | PWR
303 | 49 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking due to restraint shrinkage, creep and aggressive environment | Masonry walls: all | Concrete block | Air - indoor uncontrolled, air - outdoor | AMP305 Masonry Walls | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 50 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to abrasion, cavitation | Concrete: exterior above- and below-grade, foundation, interior slab | Concrete | Water - flowing | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 51 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material, loss of form due to currents, erosion, salt crystallization, frost action, sedimentation, seepage, settlement, surface runoff, waves | Earthen water-control structures: canal, channel, dam, embankment, pond, reservoir | Various | Water - flowing or standing | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 52 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): all, concrete exposed to: chlorides, carbon dioxid | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 53 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): all | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP307 Water-control Structures, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR, CANDU/ PHWR, PWR
303 | 54 | Structures and Component Supports | Group 6 structures (water-control structure) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation, interior slab | Concrete | Water - flowing | None - see remarks AMP307 Water-control Structures | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific | BWR, CANDU/ PHWR, PWR
303 | 55 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): exterior above- and below-grade, foundation, interior slab | Concrete | Air - outdoor | None - see remarks AMP307 Water-control Structures | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR, CANDU/ PHWR, PWR
303 | 56 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System, AMP307 Water-control Structures | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 57 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled, air - outdoor, water - flowing or standing | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 58 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material, changes in material properties due to weathering, chemical degradation, insect infestation, repeated wetting and drying, fungal decay | Wooden pile, sheeting | Wood | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, PWR
303 | 59 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring, AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 60 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring, AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 61 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance, AMP307 Water-control Structures | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 62 | Structures and Component Supports | Group 6 structures (water-control structure) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance, AMP307 Water-control Structures | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 63 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 64 | Structures and Component Supports | Group 6 structures (water-control structure) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation, interior slab | Concrete | Water - flowing | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 65 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): all | Concrete | Air - indoor uncontrolled, air - outdoor, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 66 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of sealing function due to deterioration of gaskets, moisture barriers, seals (caulking, flashing, and other sealants) | Seal, gasket, moisture barrier (caulking, flashing, and other sealants) | Elastomer (such as epdm rubber) | Various | AMP306 Structures Monitoring, AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 67 | Structures and Component Supports | Group 6 structures (water-control structure) | Cracking, loss of material properties due to thermal exposure | Seal, gasket, moisture barrier (caulking, flashing, and other sealants) | Elastomer | Air - outdoor | AMP306 Structures Monitoring, AMP307 Water-control Structures | No |  |  | BWR, PWR
303 | 68 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to soil erosion | Earthen water-control structures: canal, channel, dam, embankment, pond, reservoir | Earth | Ground water, soil | AMP307 Water-control Structures | No |  |  | PWR
303 | 69 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to general, pitting, crevice corrosion | Sheet pile | Steel | Ground water, soil | AMP307 Water-control Structures | No |  |  | PWR
303 | 70 | Structures and Component Supports | Group 6 structures (water-control structure) | Silting up of intake canal due to deposit of sediment material | Earthen water-control structures: canal, channel, dam, embankment, pond, reservoir | Earth | Ground water, soil | AMP307 Water-control Structures | No |  |  | PWR
303 | 71 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to soil erosion | River spillway that guarantee minimum water level for intake | Concrete, rock | Ground water, soil | AMP307 Water-control Structures | No |  |  | PWR
303 | 72 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to abrasion, cavitation | Concrete piping gallery, tunnel, river spillway | Concrete | Water - flowing | AMP307 Water-control Structures | No |  |  | PWR
303 | 73 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to corrosion | Prestressed cable and rod of retaining wall | Steel | Water - flowing | AMP307 Water-control Structures | No |  |  | PWR
303 | 74 | Structures and Component Supports | Group 6 structures (water-control structure) | Expansion and cracking due to sulphate attack | footings, foundation walls, retaining walls, piers, culverts and piles. The most severe attack occurs on elements where one side is exposed to sulphate solutions and evaporation can take place at the other. | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures, and AMP XXX | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 75 | Structures and Component Supports | Group 6 structures (water-control structure) | Delamination due to sulphate attack | footings, foundation walls, retaining walls, piers, culverts and piles. The most severe attack occurs on elements where one side is exposed to sulphate solutions and evaporation can take place at the other. | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures, and AMP XXX | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 76 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of strength due to sulphate attack | footings, foundation walls, retaining walls, piers, culverts and piles. The most severe attack occurs on elements where one side is exposed to sulphate solutions and evaporation can take place at the other. | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures, and AMP XXX | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 77 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of bond due to corrosion (iron oxide) of embedded steel (without spalling, scaling and loss of concrete material), corrodents on concrete surface | Concrete: submerged zone with turbulence, geometric changes | Steel | Water - flowing | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 78 | Structures and Component Supports | Group 6 structures (water-control structure) | Loss of material due to corrosion (iron oxide) of embedded steel (without spalling, scaling and loss of concrete material), corrodents on concrete surface | Concrete: submerged zone with turbulence, geometric changes | Steel | Water - flowing | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 79 | Structures and Component Supports | Group 6 structures (water-control structure) | Erosion due to biological attack | Concrete in contact with lichens, mosses, algae, roots of plants and trees, marine molluscs, sponges, soil, water, sewage, as well as food, agricultural products and waste materials | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 80 | Structures and Component Supports | Group 6 structures (water-control structure) | Increase in porosity due to biological attack | Concrete in contact with lichens, mosses, algae, roots of plants and trees, marine molluscs, sponges, soil, water, sewage, as well as food, agricultural products and waste materials | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 81 | Structures and Component Supports | Group 6 structures (water-control structure) | Increasing transport of degrading materials due to biological attack | Concrete in contact with lichens, mosses, algae, roots of plants and trees, marine molluscs, sponges, soil, water, sewage, as well as food, agricultural products and waste materials | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 82 | Structures and Component Supports | Group 6 structures (water-control structure) | Spalling due to biological attack | Concrete in contact with lichens, mosses, algae, roots of plants and trees, marine molluscs, sponges, soil, water, sewage, as well as food, agricultural products and waste materials | Concrete | Air - outdoor, water - flowing or standing, ground water, soil | AMP307 Water-control Structures | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 83 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR, CANDU/ PHWR, PWR
303 | 84 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 85 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 86 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 87 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 88 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR, CANDU/ PHWR, PWR
303 | 89 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 90 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR, CANDU/ PHWR, PWR
303 | 91 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 92 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 93 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR, CANDU/ PHWR, PWR
303 | 94 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 95 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 96 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 97 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | If protective coatings are relied upon to manage the effects of aging, the structures monitoring program is to include provisions to address protective coating monitoring and maintenance. | BWR, CANDU/ PHWR, PWR
303 | 98 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 99 | Structures and Component Supports | Group 7 structures (concrete tank and missile barrier) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific ag | BWR, CANDU/ PHWR, PWR
303 | 100 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking due to stress corrosion cracking | Steel components: tank liner | Stainless steel | Water - standing | None - see remarks | Yes, if plant- specific AMP |  | A plant-specific aging management program is to be evaluated. | BWR, CANDU/ PHWR, PWR
303 | 101 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | Steel components: tank liner | Stainless steel | Water - standing | None - see remarks | Yes, if plant- specific AMP |  | A plant-specific aging management program is to be evaluated. | BWR, CANDU/ PHWR, PWR
303 | 102 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): foundation | Concrete | Air - outdoor | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR, CANDU/ PHWR, PWR
303 | 103 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 104 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR, CANDU/ PHWR, PWR
303 | 105 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 106 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 107 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 108 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR, CANDU/ PHWR, PWR
303 | 109 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 110 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR, CANDU/ PHWR, PWR
303 | 111 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
303 | 112 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR, CANDU/ PHWR, PWR
303 | 113 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 114 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 115 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
303 | 116 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Loss of material due to corrosion | Steel components: all structural steel | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | If protective coatings are relied upon to manage the effects of aging, the structures monitoring program is to include provisions to address protective coating monitoring and maintenance. | BWR, CANDU/ PHWR, PWR
303 | 117 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR, CANDU/ PHWR, PWR
303 | 118 | Structures and Component Supports | Group 8 structures (steel tank and missile barrier) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific ag | BWR, CANDU/ PHWR, PWR
303 | 119 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (inaccessible areas): foundation | Concrete | Air - outdoor | None - see remarks | Yes, for plants located in moderate to severe weathering conditions | ASTM C33/C33M-11a, Figure 1 Architectural Institute of Japan: Construction Work Standard Specifications and Explanations: JASS5 Reinforced Concrete Work 2003 (AIJ) Figure 26.1 (Distribution Map of Degrees of Freezing Damage) | Severe exposure is defined as the cases in which concrete may be in almost continuous contact with moisture prior to freezing, or where deicing salts are used. Moderate exposure, on the other hand, is where concrete will be only occasionally exposed to mo | BWR
303 | 120 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking due to expansion from reaction with aggregates | Concrete (inaccessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Plant specific aging management program may be required in accordance AMP 312. | BWR
303 | 121 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | An evaluation of a location, which is not accessible, should be included in the evaluation of the location subject to the severest condition of accessible areas. Examination frequency to be agreed upon by the licensee and regulatory authority | BWR
303 | 122 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Loss of material (spalling, scaling) and cracking due to freeze-thaw | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
303 | 123 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (accessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | AMP306 Structures Monitoring | No |  |  | BWR
303 | 124 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR
303 | 125 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking due to expansion from reaction with aggregates | Concrete (accessible areas): all | Concrete | Any | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | Yes, see remarks |  | Plant specific aging management program may be required in accordance AMP 312. | BWR
303 | 126 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): interior and above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR
303 | 127 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR
303 | 128 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking, loss of bond, loss of material (spalling, scaling) due to corrosion of embedded steel | Concrete (accessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring | No |  | Carbonation depth at 60 years normally less than concrete cover to rebars. Therefore, unless there is evidence of cracking or corrosion, additional testing or analysis is not required. However, some member states require tests to be performed to determi | BWR
303 | 129 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR
303 | 130 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete: interior, above-grade exterior | Concrete | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR
303 | 131 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking, increase in porosity and permeability, loss of material (spalling, scaling) due to aggressive chemical attack | Concrete (inaccessible areas): below-grade exterior, foundation | Concrete | Ground water, soil | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  | An evaluation of a location which is not accessible should be substituted with the evaluation for the severest condition of accessible areas. | BWR
303 | 132 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking and distortion due to increased stress levels from settlement | Concrete | Concrete | Soil | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement |  | If a de-watering system is relied upon for control of settlement, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
303 | 133 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR
303 | 134 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR
303 | 135 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Reduction in foundation strength, cracking due to differential settlement, erosion of porous concrete subfoundation | Concrete: foundation, subfoundation | Concrete, porous concrete | Water - flowing under foundation | AMP306 Structures Monitoring, AMP310 Ground Movement Surveillance | Yes, if a de-watering system is relied upon to control settlement, TLAA304 Foundation Settlement due to Soil Movement |  | If a de-watering system is relied upon for control of erosion of cement from porous concrete subfoundations, then the licensee is to ensure proper functioning of the de-watering system through the period of extended operation. | BWR
303 | 136 | Structures and Component Supports | Group 9 Structures (BWR unit vent stack) | Increase in porosity and permeability, loss of strength due to leaching of calcium hydroxide and carbonation | Concrete (inaccessible areas): exterior above- and below-grade, foundation | Concrete | Water - flowing | None - see remarks | Yes, if leaching is observed in accessible areas that impact intended function |  | Further evaluation is required to determine if a plant-specific aging management program is needed to manage increase in porosity, and permeability due to leaching of calcium hydroxide and carbonation of concrete in Inaccessible Areas. A plant-specific ag | BWR
304 | 1 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, PWR
304 | 2 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 3 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 4 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 5 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, PWR
304 | 6 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 7 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 8 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 9 | Structures and Component Supports | Anchorage of racks, panels, cabinets, and enclosures for electrical equipment and instrumentation | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 10 | Structures and Component Supports | Support for piping and components | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 11 | Structures and Component Supports | Support for piping and components | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion | No |  |  | BWR, PWR
304 | 12 | Structures and Component Supports | Support for piping and components | Cumulative fatigue damage due to fatigue | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled | None - see remarks | Yes, if TLAA (TLAA303 Cumulative Fatigue Damage of Containment Liners and Penetrations) |  |  | BWR, CANDU/ PHWR, PWR
304 | 13 | Structures and Component Supports | Support for piping and components | Loss of mechanical function due to corrosion, dirt, distortion, overload | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 14 | Structures and Component Supports | Support for piping and components | Fatigue due to vibratory and cyclic thermal loads | Constant and variable load spring hanger, guide, stop | Steel | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 15 | Structures and Component Supports | Support for piping and components | Reduction or loss of isolation function due to humidity, radiation hardening, sustained vibratory loading, temperature | Vibration isolation element | Non-metallic (e.g. rubber) | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 16 | Structures and Component Supports | Support for piping and components | Loss of material due to general (steel only) pitting and crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel, stainless steel | Treated water <60°C (<140°F) | AMP103 Water Chemistry, AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 17 | Structures and Component Supports | Support for piping and components | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 18 | Structures and Component Supports | Support for piping and components | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 19 | Structures and Component Supports | Support for piping and components | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Stainless steel | Treated water | AMP103 Water Chemistry, AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 20 | Structures and Component Supports | Support for piping and components | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 21 | Structures and Component Supports | Support for piping and components | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP303 Safety Class 1, 2, and 3 piping and Metal Containment Components Supports | No |  |  | BWR, PWR
304 | 22 | Structures and Component Supports | Support for piping and components | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 23 | Structures and Component Supports | Support for piping and components | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 24 | Structures and Component Supports | Support for piping and components | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 25 | Structures and Component Supports | Support for piping and components | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding surfaces | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 26 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP306 Structures Monitoring | No |  |  | BWR, PWR
304 | 27 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 28 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 29 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 30 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP306 Structures Monitoring | No |  |  | BWR, PWR
304 | 31 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
304 | 32 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
304 | 33 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 34 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 35 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding support bearing, sliding support surface | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 36 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding support bearing, sliding support surface | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 37 | Structures and Component Supports | Support for cable tray, conduit, HVAC duct, tube track, instrument tubing and piping and components | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum, stainless steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 38 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP306 Structures Monitoring | No |  |  | BWR, PWR
304 | 39 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 40 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components, and other miscellaneous mechanical equipment | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 41 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 42 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP306 Structures Monitoring | No |  |  | BWR, PWR
304 | 43 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Cracking due to stress corrosion cracking | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
304 | 44 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR
304 | 45 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 46 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 47 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Reduction or loss of isolation function due to humidity, radiation hardening, sustained vibratory loading, temperature | Vibration isolation element | Non-metallic (e.g. rubber) | Air - indoor uncontrolled, air - outdoor | AMP303 Safety Class 1, 2 and 3 Piping and Metal Containment Components Supports | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 48 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding support bearing, sliding support surface | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 49 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of mechanical function due to corrosion, debris, dirt, distortion, overload, wear | Sliding support bearing, sliding support surface | Lubrite®, graphitic tool steel, fluorogold, lubrofluor | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 50 | Structures and Component Supports | Support for emergency diesel generator (EDG), HVAC system components and other miscellaneous mechanical equipment | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum, stainless steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 51 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP306 Structures Monitoring | No |  |  | BWR, PWR
304 | 52 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel | Air - indoor uncontrolled | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 53 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of preload due to self-loosening | Structural bolting | Any | Any | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 54 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to general, pitting, crevice corrosion | Structural bolting | Steel, galvanized steel | Air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 55 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to boric acid corrosion | Support member, weld, bolted connection, support anchorage to building structure | Galvanized steel, aluminum | Air with borated water leakage | AMP110 PWR Boric Acid Corrosion, AMP306 Structures Monitoring | No |  |  | BWR, PWR
304 | 56 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Reduction in concrete anchor capacity due to local concrete degradation, service-induced cracking or other concrete aging mechanisms | Building concrete at locations of expansion and grouted anchors, grout pads for support base plates | Concrete, grout | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring, AMP312 Concrete Expansion Detection and Monitoring System | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 57 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Loss of material due to general, pitting, crevice corrosion | Support member, weld, bolted connection, support anchorage to building structure | Steel | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  |  | BWR, CANDU/ PHWR, PWR
304 | 58 | Structures and Component Supports | Support for platform, pipe whip restraint, jet impingement shield, masonry walls and other miscellaneous structures | Cracking due to stress corrosion cracking, loss of material due to general, pitting and crevice corrosion | High-strength structural bolting | Low alloy steel, actual measured yield strength ≥ 1,034 MPa | Air - indoor uncontrolled, air - outdoor | AMP306 Structures Monitoring | No |  | ASTM A 325, F 1852, and ASTM A 490 bolts used in civil structures have not shown to be prone to SCC. SCC potential need not be evaluated for these bolts. | BWR, CANDU/ PHWR, PWR

## sheet1
Table number | IGALL number | Systems | Structure/ component | Ageing effect/ degradation mechanism | Critical location/ part | Material | Environment | Ageing Management Programme (AMP) | Further Action | References | Remarks | Design
101 | 1 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Class 1 piping, piping components and piping elements | Stainless steel and steel with austenitic cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 2 | Reactor pressure vessel, internals, reactor coolant system | Pump, valve | Loss of fracture toughness due to thermal ageing | Class 1 pump casings, valve bodies and bonnets | Cast austenitic stainless steel | Reactor coolant >250°C (>482°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP112 Thermal Ageing Embrittlement of Cast Austenitic Stainless Steel, AMP153 WWER Main Gate Valve, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA110 Thermal Ageing of Cast Austenitic Stainless Steels) |  |  | PWR
101 | 3 | Reactor pressure vessel, internals, reactor coolant system | Pump, valve | Cracking due to stress corrosion cracking | Class 1 pump casings, valve bodies | Steel with stainless steel cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP138 Reactor Coolant Pump, AMP153 WWER Main Gate Valve | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 4 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Closure bolting | High-strength, low alloy steel, stainless steel | Air with reactor coolant leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP115 Bolting Integrity | No |  |  | PWR
101 | 9 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to cyclic loading | Pressurizer: integral support | Steel, stainless steel | Air with metal temperature up to 288°C (550°F) | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 10 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer heater sheath and sleeve, heater bundle diaphragm plate | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 12 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer components | Steel with stainless steel or nickel-alloy cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 13 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Reactor coolant system piping and fittings: cold leg, hot leg, surge line, spray line | Steel with stainless steel cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP153 WWER Main Gate Valve | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 15 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to cyclic loading | Reactor coolant system piping and fittings: cold leg, hot leg, surge line, spray line | Steel with stainless steel cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 16 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to cyclic loading | Pressurizer components | Steel with stainless steel or nickel-alloy cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 18 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer surge and steam space nozzle, weld | Nickel alloy, Steel with stainless steel cladding | Reactor coolant, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 19 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Nickel alloy | Reactor coolant, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 25 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer relief tank: tank shell and head, flange, nozzle | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 26 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking (for stainless steel only), mechanical, thermal, vibratory loading | Class 1 piping, fittings and branch connections < 100mm (4 inch) | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP121 One-Time Inspection of Class 1 Small-bore piping | No |  |  | PWR
101 | 27 | Reactor pressure vessel, internals, reactor coolant system | Main circulation loop/ piping | Cracking due to stress corrosion cracking | Class 1 piping, piping components and piping elements | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 28 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer instrumentation penetration, heater sheath and sleeve, heater bundle diaphragm plate, manway and flange | Nickel alloy, nickel-alloy cladding, Steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 30 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to stress corrosion cracking | Pressurizer relief tank: tank shell and head, flange, nozzle | Stainless steel, steel with stainless steel cladding | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
101 | 36 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Closure head: vessel flange leak detection line | Stainless steel | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, a plant-specific ageing management programme | Yes, if plant- specific AMP |  | A plant-specific ageing management programme to mitigate or detect cracking | PWR
101 | 43 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Crack growth due to cyclic loading | Vessel shell: upper shell, intermediate shell, lower shell (including beltline weld) | Low alloy steel SA508-Cl 2 forgings clad (with stainless steel) using a high-heat-input welding process | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | Yes, if TLAA (TLAA115 Fatigue and Thermal Ageing Analysis of Manufacturing Flaws) |  |  | PWR
101 | 44 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to wear | Vessel shell: vessel flange | Steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 45 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Penetration: head vent piping (top head), instrument tube (top head) | Nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 46 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Bottom-mounted instrument guide tube (external to bottom head) | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, a plant-specific ageing management programme | Yes, if plant- specific AMP |  |  | PWR
101 | 47 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Control rod drive head penetration: nozzle weld | Nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 48 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Nozzle safe end and weld: inlet, outlet, safety injection | Stainless steel, nickel alloy weld or buttering | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 49 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of material due to pitting, crevice corrosion | Flange, head weld, nozzle, penetration, pressure housing, safe end, vessel shell | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  |  | PWR
101 | 54 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Control rod drive head penetration: pressure housing | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 55 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Core guide lugs, core support pads | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 56 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Cracking due to stress corrosion cracking | Penetration: instrument tube (bottom head) | Nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 97 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Cracking due to stress corrosion cracking or other mechanism(s) | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 98 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Babcock and Wilcox | Loss of material due to wear | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 157 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Cracking due to stress corrosion cracking or other mechanism(s) | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 158 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Combustion Engineering | Loss of material due to wear | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 219 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Cracking due to stress corrosion cracking or other mechanism(s) | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 220 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) - Westinghouse | Loss of material due to wear | Reactor pressure vessel internals: core support structure | Stainless steel, nickel alloy, cast austenitic stainless steel | Reactor coolant and neutron flux | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 227 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Loss of material due to erosion | Secondary manway cover, handhole cover | Steel | Air with leaking secondary-side water and/ or steam | AMP102 In-service Inspection/ Periodic Inspection for Class 2 components | No |  |  | PWR
101 | 229 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Steam generator components: secondary side nozzle (vent, drain, and instrumentation) | Nickel alloy | Secondary feed water, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection, AMP 116 Steam Generators | No |  |  | PWR
101 | 240 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Instrument penetration and primary side nozzle, safe end, weld | Steel with nickel-alloy cladding, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection for Class 1 components, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components, AMP 116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 242 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (once-through) | Cracking due to stress corrosion cracking | Primary side components: upper and lower head and tube sheet weld exposed to reactor coolant | Steel with stainless steel or nickel-alloy cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection for Class 1 components, AMP103 Water Chemistry, AMP 116 Steam Generators | No |  |  | PWR
101 | 262 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Steam generator: primary nozzle, nozzle to safe end weld, manway, flange | Stainless steel, steel with stainless steel cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP116 Steam Generators | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 264 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Instrument penetration and primary side nozzle, safe end, weld | Steel with nickel-alloy cladding, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP111 PWR Cracking of Nickel-Alloy Reactor Coolant Pressure Boundary Components | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 265 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Cracking due to stress corrosion cracking | Primary side components: divider plate | Steel with nickel-alloy cladding, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP116 Steam Generators | Yes, detection of ageing effects is to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | Supplemental examination (Alloy 600 only) | PWR
101 | 266 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (recirculating) | Loss of material due to general, pitting, crevice corrosion | Steam generator components: upper and lower shell, transition cone, new transition cone closure weld | Steel | Secondary feed water, steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP116 Steam Generators | No |  |  | PWR
101 | 274 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant system piping (PWR) | Loss of fracture toughness due to thermal ageing | Cold leg, crossover leg, hot leg | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 276 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cumulative fatigue damage due to fatigue | RCS pump flywheel | Steel | Air | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA112 Main Circulation Pump Flywheel) |  |  | PWR
101 | 280 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (PWR) | Cracking due to stress corrosion cracking | Lower core plate, lower internal assembly, lower support plate, lower support plate column, fuel alignment pin | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP113 PWR Vessel Internals | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 281 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (PWR) | Loss of fracture toughness due to thermal ageing | Control rod drive head penetration: pressure housing | Stainless steel | Reactor coolant >250°C (>482°F) | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
101 | 284 | Reactor pressure vessel, internals, reactor coolant system | Steam generator (PWR) | Loss of material due to wear | Primary side tube, tube plug | Stainless steel, steel with stainless steel cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP116 Steam Generators | No |  |  | PWR
101 | 293 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to erosion | Pump casing, weld | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 294 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Pump casing, weld | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 295 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Pressure cover | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 296 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Pressure cover | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 297 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to erosion | Nozzle | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 298 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to fatigue | Environments of the flanged joints of the main plane of split | Austenitic steel, Ni sealing ring, high-strength steel bolt and screw | Air with borated water leakage | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 299 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Environments of the flanged joints of the main plane of split | Austenitic steel, Ni sealing ring, high-strength steel bolt and screw | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
101 | 300 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Environments of the flanged joints of the main plane of split | Austenitic steel, Ni sealing ring, high-strength steel bolt and screw | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 301 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to fatigue | Sealing surface of the main flange | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | PWR
101 | 302 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Sealing surface of the main flange | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 303 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to wear | Sealing surface of the main flange | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 304 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Driving wheel | Cast austenitic stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 305 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to erosion | Driving wheel | Cast austenitic stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 306 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Cracking due to stress corrosion cracking | Components of the sealing-block casing | Austenitic steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 307 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to corrosion | Supporting frame, support holding | Steel | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
101 | 308 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pump (PWR) | Loss of material due to boric acid corrosion | Supporting frame, support holding | Steel | Air with borated water leakage | AMP102 In-service Inspection/ Periodic Inspection, AMP138 Reactor Coolant Pump | No |  |  | PWR
102 | 2 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Isolation condenser components | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | Yes, detection of ageing effects is to be evaluated, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 6 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to cyclic loading | Isolation condenser components | Steel, stainless steel | Reactor coolant | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | BWR
102 | 9 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of material due to pitting, crevice corrosion | Reactor coolant pressure boundary component | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
102 | 10 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, cyclic loading | Class 1 piping, fittings and branch connections < 100mm (4 inch) | Steel, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP121 One-Time Inspection of Class 1 Small-bore piping | No |  | ISI depending on national requirements | BWR
102 | 11 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking (for stainless steel only), mechanical, thermal, vibratory loading | Isolation condenser components | Steel, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | Checking the condition of ageing degradation with visual inspection or something during regular dismantling inspection is required. | BWR
102 | 14 | Reactor pressure vessel, internals, reactor coolant system | Reactor coolant pressure boundary (BWR) | Loss of preload due to thermal effects, gasket creep, self-loosening | Pump and valve closure bolting | Steel, stainless steel | System temperature up to 288°C (550°F) | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
102 | 15 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel components: flange, nozzle, penetration, safe end, thermal sleeve, vessel shell, head, weld | Steel with or without nickel-alloy or stainless steel cladding, stainless steel, nickel alloy | Reactor coolant | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  | Fatigue is a TLAA evaluated and for Class 1 components environmental effects on fatigue are to be addressed according to national requirements. | BWR
102 | 20 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking Cracking due to cyclic loading | Nozzle: control rod drive return line | Steel with or without stainless steel cladding | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP123 BWR Control Rod Drive Return Line Nozzle | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | ISI e.g. VT, UT | BWR
102 | 23 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Pressure vessel support skirt and attachment weld | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage and/or TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | In many cases the inspection here is very restricted | BWR
102 | 24 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel: flange, nozzle, penetration, safe end, vessel shell, head, weld | Steel with stainless steel or nickel-alloy cladding, stainless steel, nickel alloy | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  |  | BWR
102 | 25 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of material due to pitting, crevice corrosion | Top head enclosure: closure stud, nut | High-strength, low alloy steel | Air with reactor coolant leakage | AMP102 In-service Inspection/ Periodic Inspection | No |  | ISI - PT, ET | BWR
102 | 26 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of material due to general, pitting, crevice corrosion, wear | Top head enclosure: closure stud, nut | High-strength, low alloy steel | Air with reactor coolant leakage | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
102 | 28 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking, cyclic loading | Penetration: control rod drive stub tube, in core monitor housing, jet pump instrument, standby liquid control, flux monitor vessel instrumentation penetrations, control rod drive housing (CRDH) and incore-monitoring housing (ICMH) penetrations and standby liquid control (SLC) nozzles/Core ΔP nozzles | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP108 BWR Penetrations | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  | No safety issue , see IAEA Techdoc 1470 VT may be performed during hydro- of pressure test, ISI - VT | BWR
102 | 29 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Loss of fracture toughness due to neutron irradiation embrittlement | Penetration: drain line | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  |  | BWR
102 | 30 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel (BWR) | Cracking due to stress corrosion cracking, intergranular stress corrosion cracking | Top head enclosure (without cladding): top head, nozzle (vent, top head spray or RCIC and spare) | Steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP119 One-Time Inspection | No |  | ISI - PT, VT | BWR
102 | 36 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Cumulative fatigue damage due to fatigue | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage, TLAA106 Environmentally Assisted Fatigue) |  | A TLAA is not mandatory because only a few location will undergo fatigue. GE design: Special attention should be drawn to the jet pump braces. Fatigue is a TLAA evaluated and for Class 1 components environmental effects on fatigue are to be addressed acco | BWR
102 | 50 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of fracture toughness due to neutron irradiation and thermal ageing | Reactor pressure vessel internal components | Nickel alloy, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry | No |  | ISI - VT | BWR
102 | 51 | Reactor pressure vessel, internals, reactor coolant system | Reactor pressure vessel internals (BWR) | Loss of material due to wear | Reactor pressure vessel internals components: jet pump wedge surface | Stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection | No |  | ISI - VT | BWR
104 | 87 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to cyclic loading | High-pressure pump, casing | Stainless steel | Treated borated water | AMP102 In-service Inspection/ Periodic Inspection | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR
104 | 89 | Auxiliary systems | Chemical and volume control system (PWR) | Cracking due to cyclic loading | Heat exchanger components and tubes | Stainless steel | Treated borated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection | No |  |  | PWR
104 | 209 | Steam and power conversion system | Main steam system (PWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | PWR
105 | 8 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 9 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Stainless steel | Treated water | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 10 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 11 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Regenerative heat exchanger components | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 29 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 40 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Steel | Air - indoor uncontrolled | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 41 | Auxiliary systems | Reactor water cleanup system (BWR) | Cumulative fatigue damage due to fatigue | Piping, piping component, piping element | Stainless steel | Treated water | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection | Yes, if TLAA (TLAA101 Low-Cycle Fatigue Usage) |  |  | BWR
105 | 42 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Heat exchanger components | Stainless steel, steel with stainless steel cladding | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 43 | Auxiliary systems | Reactor water cleanup system (BWR) | Cracking due to stress corrosion cracking | Regenerative heat exchanger components | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
105 | 62 | Steam and power conversion system | Main steam system (BWR) | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR
108 | 14 | Engineered safety features | Containment isolation components | Loss of material due to general, pitting, crevice corrosion | Containment isolation piping and components (internal surfaces) | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 62 | Auxiliary systems | Overhead heavy load and light load (related to refueling) handling systems | Cumulative fatigue damage due to fatigue | Crane: structural girder | Steel | Air - indoor uncontrolled (external), Air - Outdoor | AMP101 Fatigue Monitoring, AMP102 In-service Inspection/ Periodic Inspection, AMP127 Inspection of Overhead Heavy Load And Light Load (Related To Refueling) Handling Systems A plant-specific ageing management programme | Yes, if TLAA (TLAA108 Fatigue of Cranes) |  |  | BWR, CANDU/ PHWR, PWR
108 | 141 | Auxiliary systems | Closed-cycle cooling water system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  | See ID No.17 | BWR, CANDU/ PHWR, PWR
108 | 330 | Auxiliary systems | Emergency diesel generator system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 396 | Auxiliary systems | Steam turbine system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Copper alloy | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 399 | Steam and power conversion system | Steam turbine system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 405 | Steam and power conversion system | Steam turbine system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 409 | Steam and power conversion system | Steam turbine system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 413 | Steam and power conversion system | Extraction steam system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Steam | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 414 | Steam and power conversion system | Extraction steam system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 415 | Steam and power conversion system | Extraction steam system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 416 | Steam and power conversion system | Extraction steam system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 422 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Copper alloy | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 446 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice corrosion | Piping, piping component, piping element | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 447 | Steam and power conversion system | Condensate system | Loss of material due to general (steel only) pitting and crevice corrosion | Tank（internal surface) | Steel, stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 448 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice, galvanic corrosion | Heat exchanger components | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 449 | Steam and power conversion system | Condensate system | Loss of material due to general, pitting, crevice corrosion | PWR heat exchanger components | Steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 451 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Heat exchanger components and tubes | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 452 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | PWR heat exchanger components | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 453 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 454 | Steam and power conversion system | Condensate system | Cracking due to stress corrosion cracking | Piping, piping component, piping element | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 455 | Steam and power conversion system | Condensate system | Loss of material due to pitting, crevice corrosion | Piping, piping component, piping element | Aluminum | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 460 | Steam and power conversion system | Condensate system | Reduction of heat transfer due to fouling | Heat exchanger tube | Stainless steel | Treated water | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR
108 | 461 | Steam and power conversion system | Condensate system | Cracking due to stress corrosion cracking | Tank（internal surface) | Stainless steel | Treated water >60°C (>140°F) | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP119 One-Time Inspection | No |  |  | BWR, CANDU/ PHWR, PWR

## AMP102
Table number | IGALL number | Systems | Structure/ component | Ageing effect/ degradation mechanism | Critical location/ part | Material | Environment | Ageing Management Programme (AMP) | Further Action | References | Remarks | Design
101 | 16 | Reactor pressure vessel, internals, reactor coolant system | Pressurizer | Cracking due to fatigue | Pressurizer components | Steel with stainless steel or nickel-alloy cladding, stainless steel | Reactor coolant | AMP102 In-service Inspection/ Periodic Inspection, AMP103 Water Chemistry, AMP154 WWER Pressurizer | No Yes, if TLAA (TLAA103 Crack Growth Analyses for Flaws Detected Inservice) |  |  | PWR