## AMP 102 	IN-SERVICE INSPECTION / PERIODIC INSPECTION

### Programme Description

The In-service Inspection (ISI) / Periodic Inspection Programme defines the NPP components which must be inspected, as well as methods for non-destructive testing (NDT) and the intervals between inspections.

The programme generally includes periodic visual, surface, and/or volumetric examination and leakage test of all safety class pressure-retaining components and their integral attachments. Repair/replacement activities for these components and acceptance by analysis (such as flaw analysis) are also covered.

The programme has been shown to be generally effective in managing ageing effects of safety classified components and their integral attachments in water cooled power plants. The ISI programmes for all types of nuclear power plant rely mostly on national codes and regulation [1-10], as well as some international inservice inspection requirements or guidance documents [11-15].

### Evaluation and Technical Basis

- Scope of the ageing management programme based on understanding ageing:

The programme provides the requirements for ISI of safety classified pressure-retaining components and their integral attachments in water cooled nuclear power plants. The programme also includes for acceptance by analysis (such as flaw evaluations), repair or replacement of degradation identified by the ISI.

- Preventive actions to minimize and control ageing degradation:

This is a condition monitoring programme. It does not implement preventive actions. However, if unacceptable indicators and deterioration are found in inspection, additional inspections, expansion of inspection scope, and increase in inspection frequency, are considered.

- Detection of ageing effects:

The programme detects degradation of components by using examination and inspection requirements for safety classified components.

Standards for examination methods, procedures, and personnel are provided in the programme, with preference to well-established examination methods. These methods include volumetric UT examination methods for detecting flaws in bolting, physical measurements for detecting changes in dimension, and various visual (e.g. VT-3, VT-1, and EVT-1 for IAEA Member States which apply ASME Codes) examinations for detection of general surface conditions and detection and sizing of surface-breaking discontinuities. Surface examinations may be used as an alternative to visual examinations for detection and sizing of surface-breaking discontinuities.

For IAEA Member States which apply PNAE G procedures, a description of the visual examination is given in a corresponding PNAE G [16].

Surface examination uses magnetic particle, liquid penetrant, or eddy current examinations, and in some cases ultrasonic examination, to indicate the presence of surface discontinuities and flaws.

Volumetric examination uses radiographic, ultrasonic, or eddy current examinations to indicate the presence of discontinuities or flaws throughout the volume of material included in the inspection programme.

The extent and schedule of the inspection and test techniques prescribed by the programme are designed to maintain structural integrity and ensure that ageing effects are discovered and corrected (repair or replacement) before the loss of intended function of the component. Inspection can reveal cracking, loss of material due to corrosion, leakage of coolant, and indications of degradation due to wear or stress relaxation of fitted connections such as bolts and keys, through detection of changes in clearances, settings, physical displacements, loose or missing parts, debris, wear, erosion, or loss of integrity at bolted or welded connections.

Components are examined and tested as specified in the pertinent governing requirements or guidance documents, such as ASME, JSME, etc., which specify the examination methods for the components of the pressure-retaining boundaries.

For example, “Rules of construction and safe operation of equipment and pipelines of the reactor installation” are given in [16], “Inspection and Evaluation Guidelines for PWR and BWR Reactor Vessel Internals” are in [17-23].

- Monitoring and trending of ageing effects:

For safety class components, the schedule, extent and frequency of inspections in accordance with the pertinent governing requirements or guidance documents, such as ASME, JSME, etc., provide for timely detection of degradation. The sequence of component examinations that is established during the first inspection interval is repeated during each successive inspection interval, to the extent practical. If flaw conditions or relevant conditions of degradation are evaluated in accordance with guidelines and the component is qualified as acceptable for continued service, the areas containing such flaw indications and relevant conditions are reexamined during the specified inspection periods.

- Mitigating ageing effects:

This is a condition monitoring programme. It does not implement mitigating actions. However, methods for water chemistry control are established to control and monitor any adverse effects of the water chemistry conditions on the ageing effects. The programme description and evaluation and technical basis of monitoring and maintaining reactor coolant chemistry are addressed in AMP 103.

- Acceptance criteria:

Any indication or relevant conditions of degradation may be evaluated for acceptance in accordance with the pertinent governing requirements or guidance documents. Examination results and flaws that exceed the acceptance criteria in the pertinent governing requirements or guidance documents may require repair or replacement activities, or further evaluation to demonstrate fitness-for-service of the component, to the satisfaction of the regulatory authority, until the end of the next periodic inspection interval.

- Corrective actions:

Repair and replacement activities are performed in conformance with the pertinent governing requirements or guidance documents when indications or relevant conditions of degradation cannot be demonstrated to be acceptable.

- Operating experience feedback and feedback of research and development results:

This AMP addresses the industry-wide generic experience. Relevant plant-specific operating experience is considered in the development of the plant AMP to ensure the AMP is adequate for the plant. The plant implements a feedback process to periodically evaluate plant and industry-wide operating experience and research and development (R&D) results, and, as necessary, either modifies the plant AMP or takes additional actions (e.g. develop a new plant-specific AMP) to ensure the continued effectiveness of the ageing management.

Because ISI has been widely used over a long period, it has been shown to be generally effective in managing ageing effects in safety classified components and their integral attachments in water cooled power plants.

Component specific information on operating experience feedback and on feedback of R&D results is given in [24-38]. Some specific examples of operating experience of component degradation are given in [12, 39].

This programme includes provisions for continuing review of plant-specific and industry-wide operating experience, and research and development results, such that impact on the programme is evaluated and any necessary actions or modifications to the programme are performed.

- Quality management:

Site quality assurance procedures, review and approval processes, and administrative controls are implemented in accordance with the different national regulatory requirements (e.g., 10 CFR 50, Appendix B [40]).

### References

- UNITED STATES NUCLEAR REGULATORY COMMISSION, 10 CFR 50.55a, Codes and Standards, Office of the Federal Register, National Archives and Records Administration, USNRC, 2015.

- AMERICAN SOCIETY of MECHANICAL ENGINEERS, ASME Section XI, Rules for Inservice Inspection of Nuclear Power Plant Components, The ASME Boiler and Pressure Vessel Code, 2008 addenda as approved in 10 CFR 50.55a, New York, NY.

- JAPAN NUCLEAR ENERGY SAFETY ORGANIZATION, Aging-Related Technology Assessment Review Manual Irradiation-Assisted Stress Corrosion Cracking (IASCC), JNES-SS-0809, JNES, 2009.

- KERNTECHNISCHER AUSSCHUSS, Safety Standards of the Nuclear Safety Standards Commission (KTA), In-service Inspections and Operation Monitoring, KTA 3201.4 and KTA 3211.4, KTA.

- ATOMIC ENERGY REGULATORY BOARD, Inservice Inspection of Nuclear Power Plants, AERB/NPP/SG/O-2, AERB, Mumbai, India, March 2004.

- ATOMIC ENERGY REGULATORY BOARD, Life management of Nuclear Power Plants, AERB/NPP/SG/O-14, AERB, Mumbai India, March 2005.

- French Ministerial Order of 10 November 1999, Operational surveillance of the main primary circuit and the main secondary circuits of pressurised water nuclear reactors.

- French Ministerial Order of 12 December 2005, Nuclear Pressure Equipment.

- French Ministerial Order of 15 March 2000, Operation of Pressure Equipment.

- RSE-M Code, In-Service Inspection Rules for Mechanical Components of PWR Nuclear Islands - 2010 edition - AFCEN (French Association for the rules governing the Design, Construction and Operating Supervision of the Equipment Items for Electro Nuclear Boilers).

- ELECTRIC POWER RESEARCH INSTITUTE, Primary System Corrosion Research Program: EPRI Materials Degradation Matrix, EPRI 1020987, Revision 2, EPRI, Palo Alto, CA, August 2010.

- ELECTRIC POWER RESEARCH INSTITUTE, Materials Reliability Program: PWR Internals Material Aging Degradation Mechanism Screening and Threshold Values MRP-175, (EPRI 1021024), EPRI, Palo Alto, CA, December 2005.

- ELECTRIC POWER RESEARCH INSTITUTE, BWR Vessel and Internals Project, Boiling Water Reactor Issue Management Tables, EPRI BWRVIP-167NP, Revision 2,  EPRI, Palo Alto, CA, August 2010.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Maintenance, Surveillance and In-Service Inspection in Nuclear Power Plants, Safety Guide, Safety Standards Series No. NS-G-2.6, IAEA, Vienna (2002).

- European Directive 97/23/EC of the European Parliament and of the Council of 29 May 1997 on the approximation of the laws of the Member States concerning pressure equipment.

- Rules of construction and safe operation of equipment and pipelines of the reactor installation, PNAEG-7-008-89, Russia.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE, Inspection and Evaluation Guidelines for BWR Reactor Vessel Internals, Shroud support, JANTI-VIP-04, JANTI, Tokyo, Japan.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE Inspection and Evaluation Guidelines for BWR Reactor Vessel Internals, Core Shroud, JANTI-VIP-05, JANTI, Tokyo, Japan.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE Guidelines for the Inspection and Evaluation of Reactor Internals, No.3 Edition, JANTI-VIP-06, JANTI, Tokyo, Japan.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE Inspection and Evaluation Guidelines for PWR Reactor Vessel Internals, Class1 Vessel, Safe End dissimilar metal weld joints, JANTI-VIP-08, JANTI, Tokyo, Japan.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE, Inspection and Evaluation Guidelines for PWR Reactor Vessel Internals, Reactor Vessel Bottom Mounted Instrumentation (BMI) , JANTI-VIP-09, JANTI, Tokyo, Japan.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE, Inspection and Evaluation Guidelines for BWR Reactor Vessel Internals, Jet pump, JANTI-VIP-14, JANTI, Tokyo, Japan.

- JAPAN NUCLEAR TECHNOLOGY INSTITUTE, Inspection and Evaluation Guidelines for BWR Reactor Vessel Internals, Core spray piping and sparger, JANTI-VIP-15, JANTI, Tokyo, Japan.

- INTERNATIONAL ATOMIC ENERGY AGENCY, Training guidelines I Non-destructive Testing Techniques, IAEA-TECDOC-628/Rev. 2, IAEA, Vienna (2008).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: Steam Generators, IAEA-TECDOC-981, IAEA, Vienna (1997).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: PWR Pressure Vessels, IAEA-TECDOC-1120, IAEA, Vienna (1999).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: Primary piping in PWRs, IAEA-TECDOC-1361, IAEA, Vienna (2003).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: BWR Pressure Vessels, IAEA-TECDOC-1470, IAEA, Vienna (2005).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: BWR Pressure Vessel Internals, IAEA-TECDOC-1471, IAEA, Vienna (2005).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power: PWR Pressure Vessels, IAEA-TECDOC-1556, IAEA, Vienna (2007).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: PWR Vessel internals, IAEA-TECDOC-1557, IAEA, Vienna (2007).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Strategy for Assessment of WWER Steam Generator Tube Integrity, IAEA-TECDOC-1577, IAEA, Vienna (2007).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Intercomparison of Techniques for Inspection and diagnostics of Heavy Water Reactor Pressure Tubes, IAEA-TECDOC-1609, IAEA, Vienna (2009).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Assessment and Management of Ageing of Major Nuclear Power Plant Components Important to Safety: Steam Generators, IAEA-TECDOC-1668, IAEA, Vienna (2011).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Risk-Informed In-Service Inspection of Piping Systems of Nuclear Power Plants: Process, Status, Issues and Development, IAEA Nuclear energy series NP-T-3.1, IAEA, Vienna (2010).

- INTERNATIONAL ATOMIC ENERGY AGENCY, Stress Corrosion Cracking in Light Water Reactors: Good Practices and Lessons Learned, IAEA Nuclear energy series NP-T-3.13, IAEA, Vienna (2011).

- NUCLEAR ENERGY AGENCY, Technical Basis for Commendable Practices on Ageing Management - SCC and Cable Ageing Project (SCAP) Final Report NEA/CSNI/R(2010)15, NEA.

- Materials Degradation and Related Managerial Issues at Nuclear Power Plants, Proceedings of a Technical Meeting, Vienna, 2005.

- UNITED STATES NUCLEAR REGULATORY COMMISSION, Generic Aging Lessons Learned (GALL) Report, NUREG-1801, Rev. 2, USNRC, 2010.

- UNITED STATES NUCLEAR REGULATORY COMMISSION, 10 CFR Part 50, Appendix B, Quality Assurance Criteria for Nuclear Power Plants, Office of the Federal Register, National Archives and Records Administration, USNRC, 2015.