Начало формы

| WANO Event Report WANO Moscow Centre, 2020-0153 | #PRELIMINARY# The Unit Was Tripped Off Line to Identify the Causes of Aerosol Activity. Zaporozhye 6, 14.05.2020 | Revision Number 00 - Posted date 19.05.2020 |
| --- | --- | --- |

T

| Unit (Year) :; Zaporozhye 6 (1996). Additional Units :. Reactor Type :; PWR. Reactor Manufacturer :; KhO AEP. Plant Designer :; Ministry of Heavy Engineering. Event Date :; 14.05.2020. INES :; 0. | OE Station Information Contact WANO Information Contact Name : Sergey Kezin, WANO Moscow Centre , Email : kezin@wanomc.ru , Phone : - |
| --- | --- |

| Reference : |  |
| --- | --- |

OECT Information

Summary
N/A 

Causes
N/A 

Keywords
N/A 

References
N/A

Summary

Unit 6 was operating at limited 1,700MW thermal power and 545MWe electrical load due to dispatcher limitations.

12.05.2020

Indications of high aerosol activity in the containment were observed. An application was filed to trip the unit to locate a source of the high aerosol activity.

14.05.2020

11:02

The unit was downpowered at the operating rate and subsequently tripped off line by the operations personnel.

13:15

The unit was placed in the hot shutdown conditions.

14:20

The containment was inspected to find a leak from the pulse line on the vertical section of the reactor coolant system in the area between steam generator No. 1 and Reactor Coolant Pump (RCP) No.1 suction pipeline bend. This pipeline section is non-isolable. The following defect was recorded: A leak from the weld upstream of shut-off device YA10P14R2 (Reactor Coolant Pipeline No. 1 cold leg) in room GA407/1.

The unit was placed into the routine maintenance condition.

The event is under investigation.

Description

Unit 6 was operating at limited 1,700MW thermal power and 545MWe electrical load due to dispatcher limitations.

12.05.2020

Indications of high aerosol activity in the containment were observed. An application was filed to trip the unit to locate a source of the high aerosol activity.

14.05.2020

11:02

The unit was downpowered at the operating rate and subsequently tripped off line by the operations personnel.

13:15

The unit was placed in the hot shutdown conditions.

14:20

The containment was inspected to find a leak from the pulse line on the vertical section of the reactor coolant system in the area between steam generator No. 1 and Reactor Coolant Pump (RCP) No.1 suction pipeline bend. This pipeline section is non-isolable. The following defect was recorded: A leak from the weld upstream of shut-off device YA10P14R2 (Reactor Coolant Pipeline No. 1 cold leg) in room GA407/1.

The unit was placed into the routine maintenance condition.

Consequences

The unit was tripped off line.

Loss of energy generation.

Limits and conditions of safe plant operation were not violated.

Analysis/Comments

The event is under investigation.

Corrective Actions

Actions will be taken as the investigation progresses.

Attachments

Coded Fields

| Field | Code | Description |
| --- | --- | --- |
| Category | 02 | Safety system malfunctions or improper operations |
| Consequences | 02 | Station transient |
| Systems | 150 | Reactor Coolant System |
| Components | 260 | Tubes, Pipes, Ducts |
| Status | 110 | Steady power operation |
| Activity | 40 | Fault finding or troubleshooting |
| Group | 140 210 220 340 | Mechanical Shift - Control Room Operators Shift - Field Operators Mechanical |
| Direct Cause | 0106 | Break, rupture, crack, weld failure |
| Root Cause |  |  |
| Causal Factor |  |  |

CONFIDENTIALITY NOTICE: Copyright © 1987-2020 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale or commercial use. This document is protected as an unpublished work under the copyright laws of all countries which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. This document and its contents are confidential and shall be treated in strictest confidence. In particular, except with the prior written consent of the WANO Coordinating Centre, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations.

LIABILITY DISCLAIMER NOTICE: This information was prepared in connection with work sponsored by the WANO. Neither WANO, WANO members, nor any person acting on the behalf of them (a) makes warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that use of any information, apparatus, method or process disclosed in this document may not infringe on privately owned rights, or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of any information, apparatus, method, or process disclosed in this document.

Конец формы