## Sheet
Significance | INES | Event Number | Event Date | Reference Unit | Title | OECT Description | OECT Causes | Keywords | OECT Reference | PO&Cs
Significant | N | WER TYO 15-0221 | 2015-01-08 | Chasnupp 1 | Plant Trip on Loss of Grid and Failure of One EDG | During normal operation, complete loss of offsite power resulted in automatic reactor scram on under frequency signal on 6 kV bus supplying reactor coolant pumps. Both emergency diesel generators (EDG) started automatically but soon one EDG stopped due to excitation problem. Onsite emergency plan was activated. An alternate AC diesel generator was started 23 minutes later. Core cooling was established through natural circulation. The event is classified as Significant because of complete loss of offsite power for about eight hours, failure of one EDG and activation of emergency plan. The loss of offsite power also effected unit 2, see WER TYO 15-0211. | The cause of loss of offsite power was tripping of a 500kV transmission line on national grid due to severe weather condition. The cause of failure of one EDG was a drifted set point which resulted in cutoff of excitation during initial loading of the EDG. | diesel generator,emergency plan,grid,loss of offsite power,automatic scram,setpoint drift,1 - For information only | SOER 1999-1 Rec 1 | OPERATION CONFIGURATION CONTROL (CM.2); EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Noteworthy | N | WER PAR 15-0627 | 2015-02-15 | Yangjiang 1 | Air Leakage in Diaphragms & Breathing Holes of Some VELAN Pneumatic Cutoff Valves of Unit Y1 | During inspection of VELAN pneumatic cutoff valves used in various safety related systems, air leakage was found from breathing holes of the valves. This was a common mode failure and excessive leakage may effect valve opening and closing. This event is classified as Noteworthy due to a common mode failure of pneumatic valves used in safety related systems. | The root cause was too thick valve diaphragm compensation ring designed and insufficient torque of pneumatic rod central nut, resulting in insufficient diaphragm compression. | common mode failure,design,diaphragm,instrument air,leak,pneumatic actuator,torque,2 - Important lessons |  | ENGINEERING FUNDAMENTALS (EN.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Noteworthy | N | WER ATL 15-1106 | 2015-06-03 | Waterford 3 | Manual Reactor Trip Due to Loss of Main Feedwater | During normal operation and while performing preventive maintenance, one main feedwater pump (FWP) tripped, resulting in low steam generator level and a manual reactor scram. The remaining FWP was lost due to the failure to transfer power supply from the station startup transformer. Emergency diesel generators (EDG) and emergency feedwater (EFW) system started up. This event is classified as Noteworthy because of the operation complications after the scram including the failure to fast transfer and EFW flow oscillations requiring manual actions. (Also see WER alt 15-1107) | The direct cause was the failure of intermediate pressure heater normal level control valve due to stem/disc separation. The root cause was the failure to identify the failure mechanism for repeated failures of non-safety related feedwater heater drain valves. A contributing cause was inadequate scheduling of preventive maintenance creating the trip initiator condition. The possible cause of failing to transfer to the startup transformer was the failure of the relay contact set. | auxiliary feedwater pump,control valve,diesel generator,emergency feedwater,feedwater,heater drain,loss of offsite power,manual scram,steam generator,transformer,work control,2 - Important lessons |  | EQUIPMENT PERFORMANCE (ER.1); OPERATIONAL RISK (OF.2); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2); ONLINE AND OUTAGE WORK MANAGEMENT (WM.1);
Noteworthy | N | WER ATL 15-1102 | 2015-05-26 | Pickering B8 | Passing Valves in Liquid Injection Shutdown System Required a Forced Outage of the Unit | During normal operation, liquid injection shutdown system (LISS) injection valve on one channel was passing helium, resulting in restrictions on the unit testing and operation. When another valve also experienced passing, as a result of unknown failure modes, and a 13-day forced outage was required to overhaul the valves. This event is classified as Noteworthy because leaking shutdown system injection valves posing increased operational risk and long duration of the forced outage. | The direct cause was valve plug o-ring degradation. The apparent cause was the previous change that increased the valve overhaul frequency from 4 to 8 years. A contributor was that ventilation units did not provide proper local temperature condition. | environment,leak,preventive maintenance,reactivity management,reactor protection system,reactor shutdown,valve,2 - Important lessons | SOER 2007-1 Rec 5 | EQUIPMENT FAILURE PREVENTION (ER.2); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Noteworthy | N | WER TYO 15-0222 | 2015-01-24 | Chasnupp 1 | Plant Trip on Loss of Grid | While disconnected from the grid and operating at 4% power, both offsite power sources were lost. The reactor automatically scrammed due to a reactor coolant pump under frequency bus signal. Both emergency diesel generators (EDG) automatically started and energized the two emergency buses. A station emergency was declared. This event is classified as Noteworthy because of total loss of offsite power and the length of time that the EDGs were in operation (~10 hours). Unit 1 was also affected. (see WER TYO-15-0213) | The cause was the tripping of the offsite 500kV transmission line which resulted in a nationwide grid loss. Grid instability causes frequent loss of offsite power events. | diesel generator,emergency response,loss of offsite power,reactor coolant pump,automatic scram,transmission line,1 - For information only | SOER 1999-1 Rec. 1 | EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Noteworthy | N | WER TYO 15-0213 | 2015-01-24 | Chasnupp 2 | Plant Trip on Loss of Grid | During normal operation, complete loss of offsite power resulted in automatic reactor scram on under frequency signal on 6 kV bus supplying reactor coolant pumps. Both emergency diesel generators (EDG) started automatically. Standby emergency was declared and core cooling was established through natural circulation. The event is classified as Noteworthy because of complete loss of offsite power for over 10 hours. The loss of offsite power also effected Unit 1, see WER TYO 15-0222. | The cause was tripping of 500 kV transmission line in national grid. Grid instability causes frequent losses of offsite power. | emergency plan,grid,loss of offsite power,automatic scram,1 - For information only | SOER 1999-1 Rec 1 | EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Noteworthy | N | WER TYO 15-0212 | 2014-12-12 | Chasnupp 2 | Plant Trip on Loss of Grid | During normal operation, both offsite power sources were lost. The reactor automatically scrammed due to a reactor coolant pump under frequency bus signal. Both emergency diesel generators (EDG) automatically started and energized the two emergency buses. A station emergency was declared. This event is classified as Noteworthy because of a total loss of offsite power and the length of time that the EDGs were in operation (~7 hours). | The cause was the tripping of the offsite 500kV transmission line which resulted in nationwide grid loss. Grid instability causes frequent loss of offsite power events. | diesel generator,emergency response,loss of offsite power,reactor coolant pump,automatic scram,transmission line,1 - For information only | SOER 1999-1 Rec. 1 | EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Noteworthy | N | WER TYO 15-0211 | 2015-01-08 | Chasnupp 2 | Plant Trip on Loss of Grid | During normal operation, complete loss of offsite power resulted in automatic reactor scram on under frequency signal on 6 kV bus supplying reactor coolant pumps. Both emergency diesel generators (EDG) started automatically. Standby emergency was declared and core cooling was established through natural circulation. The event is classified as Noteworthy because of complete loss of offsite power for over seven hours. The loss of offsite power also affected Unit 1, see WER TYO 15-0221. | The cause was tripping of a 500 kV transmission line on national grid due to severe weather conditions. Grid instability causes frequent losses of offsite power. | emergency plan,grid,loss of offsite power,automatic scram,1 - For information only | SOER 1999-1 Rec 1 | EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Other | 0 | WER PAR 15-0651 | 2015-06-13 | Forsmark 2 | #PRELIMINARY# Ground fault in 110V DC system | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0660 | 2015-01-22 | Ringhals 2 | #PRELIMINARY# Malfunctioning 6kV breaker, type VA10020/12-2, Schneider Electric AB | See summary below. | See causes below. | 1 - For information only
Other | N | WER PAR 15-0628 | 2015-02-22 | Yangjiang 2 | Activation of Fire Fighting in the Room due to Back Filling of Exhaust Steam during Operation of Y2ASG003PO(Unit Y2 Auxiliary Feedwater003 Pump) | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0642 | 2015-08-20 | Heysham B2 | Adverse Trend – Plant Walkdowns | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1129 | 2015-06-17 | Fort Calhoun 1 | Air Void Discovered in Raw Water Header | See summary below. | See causes below. | 1 - For information only
Other | N | WER TYO 15-0217 | 2014-08-15 | Shin-Kori 1 | Application of improved equipment and retrieval tool for small foreign objects in steam generator tube bundle | See summary below. | See causes below. | 2 - Important lessons
Other | N | WER ATL 15-1130 | 2015-07-02 | Seabrook 1 | Boron Waste Storage Tank Level Change Due to Mispositioned Valve | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0647 | 2015-07-31 | Forsmark 1 | Closed indication for isolation valve 756 V101 not functioning | See summary below. | See causes below. | 1 - For information only
Other | N | WER PAR 15-0630 | 2015-03-03 | Yangjiang 1 | Corrosion of a Number of Pipe/Valve Flanges of Y1SEC (Yangjiang Unit 1 Essential Service Water )System | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0636 | 2015-06-03 | Krsko 1 | Dual Resistance Temperature Detectors (RTD) on Cold Leg Issue | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0661 | 2015-01-14 | Dungeness B 2 | Electro-chlorination Plant Return to Service | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0662 | 2015-05-05 | Dungeness B 2 | Failure to Achieve Stationary Seal on Gas Circulator (GC) 25 | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0657 | 2015-04-14 | Hartlepool 1 | Fixed Jet Pressure Sustaining Unit Isolation | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0639 | 2015-05-11 | Heysham B1 | Generator Hydrogen Dryer 7 Unavailability | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1123 | 2015-07-09 | Seabrook 1 | Grinding Activities Resulted in Fire Alarm Activation Due to Smoldering Rag | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0634 | 2015-08-13 | Forsmark 2 | Ground fault in 110V DC system | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0648 | 2015-07-27 | Krsko 1 | Increased Vibration on Turbine Governor Valve No. 4 | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1132 | 2015-08-13 | Point Beach 1 | Level 3 Misposition During Modification Acceptance Test | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0003 | 2014-11-12 | La Hague 1 | Limited liquid waste transfer from the R7 facility to the R2 facility wrongly based on the sampling results of a previous liquid transfer | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0644 | 2015-08-17 | Sizewell B 1 | Loss of Refrigerant from Chiller Units | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1124 | 2015-06-08 | Davis Besse 1 | Mispositioning Event Occurred During Removal of Battery Charger from Service | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0640 | 2015-08-03 | Sizewell B 1 | Near Miss - Technical Specification Channel Check | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER ATL 15-1114 | 2015-09-28 | Koeberg 1 | One of two samples taken from the Surge Tank for the Boron Injection Tank was mistakenly placed in a Core Flooding Accumulator sample bottle. | See summary below. | See causes below. | 1 - For information only
Other | 0 | WER PAR 15-0652 | 2015-07-01 | Sizewell B 1 | Potential Adverse Trend in Engineering Change Related Configuration Control Events | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1111 | 2015-06-27 | River Bend 1 | Reactor Feedwater Master Level Controller Unexpectedly Shifted to Manual Resulting in a Reactor Vessel High Water Level Alarm | See summary below. | See causes below. | 1 - For information only
Other | N | WER TYO 15-0216 | 2015-06-27 | Fukushima Daiichi 1 | Right hand injury of a worker | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1125 | 2015-07-06 | Cooper 1 | Startup Transformer Inoperable due to Grid Voltage | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1122 | 2015-07-17 | Seabrook 1 | Steam Generator Blowdown Heat Exchanger Temperature Controller Found Mispositioned | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1121 | 2015-07-01 | Cooper 1 | Survey Instrument Became Lodged in the Refuel Bridge Mast | See summary below. | See causes below. | 1 - For information only
Other | N | WER TYO 15-0215 | 2015-06-11 | Fukushima Daiichi 1 | Suspended operation of multi-nuclide removal facility circulation pumps | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1112 | 2015-08-10 | Point Lepreau 1 | Temporary Modification Installed Without Proper Approval | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1126 | 2015-07-05 | South Texas 1 | Turbine Building Sump Pump Handswitch Mispositioned | See summary below. | See causes below. | 1 - For information only
Other | N | WER ATL 15-1116 | 2015-08-28 | Pickering A1 | Turbine Lubricating Oil Purifier Operational Issues Resulted in Operator Burdens and the Purifier Reliability Issues | See summary below. | See causes below. | 2 - Important lessons
Other | N | WER ATL 15-1119 | 2015-06-17 | Oconee 1 | Valve Found Closed When Its Expected Position Was Open | See summary below. | See causes below. | 1 - For information only
Trending | 0 | WER PAR 15-0649 | 2015-06-09 | Forsmark 2 | #PRELIMINARY# Automatic relief path for filtered pressure relief of the reactor containment not ready for operation | During normal operation and while performing reactor containment integrity test, a rupture disk ruptured at too low pressure. This resulted in an increased risk for inadequate margin to loss of net positive suction head for containment spray system and emergency core cooling system. | The direct cause was installation of a rupture disk with incorrect burst pressure. The underlying cause was misinterpretation of burst pressure requirement for the rupture disk by the supplier. | design,differential pressure,rupture disc,specification,vendor,1 - For information only |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | 0 | WER PAR 15-0633 | 2015-07-04 | Forsmark 2 | #PRELIMINARY# Control rod drive R45 not ready for operation | While operating at 54% power and during rod movement in conjunction with flux tilting, a control rod could not be completely withdrawn. | The direct cause was foreign material, a small metal pin, had caused the control rod drive to seize. The origin of the pin is under investigation. | control rod drive,flux tilt,FME |  | CONDUCT OF MAINTENANCE (MA.2);
Trending | N | WER ATL 15-1099 | 2015-08-12 | Chalk River NRU 1 | #PRELIMINARY# Radiation Dose(s) Received in Excess of the Action Level | During removal of fuel-end from a spent fuel rod assembly, a radiation surveyor was exposed to a peak dose rate of 2320 mrem/h and other members of the crew were exposed to 444-864 mrem/h. | The direct cause was mistake by the workers as they removed the orifice section without first completing the procedure to remove the fuel-end. Poor underwater lighting and reduced local visibility due to turbidity complicated the work. The apparent cause is under investigation. | fuel rod,human error,radiation exposure,1 - For information only | SOER 2001-1 Rec 8 | FUELLING ACTIVITIES (FA.1); MAINTENANCE FUNDAMENTALS (MA.1); RADIOLOGICAL SAFETY (RS.1);
Trending | 0 | WER MOW 15-0201 | 2015-09-25 | Mochovce 2 | #PRELIMINARY# Steam dump to the atmosphere and SG safety valve failure | While shutting down for an outage and at 90% power, a steam dump valve to atmosphere failed to open during a test. Later in another test, safety valve of a steam generator failed to open from main control room. | The direct cause was activation of protection of steam dump to atmosphere and failure of remote control of the steam generator safety valve. The root causes are under investigation. | control circuit,safety relief valve,steam dump valve,steam generator,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1);
Trending | 0 | WER MOW 15-0202 | 2015-10-02 | Kalinin 4 | #PRELIMINARY# The Reactor Protection System (RPS) actuated on low Steam Generator (SG) level. | Following power reduction and while operating at 945 MWe, an in-service turbine feedwater pump (TFP) tripped, resulting in low water level in a steam generator. Consequentially, all four reactor coolant pumps tripped and the reactor scrammed automatically. | The cause was attributed to the malfunctioning modules that had disturbed the power supply of the TFP instrumentation channel position indicator, thereby causing a false TFP control mode algorithm. Investigation of the root causes is in progress. | feedwater pump,reactor coolant pump,reactor protection system,automatic scram,steam generator,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1);
Trending | N | WER ATL 15-1107 | 2015-06-03 | Waterford 3 | 4KV Fast Bus Transfer Failure | During plant transient reported in WER ATL 15-1006, the 4 kV fast bus transfer failed to automatically transfer power to startup transformer from unit auxiliary transformer. This resulted in loss of offsite power to a safety train, which caused starting of an emergency diesel generator. | The cause was failure of a relay. A contributing cause was that failure was not identified prior to the loss of offsite power due to an inadequate design change. | alarm,design,diesel generator,loss of offsite power,modification,relay,transformer,1 - For information only | SER 2005-3 | DESIGN CHANGE PROCESSES (CM.3); ENGINEERING FUNDAMENTALS (EN.1); EQUIPMENT PERFORMANCE (ER.1);
Trending | 0 | WER ATL 15-1115 | 2015-08-11 | Barakah 1 | Adverse Trend Identified for Personnel Injuries during Construction | During construction stage, an adverse trend was identified regarding personnel injuries. There were 17 industrial safety events involving loss time accidents and injuries requiring off-site medical treatment during last four months. | The common causes were inadequate written process, lack of supervision, inadequate risk assessment, improper dissemination of lessons learned and inadequate training. | industrial safety,injury,procedure inadequacy,supervisory oversight,1 - For information only |  | INDUSTRIAL SAFETY (IS.1);
Trending | N | WER TYO 15-0220 | 2015-04-20 | Chinshan 1 | An Abnormal Seismic Monitor Response During an Earthquake Event | During normal operation and a second level earthquake strike, the strong seismic monitor was triggered but the weak monitor was not. | The root cause was that the weak and strong sensor covers were swapped during installation following calibration. The contributing cause was that maintenance staff did not verify the serial number of the cover and sensor prior to installation. 4c | human error,seismic event,seismic monitoring,1 - For information only |  | MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER ATL 15-1109 | 2014-08-03 | Comanche Peak 2 | Centrifugal Charging Pump Main Lube Oil Pump Coupling Fails Causing Out of Service Time to Exceed Tech Spec Action Statement | During normal operation and while checking the normal equipment rotations, a centrifugal charging pump (CCP) main lube oil pump (MLO) coupling failed. A past operability review found that the CCP was inoperable longer than allowed by tech specifications, making the event reportable to the regulator. | The direct cause was disengagement of shaft driven MLO coupling from the speed increaser shaft due to incorrect assembly during last inspection. The root cause was inadequate accessibility of the coupling as it does not allow post-installation verification. The contributing cause was that MLOP driven coupling hub shaft bore was not true and the personnel assigned to the reassembly lack proficiency. | centrifugal charging pump,coupling,design,human error,lube oil pump,technical specification,2 - Important lessons |  | ENGINEERING FUNDAMENTALS (EN.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER ATL 15-1118 | 2015-06-23 | Brunswick 1 | Component Mispositioning Causes Loss of Wide-Range Gas Monitor | See summary below. | See causes below. | human error,limiting condition of operation,mispositioned valve,procedure inadequacy,pump,radiation monitor,1 - For information only |  | OPERATION CONFIGURATION CONTROL (CM.2); CHEMISTRY FUNDAMENTALS (CY.1);
Trending | 0 | WER PAR 15-0641 | 2015-05-16 | Dungeness B 2 | Configuration Control – Essential Cooling Water Ring Main Segregation | During an outage, reactor 21 and reactor 22 essential cooling water re-circulating (ECWR) half ring mains were found in an incorrect configuration. The event resulted in non-conformance with the requirements of technical specification. | The direct cause was that configuration checks in reactor return to service paperwork did not include all ring main sectioning valves. The root cause was inadequate procedure. | configuration control,cooling water,procedure deficiency,1 - For information only | SOER 1998-1 Rec 1 | OPERATION CONFIGURATION CONTROL (CM.2); CONDUCT OF OPERATIONS (OP.2);
Trending | N | WER ATL 15-1103 | 2015-03-08 | Salem 1 | Containment Fan Coil Unit Tripped While in Low Speed | During a planned power reduction and while testing a containment fan coil unit (CFCU), the CFCU breaker tripped open on thermal overload resulting in entry into a shutdown limiting condition of operation (LCO). The CFCU surpassed its LCO resulting in a forced shutdown for approximately seven days. | The apparent cause was failure of stator support frame welds, allowing contact between the rotor and the stator. The contributing cause was inadequate preventive maintenance. | containment,fan cooler,heating ventilating and air conditioning,limiting condition of operation,preventive maintenance,reactor shutdown,weld,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1); EQUIPMENT FAILURE PREVENTION (ER.2);
Trending | 0 | WER PAR 15-0631 | 2015-07-28 | Forsmark 2 | Control rod drive K40 not ready for operation | During nuclear heating after an outage and while testing reactor protection system on the emergency core cooling system, a signal for spurious insertion of 7 control rod drives was received and later when operator performed a manual trip of the control rod screw insertion circuit, a control rod drive failed to actuate. | The direct cause was spurious insertion of seven control rod drives. The cause of failure of a control rod drive was a fault in the control rod drive cassette. The root cause was a broken relay in the control rod drive cassette which prevented actuation of the control rod drive. | ageing,control rod drive,reactor protection system,relay,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1); LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | N | WER ATL 15-1105 | 2015-05-13 | Quad Cities 1 | Control Rod Scrammed During Testing | During normal operation and while performing reactor protection system test switch functional test, a control rod drop resulted in reduction in reactor power by 4%. | The apparent cause was an intermittent short or ground at the scram solenoid pilot valve which caused the fuse to blow. The contributing cause was inadequate preventive maintenance. | control rod,fuse,ground fault,power reduction,preventive maintenance,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1); EQUIPMENT FAILURE PREVENTION (ER.2);
Trending | N | WER ATL 15-1128 | 2015-06-10 | Hatch 2 | Core Spray Pump Discharge Check Valve Failed Check | During normal operation and after the core spray (CS) pump surveillance, one CS loop was unable to maintain the system pressure when the pump was secured due to a discharge check valve failing to check. | The cause was the valve binding due to degradation. The valve disc did not have an anti-rotation pin, which can prevent the wear caused by disc rotation. The most likely cause was inadequate inspection during the previous maintenance. The same event had previously occurred. | binding,check valve,core spray,degradation,human performance,leak,pressure,1 - For information only |  | EQUIPMENT FAILURE PREVENTION (ER.2); MAINTENANCE FUNDAMENTALS (MA.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Trending | N | WER ATL 15-1134 | 2015-06-17 | Calvert Cliffs 1 | Diesel Generator Load Run Failure Due to High Lubrication Oil Differential Pressure | During normal operation and while performing a diesel generator test, lubricating oil differential pressure at the lubricating oil filters increased excessively. The diesel generator was declared inoperable and a technical specification action statement entry was made. | The cause was fouling of the lubrication oil filters caused by a cylinder liner cooling water leak. Human performance during installation resulted in damage to the filter o-ring. | diesel generator,filter,fouling,human performance,leak,limiting condition of operation,lubrication,pressure,test,1 - For information only |  | MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER ATL 15-1142 | 2015-07-14 | Susquehanna 1 | Diesel Generator Mode Switch Inadvertently Manipulated During Certification Exam | While performing an in-plant training examination, a trainee inappropriately operated an emergency diesel generator (EDG) control mode select switch, placing the mode switch in the LOCAL position. This resulted in the EDG being declared inoperable and entry into limiting condition of operations. | The cause was the trainee failed to use human performance tools and inadequate verification of the instructor. | diesel generator,human performance,limiting condition of operation,misposition,2 - Important lessons |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER ATL 15-0616 | 2015-03-16 | Brunswick 2 | Diesel Generator Output Breaker Failed to Close Due to Relay Timer Oscillations | During an outage and while performing a loss of offsite power (LOOP) test, a diesel generator (DG) output breaker failed to close while another DG was inoperable. The fault occurred only if the DG was already running and received a breaker closure signal. This resulted in about 2.5 day delay in outage critical path. | The direct cause was the relay failure due to the electromagnetic kickback generated by another relay downstream. The output breaker closure logic was found susceptible to the voltage transient. The vendor changed material/parts without prior communication. | breaker,communication,diesel generator,relay,spare part,vendor |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | N | WER ATL 15-1133 | 2015-06-08 | Callaway 1 | Emergency Diesel Generator Ventilation Supply Fan Breaker Tripped | During normal operation, an emergency diesel generator (EDG) ventilation supply fan tripped. This caused entry into a shutdown technical specification action statement. | The cause was burning of the control power fuse of the EDG ventilation supply fan. This was caused by unlatched starter contact cover clip, which prevented the holding coil in the starter from energising and caused the pick-up coil in the starter to continue to draw in-rush current until it overheated and experienced an internal short which caused control power fuse to blow. | diesel generator,fan,fuse,heating ventilating and air conditioning,limiting condition of operation,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1);
Trending | 0 | WER PAR 15-0645 | 2015-08-08 | Forsmark 2 | Emergency ventilation not ready for operation while fuel was being handled | During normal electrical power system testing and while moving fuel with refuelling machine from the reactor pressure vessel to a pool, the normal electrical power in the train supplying refuelling machine was lost. This resulted in the refuelling machine stopping with fuel in the grapple. The loss of power also rendered emergency filter system for reactor building not ready for operation. In the case of loss of coolant accident during the outage, the fuel assembly in the machine could have been uncovered. | The direct cause was loss of power supply during electrical testing. The underlying cause was deficient self-check as actions were performed that were not planned according to the governing documents.&nbsp; | fuel handling,heating ventilating and air conditioning,human error,power supply,1 - For information only | SOER 2010-1 Rec 8 | FUELLING ACTIVITIES (FA.1); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | 0 | WER PAR 15-0656 | 2015-08-05 | Forsmark 1 | Failure of fire damper 742V112 to close during annual test | During functional testing of reactor building fans and dampers, a damper which prevents the spread of smoke from adjacent spaces into one of the two reactor trip rooms did not close. | The direct cause was the plastic on the coil had melted and stuck to the holder, which prevented the damper from dropping. The underlying cause was that the coil had corroded due to water dropping on it from previous leakage from the ceiling of the room. Corrosion combined with heat caused the anchor plate and the coil to stick. | coil,corrosion,fire damper,surveillance,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1);
Trending | N | WER TYO 15-0219 | 2015-07-27 | Kashiwazaki Kariwa 1 | Feeling of illness during outdoor work | A worker who was engaged in traffic control complained of feeling ill and was transported to a hospital. He was diagnosed with mild heat stroke. | The cause was insufficient pre-work check-ups of physical condition and replacement of water and minerals during extremely hot summer season. | contractor,environment,industrial safety,1 - For information only |  | INDUSTRIAL SAFETY (IS.1);
Trending | N | WER TYO 15-0218 | 2015-07-13 | Kashiwazaki Kariwa 1 | Feeling of illness during outdoor work | While working in the field, a contractor reported feeling ill. The contractor was transported to the hospital for mild heat stroke. | The cause was that pre-work check-ups of the work area conditions and replacement of water and minerals, including salt, for the contractor were insufficient. | industrial safety,personnel injury,1 - For information only |  | INDUSTRIAL SAFETY (IS.1);
Trending | N | WER TYO 15-0214 | 2015-08-18 | Kori 1 | Fire Extinguishing Water Sprinkling by the Actuation of Fire Detector in EDG Room | During normal operation and after completing an emergency diesel generator (EDG) surveillance test, the fire sprinkler system automatically activated in the EDG room. Operators manually stopped the deluge after about two minutes as there was no actual fire. | The direct cause was heat from the EDG exhaust pipe triggered the fire detector. A contributing factor was that the EDG room fan was stopped and bypass dampers was closed immediately after the test as the surveillance procedure did not specify how long to keep the room ventilated after the test. | diesel generator,fire suppression,surveillance,1 - For information only |  | OPERATION CONFIGURATION CONTROL (CM.2); CONDUCT OF OPERATIONS (OP.2);
Trending | 0 | WER PAR 15-0659 | 2015-07-29 | Forsmark 3 | Fire sprinkler valve VC59 failed to open during actuation test | During normal operation and while testing fire sprinkling system, a sprinkler valve did not open. According to the technical specification, the water sprinkler system should be ready for operation when the reactor temperature is greater than 100 degrees celsius. | The cause was a faulty solenoid valve associated with the sprinkler valve. | fire protection,solenoid valve,sprinkler,technical specification,valve,1 - For information only |  | FIRE PROTECTION (FP.1);
Trending | N | WER ATL 15-1100 | 2015-05-31 | Columbia Generating Station | Flow Accelerated Corrosion Discovered in Reactor Water Cleanup System Piping | During an outage, interconnecting piping between reactor water cleanup system regenerative heat exchangers was found to be below the required minimum wall thickness. Consequently, the outage was extended by approximately 3.4 days for repairs. | The direct cause was flow accelerated corrosion (FAC) due to low dissolved oxygen levels in unprotected carbon steel piping as a result of inadequate chemistry control. The apparent cause was inadequate and misapplied internal and external operating experience. A contributing cause was inadequate FAC inspection. | chemistry,erosion/corrosion,inspection,pipe,2 - Important lessons | SER 2006-1 | EQUIPMENT FAILURE PREVENTION (ER.2); MATERIALS RELIABILITY (ER.4); SOLUTIONS IMPLEMENTATION (PI.3);
Trending | N | WER TYO 15-0014 | 2014-12-28 | Chinshan 1 | Fuel Assembly Load Chain Failure Event | During an outage and when attempting to raise a fuel bundle from the reactor core, sudden reduction of load indication on the refuelling machine was observed and the refuelling was suspended. | The most probable causes are a surface imperfection possibly arising from a material defect, and an unexpected stress state, unique to this fuel assembly. This failure was evaluated as a non-generic event with low possibility of recurrence. | fuel handling,refuelling,1 - For information only |  | FUELLING ACTIVITIES (FA.1);
Trending | 0 | WER PAR 15-0637 | 2015-05-04 | Tihange 1 | House Load Operation of the South Turbo Generator due to Primary Pump 2 Low Speed | During normal operation and while testing speed sensors of a reactor coolant pump, a sensor was disconnected for re-tightening when the other sensor was on test mode. This resulted in house load operation of one of the two turbine generators due to actuation of low speed logic in the reactor coolant pump and consequently the reactor power reduced to 50%. | The direct cause was error in disconnection of a speed sensor when the test mode was already selected for logic chain in another CRP sensor. The root cause was inadequate pre-job brief and lack of questioning attitude as the technician did not check the label present on the sensor. | human error,label,power reduction,prejob brief,reactor coolant pump,speed sensing device,turbine generator,1 - For information only |  | MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER PAR 15-0635 | 2015-04-15 | Hartlepool 1 | Inadequate Control of Open Hole as per BEG/SPEC/SHE/COP/024A | An operator while investigating an alarm in the field, injured his lower leg that went through an 8 inch gap in the grating. He was sent to local healthcare center for treatment. | The direct cause was an unauthorised open hole due to lifting of grating. The root cause was that the work order card and pre-job brief was not followed. The contributing causes were that barriers or signage was not erected to alert personnel and requirement of an open hole document was not followed. | grating,industrial safety,injury,procedure adherence,1 - For information only |  | INDUSTRIAL SAFETY (IS.1);
Trending | N | WER ATL 15-1108 | 2015-06-22 | Fort Calhoun 1 | IsoPhase Bus Duct Cooling Fan Tripped | During normal operation, both isophase bus duct cooling fans unexpectedly tripped multiple times, resulting in a loss of isophase bus duct cooling and a power reduction to 60%. | The apparent cause was inadequate design and installation of the overload relay circuit. A contributing cause was an elevated temperature at the motor control centre, inadequate thermal overload relay setting and use of the non-compensated thermal overloads relay. | cooling,design,fan,installation,motor,motor control centre,overload,power reduction,relay,setpoint,temperature,1 - For information only |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | N | WER TYO 15-0209 | 2014-08-04 | Fuqing 1 | KIC (Plant Computer Information & Control System) operator station shortly unavailability | During commissioning at 0.95% reactor power, plant digital computer information and control system (KIC) was unavailable. KIC lost its functions, station monitoring and control switched to back up panel (BUP) and control rods switched to auto mode. | The direct cause was incorrect configuration of KIC. The root cause was that I and C personnel failed to comprehensively verify the parameter data during modification. Another root cause was inadequate risk awareness of I and C personnel on the essential equipment related to DCS. | human error,modification,monitor |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | 0 | WER PAR 15-0646 | 2015-06-03 | Fessenheim 2 | Loss of condenser vacuum causing a turbine trip followed by a reactor trip | During normal operation, the condenser pressure increased due to an air intake into the condenser. The turbine tripped followed by an automatic reactor scram. | The direct cause was three 1mm-diameter holes compacting water seal on the common line collector. Inadequate visual check in previous maintenance was identified. | condenser,inspection,intake,pressure,automatic scram,seal,turbine trip,1 - For information only |  | EQUIPMENT FAILURE PREVENTION (ER.2); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER ATL 15-1131 | 2015-08-14 | Diablo Canyon 2 | Main Condenser High Differential Pressure Causes Planned Power Reduction | During normal operation, the main condenser differential pressure increased. The unit power was reduced to 50% to clean the condenser. | The cause was a gap between the travelling screen frame and the bottom of the screen bay. | condenser,design,differential pressure,power reduction,travelling screen,1 - For information only | SOER 2007-2 Rec 3 | DESIGN AND OPERATING MARGIN MANAGEMENT (CM.1);
Trending | N | WER ATL 15-0550 | 2015-04-02 | North Anna 1 | Main Generator Automatic Voltage Regulator Single-Point Vulnerability Contributed to a Manual Scram | During normal operation, the reactor was scrammed manually when main generator reactive output reached greater than 600 MVARs and could not be controlled automatically or manually through the automatic voltage regulator (AVR). | The cause was failure of the AVR due to a failed gate firing module (GFM). A presumed independent common supervisory power circuit for the GFMs was identified for both input power due to a design deficiency. The contributing causes were inadequate maintenance procedure for checking the power redundancy and insufficient stock of the spare part due to the design information. | circuit,design,manual scram,power supply,procedure inadequacy,single point vulnerability,spare part,turbine generator,voltage regulator |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); CONDUCT OF MAINTENANCE (MA.2);
Trending | N | WER PAR 15-0629 | 2015-03-02 | Yangjiang 1 | Multiple Crack Defects on Y1ABP (Unit Y1 Low Pressure Feedwater Heater )LP Heater, Y1GSS (Unit Y1 Moisture Separator Reheater ) Drain Tank Shell | During an outage and while carrying out magnetic particle testing, multiple cracks were found on the shell circumferential weld of low pressure feedwater heaters and moisture separator reheater drain tanks. This resulted in decrease in the equipment safety reliability during operation. | The direct cause was&nbsp;large restraint stress of the circumferential weld workpiece of the head and the shell body. The root cause was failure to make heat treatment immediately after welding and also no post heat treatment was added. The contributors were failure to perform non-destructive testing for the weld inner surface and inadequate heat treatment temperature.&nbsp; | feedwater heater,heat treatment,moisture separator reheater,weld,2 - Important lessons |  | MATERIALS RELIABILITY (ER.4);
Trending | 0 | WER PAR 15-0663 | 2015-08-14 | Dungeness B 2 | Oil Leak at Turbine 22 Bearing | During startup and while on turbine run up, oil leakage was found from pilot exciter inboard bearing. The turbine was tripped and the reactor shutdown to rectify the problem. | The cause was that axial liner of the bearing was missing after it was returned by the machining company during last outage. The root cause was that the liner was not included on the relevant drawings or work instructions. | bearing,leak,oil,reactor shutdown,turbine generator,1 - For information only |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3); MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
Trending | 0 | WER PAR 15-0658 | 2015-07-29 | Forsmark 2 | Outboard steam isolation valve 411 V6 not ready for operation increase | During unit startup activities, noise was detected from the outboard steam isolation valve. The reactor was placed back into cold shutdown for valve repairs. | The direct cause was a damaged stem nut bearing caused by thermal locking during shutdown. The underlying cause was thermal locking damage caused by the previous year's outage. | bearing,isolation valve,power reduction,steam line,1 - For information only |  | EQUIPMENT FAILURE PREVENTION (ER.2);
Trending | 0 | WER PAR 15-0653 | 2015-06-16 | Heysham B2 | Reactor 8 Make Up Shield Shear Pins Failure | During refuelling and after completing a control assembly exchange at a reactor channel, it was found that two make up shield (MUS) pressure vessel (PV) shear pins had failed. This resulted in an operability issue in terms of being able to connect the fuelling machine telescopic tube to the top of the MUS PV. | The apparent cause was inadequate preventive maintenance and incomplete maintenance procedure. | pin,preventive maintenance,procedure inadequacy,reactor vessel,1 - For information only |  | EQUIPMENT FAILURE PREVENTION (ER.2); FUELLING ACTIVITIES (FA.1);
Trending | N | WER ATL 15-1110 | 2015-01-20 | Salem 2 | Reactor Coolant Over Temperature Delta Temperature Inoperable for longer than allowable by Technical Specifications | During normal operation and following a calibration, the isolator output in a neutron monitoring channel, which is an over temperature delta temperature input setpoint, was found low and outside the technical specification allowable values. This resulted in the channel being inoperable for longer than allowable by technical specifications. | The cause was ageing due to inadequate preventive maintenance. | ageing,neutron monitor,preventive maintenance,protection system,setpoint,technical specification,1 - For information only |  | EQUIPMENT FAILURE PREVENTION (ER.2);
Trending | N | WER ATL 15-1098 | 2015-08-16 | Chalk River NRU 1 | Reactor Trip Due to Failed Thermovolt | During normal operation, the reactor automatically scrammed due to spurious alarms of fuel rod very low flow condition. | The probable cause was a short circuit and a blown fuse in the rod flow monitoring system due to deteriorated wire insulation. | ageing,alarm,flow rate,fuel rod,fuse,insulation,automatic scram,short circuit,1 - For information only |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | 0 | WER PAR 15-0650 | 2015-06-12 | Cattenom 1 | Reactor trip on very high steam generator level | During startup and while operating at 25% power, two main feedwater valves for one steam generator (SG) opened to 100% despite manual override of the valve controls, resulting in the SG water level increase. The reactor scrammed automatically and the auxiliary feedwater system actuated. | The cause was that the associated electronic boards malfunctioned. Failure of the SG level regulation led to the feedwater flow control valves opening wide. Ageing was a contributing cause. | ageing,automatic scram,regulating valve,steam generator,switchboard,1 - For information only |  | LONG-TERM EQUIPMENT RELIABILITY (ER.3);
Trending | N | WER PAR 13-0008 | 2012-06-05 | Neckar 1 | Reduced power of an emergency diesel during surveillance test | During a test run of emergency diesel generator (EDG), the start fuel delivery limitation function failed to clear resulting in the EDG not running up to full power when synchronized to the grid. | Small dirt particles resulted in the cross section of the throttle valve clogging temporarily. Detail investigations are in progress. | diesel generator,FME,throttle valve,1 - For information only |  | EQUIPMENT FAILURE PREVENTION (ER.2);
Trending | N | WER ATL 15-1120 | 2015-08-12 | Virgil C. Summer 1 | Scaffold Builder Stepped On Pipe, Slipped and Injured Himself | A contractor scaffold builder fell on a scaffold runner while stepping on a pipe, causing fractured ribs. | The cause was losing balance. Stepping on equipment was less than adequate work practice. | fracture,industrial safety,personnel injury,scaffold,1 - For information only |  | INDUSTRIAL SAFETY (IS.1);
Trending | N | WER ATL 15-1117 | 2015-06-25 | Clinton 1 | Severe Weather Caused A Momentary Loss of Offsite 138kV Source | During normal operation, a momentary loss of offsite 138 kV source occurred that resulted in tripping of the emergency reserve auxiliary transformer static&nbsp;VAR compensator and entry into a technical specification shutdown limiting condition for operation. | The apparent cause for the loss of the 138kV line was a lightning strike during severe weather. | lightning,limiting condition of operation,loss of offsite power,storm,transformer,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1);
Trending | N | WER ATL 15-1113 | 2015-06-28 | South Texas 2 | Solid State Protection System Circuit Card Failure Causes Source Range Nuclear Instrument Detectors to Unexpectedly Energize at 100% Power | During normal operation, two source range channels experienced energisation. Both channels were declared inoperable, resulting in entry into multiple technical specifications associated with automatic actuation logic including a 24 hour shutdown limiting condition of operation. | The cause was failure of a safeguard driver board in the solid state protection system logic cabinet. | circuit card,limiting condition of operation,reactor protection system,source range monitor,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1);
Trending | N | WER ATL 15-1101 | 2014-11-27 | Salem 1 | Steam Generator Feed Pump Manual Trip due to Oil Leak | During normal operation, oil leakage occurred on the main oil supply flange weld for a steam generator feed pump (SGFP). The unit power was reduced to 61% and the pump was tripped to rectify the problem. | The cause was high turbine bearing vibrations due to an imbalance associated with the turbine rotor. Inadequate maintenance procedures and processes performed during last refuelling outage resulted in higher than expected turbine bearing vibrations. | bearing,leak,oil,power reduction,turbine,vibration,2 - Important lessons |  | MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
Trending | N | WER ATL 15-1135 | 2015-05-15 | Wolf Creek 1 | Technical Specification Shutdown Due to 2 AC Inverters Inoperable | During normal operation, an electrical air conditioning unit was found tripped due to lube oil failure.This resulted in two of four trains of inverters declared inoperable requiring a technical specification plant shutdown. Load reduction was stopped at 95% power after finding that low lube oil signal was false. | The cause was that residual contaminants from a compressor replacement work entrained within the compressor sump and migrated to the lube oil sensor inlet screen resulting in a false low lube oil signal. The root cause was inadequate monitoring of compressor replacement work. | contamination,heating ventilating and air conditioning,inverter,limiting condition of operation,lube oil,supervisory oversight |  | MAINTENANCE FUNDAMENTALS (MA.1); CONDUCT OF MAINTENANCE (MA.2);
Trending | N | WER ATL 15-1127 | 2015-07-02 | Millstone 3 | Tube Leak In Component Cooling Heat Exchanger | During normal operation, a leak of 290 gallons per day developed in the component cooling water heat exchanger. A limiting condition of operation was entered. | The cause of the leak was from ageing and pitting over the long service life of the heat exchangers. The degraded condition of the tubes has been well documented in system health reports. | ageing,component cooling water,heat exchanger,leak,1 - For information only |  | EQUIPMENT PERFORMANCE (ER.1); SOLUTIONS ANALYSIS, IDENTIFICATION AND PLANNING (PI.2);
Trending | 1 | WER PAR 15-0654 | 2015-06-19 | Tricastin 4 | Unavailability of a chemical and volume control system discharge line following a unit mix-up. | During normal operation and while performing a surveillance test, the component cooling system (CC) valves were inadvertently closed for Unit 4. The CC valves supply cooling to a chemical and volume control system (CVCS) minimum-flow exchanger on the CVCS pumps. A limiting condition of operations was entered. | The cause was a line-up human error. The valve for the unit 3 and unit 4 were not physically differentiated or identifiable. | chemical volume control system,configuration control,human error,limiting condition of operation,1 - For information only |  | OPERATION CONFIGURATION CONTROL (CM.2); OPERATIONS FUNDAMENTALS (OP.1);
Trending | 1 | WER PAR 15-0638 | 2015-05-05 | Gravelines 4 | Unavailability of the reactor vessel train B level meter following inappropriate closure of reactor coolant system valves 897 and 899 | During startup and while performing surveillance tests, a reactor coolant system pressure sensor for vessel level monitoring did not meet the operating procedure requirement. An limiting condition of operations was entered. | The cause was human errors from maintenance that two associated reactor coolant system valves were closed erroneously. Deficiencies in use of error-reduction techniques, procedure adherence, and the strategy for returning the equipment to service were identified. | configuration control,human error,level instrument,limiting condition of operation,operating procedure,pressure sensor,procedure adherence,reactor coolant,1 - For information only |  | OPERATION CONFIGURATION CONTROL (CM.2); MAINTENANCE FUNDAMENTALS (MA.1);
Trending | N | WER ATL 15-1104 | 2015-07-21 | Surry 2 | Unit 2 Automatic Reactor Trip During Turbine Overspeed Circuit Testing | During startup and while conducting main turbine testing, a steam pressure spike occurred when the test keyswitch was returned to the normal position, resulting in a turbine trip and automatic reactor scram. | The direct cause was the governor valves opening with a speed error between the turbine speed and the reference. The root cause was inadequate procedure instructions of the initial plant and test conditions. A contributing cause was the movement of the limiter from 10% to 30%. | pressure tube,procedure inadequacy,automatic scram,test,turbine trip,1 - For information only |  | OPERATION CONFIGURATION CONTROL (CM.2); OPERATIONS FUNDAMENTALS (OP.1); CONDUCT OF OPERATIONS (OP.2);