<!DOCTYPE html PUBLIC "-//W3C//DTD XHTML 1.0 Transitional//EN" "http://www.w3.org/TR/xhtml1/DTD/xhtml1-transitional.dtd">

<html xmlns="http://www.w3.org/1999/xhtml">

<head id="ctl00_Head1">

<script type="text/javascript">

function CopyToClipBoard() {

var uri = document.getElementById('ctl00_cphBody_URIToCopy');

var uriValue = uri.value;

//copy to clipboard

window.clipboardData.setData('Text', uriValue);

}

</script>

<style>

table, td

{

margin-left:0;

}

.reportDetail_Formview

{

min-width:100%;

}

.reportDetail_TopMiddle p, .reportDetail_TopRight p, .reportDetail_TopLeft p

{

font-weight:bold;

color:Black;

}

.reportDetail_TopMiddle

{

width:50%;

}

.reportDetail_TopRight, .reportDetail_TopLeft

{

width:25%;

}

.reportDetail_TopRight p

{

text-align:right;

}

.reportDetail_TopLeft p

{

text-align:left;

}

.reportDetail_TopMiddle p

{

text-align:center;

}

.reportDetail_header

{

text-transform:uppercase;

color:#7c51a8;

font-size:14px;

cursor:hand;

min-width:100%;

margin-left:11px;

}

.reportDetail_lvl2header

{

text-transform:uppercase;

font-size:12px;

color:#7c51a8;

}

.reportDetail_confidentialtyNotice

{

margin-top:60px;

border:1px solid black;

font-style:italic;

text-align:center;

font-size:10px;

}

.reportDetail_CloseLink

{

float:right;

}

.reportDetail_EventInformationTable

{

width:100%;

}

.reportDetail_InformationContact

{

font-weight:bold;

}

.reportDetailEventInformation_block

{

}

.reportDetail_OECTMembreInformation

{

text-align:right;

}

.reportDetail_attachmentList li

{

list-style-type:none;

margin-left:2px;

float:left; /*for IE*/

}

.reportDetail_attachmentList li a

{

display:block;

float:left;

width:100px;

text-decoration:none;

padding:5px;

}

.reportDetail_ReportNote

{

font-style:italic;

text-align:center;

}

</style>

<title>

</title></head>

<body topmargin="0" leftmargin="0" LINK="#0066cc" VLINK="#666666" marginwidth="0" marginheight="0">

<form method="post" action="EventReportDetail.aspx?mode=print&amp;ids=16032&amp;bt=" id="aspnetForm">

<div class="aspNetHidden">

<input type="hidden" name="__VIEWSTATE" id="__VIEWSTATE" value="/wEPDwUKLTQ4Mjg4NzgyNQ9kFgJmD2QWAgIDD2QWBAIBD2QWAgIBDw8WAh4HVmlzaWJsZWhkZAIHD2QWCAIDDw8WAh8AaGRkAgUPFgQeDERhdGFTb3VyY2VJRAUJb2RzUmVwb3J0HgtfIUl0ZW1Db3VudAIBFgJmD2QWIgIDDw8WAh4EVGV4dAURV0FOTyBFdmVudCBSZXBvcnRkZAIFDw8WAh8DBRNXQU5PIEF0bGFudGEgQ2VudHJlZGQCBw8PFgIfAwUEMjAxM2RkAgkPDxYCHwMFBDAxNzlkZAILDw8WAh8DBVlOb3RpZmljYXRpb24gb2YgVW51c3VhbCBFdmVudCBEZWNsYXJlZCBCZWNhdXNlIG9mIEJyZWFrZXIgRXhwbG9zaW9uIGluIHRoZSBQcm90ZWN0ZWQgQXJlYWRkAg0PDxYCHwMFFkFya2Fuc2FzIE51Y2xlYXIgT25lIDFkZAIPDw8WAh8DBQozMS4wMy4yMDEzZGQCEw8PFgIfAwUCMDBkZAIXDw8WAh8DBQowMS4wNC4yMDEzZGQCGQ8PFgIfAGhkZAIbDw8WAh8AaGRkAh0PDxYCHwMFBE5vbmVkZAIfDxYCHwICARYCZg9kFhQCAw8PFgIfAwUWQXJrYW5zYXMgTnVjbGVhciBPbmUgMWRkAgUPDxYCHwMFBDE5NzRkZAIJDw8WAh8DBRZBcmthbnNhcyBOdWNsZWFyIE9uZSAyZGQCDQ8PFgIfAwUDUFdSZGQCEQ8PFgIfAwUWQmFiY29jayAmIFdpbGNveCAoQiZXKWRkAhUPDxYCHwMFB0JlY2h0ZWxkZAIZDw8WAh8DBQozMS4wMy4yMDEzZGQCHQ8PFgIfAwUDTi9BZGQCIQ8PFgIfA2VkZAIlDw8WAh8DBWQgTmFtZSA6ICBCb2IgQ2ltaW5lbCAsIEVtYWlsIDogIGNpbWluZWxyakB3YW5vLm9yZyAsIFBob25lIDogICsgMSA3NzAgNjQ0IDgzMTANCkZheCA6ICsxIDc3MCA2NDQgODUgZGQCIw8PFgIfAwUYVVNOUkMgRXZlbnQgUmVwb3J0IDQ4ODY5ZGQCJQ8PFgIfAGhkZAInDw8WAh8AaGRkAikPZBZMZg8VAQ1kaXNwbGF5Om5vbmU7ZAIBDw9kFgIeBVN0eWxlBQ1kaXNwbGF5Om5vbmU7ZAICDxUBDWRpc3BsYXk6bm9uZTtkAgMPD2QWAh8EBQ1kaXNwbGF5Om5vbmU7ZAIFDw8WAh8DBQNOL0EWAh8EBQ1kaXNwbGF5Om5vbmU7ZAIHDw9kFgIfBAUNZGlzcGxheTpub25lO2QCCQ8PFgIfAwUDTi9BFgIfBAUNZGlzcGxheTpub25lO2QCCw8PZBYCHwQFDWRpc3BsYXk6bm9uZTtkAg0PDxYCHwMFA04vQRYCHwQFDWRpc3BsYXk6bm9uZTtkAg8PD2QWAh8EBQ1kaXNwbGF5Om5vbmU7ZAIRDw8WAh8DBQNOL0EWAh8EBQ1kaXNwbGF5Om5vbmU7ZAIVDw8WAh8DBaoXPHNwYW4gc3R5bGU9ImZvbnQtZmFtaWx5OiB2ZXJkYW5hLHNhbnMtc2VyaWY7IGZvbnQtc2l6ZTogOXB0OyI+QXQgMDc1MCBbbG9jYWwgdGltZV0gb24gMy8zMS8yMDEzLCBkdXJpbmcgbW92ZW1lbnQgb2YgdGhlIFVuaXQgMSBNYWluIFR1cmJpbmUgR2VuZXJhdG9yIFN0YXRvciAofjUwMCB0b25zKSwgdGhlIFVuaXQgMSB0dXJiaW5lIHRlbXBvcmFyeSBsaWZ0IGRldmljZSBmYWlsZWQuIFRoaXMgY2F1c2VkIGEgbG9zcyBvZiBhbGwgb2ZmLXNpdGUgcG93ZXIgb24gVW5pdCAxLiBUaGUgQU5PIFVuaXQgMSAjMSBhbmQgIzIgRURHIFtFbWVyZ2VuY3kgRGllc2VsIEdlbmVyYXRvcl0gaGF2ZSBzdGFydGVkIGFuZCBhcmUgc3VwcGx5aW5nIEEtMyA0MTYwViBzd2l0Y2hnZWFyIGFuZCBBLTQgNDE2MFYgc3dpdGNoZ2Vhci4gUC00QSBTZXJ2aWNlIFdhdGVyIHB1bXAgYW5kIFAtNEMgU2VydmljZSBXYXRlciBwdW1wIGhhcyBiZWVuIHZlcmlmaWVkIHJ1bm5pbmcuIFVuaXQgMSBoYXMgZW50ZXJlZCBbcHJvY2VkdXJlc10gMTIwMi4wMDcgLSBEZWdyYWRlZCBQb3dlciwgMTIwMy4wMjggLSBMb3NzIG9mIERlY2F5IEhlYXQsIGFuZCAxMjAzLjA1MCAtIFNwZW50IEZ1ZWwgRW1lcmdlbmNpZXMuIFVuaXQgMSBpcyBpbiBNT0RFIDYgW1JlZnVlbGluZ10uJm5ic3A7PGJyIC8+CiZuYnNwOzxiciAvPgpBTk8tMSBlbnRlcmVkIFRTIFt0ZWNobmljYWwgc3BlY2lmaWNhdGlvbl0mbmJzcDszLjguMiBBLCAnT25lIFJlcXVpcmVkIE9mZnNpdGUgQ2lyY3VpdCBJbm9wZXJhYmxlJy4gQWxsIHJlcXVpcmVkIGFjdGlvbnMgYXJlIGNvbXBsZXRlLiBUaGUgZXZlbnQgY2F1c2VkIGEgbG9zcyBvZiBkZWNheSBoZWF0IHJlbW92YWwgb24gQU5PIFVuaXQgMSB3aGljaCB3YXMgcmVzdG9yZWQgaW4gMyBtaW51dGVzIGFuZCA1MCBzZWNvbmRzLiZuYnNwOzxiciAvPgombmJzcDs8YnIgLz4KVW5pdCAyIHRyaXBwZWQgYW5kIGlzIGluIE1PREUgMyBbSG90IFN0YW5kYnldLiBFbWVyZ2VuY3kgRmVlZCBXYXRlciB3YXMgaW5pdGlhdGVkIG9uIFVuaXQgMiBhbmQgVW5pdCAyIHdhcyBpbiBbVGVjaG5pY2FsIFNwZWNpZmljYXRpb25dIDMuMC4zIGZyb20gMDgxNyBbQ0RUXSB0byAwODQ4IFtDRFRdIGR1ZSB0byBFbWVyZ2VuY3kgRmVlZHdhdGVyLiBVbml0IDIgaXMgYmVpbmcgcG93ZXJlZCBieSBvZmYtc2l0ZS4gVW5pdCAyIFN0YXJ0dXAgMyBbdHJhbnNmb3JtZXJdIGxvY2sgb3V0IGF0IDA5MjEgW0NEVF0uIFtCdXNdIDJBMSBpcyBvbiBTdGFydCB1cCAyIFt0cmFuc2Zvcm1lcl0gYW5kIFtidXNdIDJBMyBpcyBvbiAjMiBFREcuJm5ic3A7PGJyIC8+CiZuYnNwOzxiciAvPgoxMENGUjUwLjcyIChiKSgzKShpdikoQSkgLSA0LWhyLiBub3RpZmljYXRpb24gZHVlIHRvIHRoZSBFUyBbRW5naW5lZXJlZCBTYWZlZ3VhcmQgRmVhdHVyZV0gYWN0dWF0aW9uIG9uIGJvdGggVW5pdCAxIGFuZCBVbml0IDIuIDxiciAvPgoxMENGUjUwIDcyIChiKSgyKShpdikoQikgLSA0LWhyLiBub3RpZmljYXRpb24gZHVlIHRvIFJQUyBbUmVhY3RvciBQcm90ZWN0aW9uIFN5c3RlbV0gYWN0dWF0aW9uIG9uIFVuaXQgMi4gPGJyIC8+CjEwQ0ZSNTAuNzIgKGIpKDIpKHhpKSAtIDQtaHIuIG5vdGlmaWNhdGlvbiBkdWUgdG8gR292ZXJubWVudCBOb3RpZmljYXRpb24uIDxiciAvPgoyOUNGUjE5MDQuMzlhIC0gW09TSEFdIDgtaHIuIG5vdGlmaWNhdGlvbiBkdWUgdG8gZGVhdGggb24gc2l0ZS4mbmJzcDs8YnIgLz4KJm5ic3A7PGJyIC8+CkF0IDEwMzMgW0NEVF0gb24gMy8zMS8yMDEzLCBVbml0IDIgZW50ZXJlZCBhIE5vdGlmaWNhdGlvbiBvZiBVbnVzdWFsIEV2ZW50IGJhc2VkIG9uIEVBTCBIVTQgZHVlIHRvIGRhbWFnZSBpbiAyQTEgc3dpdGNoZ2Vhci4gTm90aWZpY2F0aW9uIG9mIHRoZSBOVUUgd2lsbCBiZSBtYWRlIGxBVyBbaW4gYWNjb3JkYW5jZSB3aXRoXSBFbWVyZ2VuY3kgUGxhbiByZXF1aXJlbWVudHMuIEZvbGxvdy11cCBub3RpZmljYXRpb25zIHdpbGwgYmUgbWFkZSBhcyBhcHByb3ByaWF0ZS4iIDxiciAvPgo8YnIgLz4KQXQgdGhpcyB0aW1lLCB0aGUgZnVsbCBleHRlbnQgb2Ygc3RydWN0dXJhbCBkYW1hZ2Ugb24gVW5pdCAxIGlzIG5vdCBrbm93bi4gVGhlcmUgd2FzIG9uZSBrbm93biBmYXRhbGl0eSBhbmQgNCBrbm93biBzZXJpb3VzIGluanVyaWVzIHRvIHdvcmtlcnMuIFRoZSBsb2NhbCBjb3JvbmVyIGlzIG9uIHNpdGUgZm9yIHRoZSBmYXRhbGl0eSBhbmQgdGhlIGluanVyZWQgcGVyc29ubmVsIGhhdmUgYmVlbiB0cmFuc3BvcnRlZCBvZmZzaXRlIHRvIGxvY2FsIGhvc3BpdGFscy4gSW52ZXN0aWdhdGlvbiBpbnRvIHRoZSBjYXVzZSBvZiB0aGUgZmFpbHVyZSBhbmQgZXh0ZW50IG9mIGRhbWFnZSBpcyBvbmdvaW5nLiA8YnIgLz4KPGJyIC8+Ck9uIFVuaXQgMiwgYWxsIHJvZHMgaW5zZXJ0ZWQgZHVyaW5nIHRoZSB0cmlwLiBUaGUgY29yZSBpcyBiZWluZyBjb29sZWQgdmlhIG5hdHVyYWwgY2lyY3VsYXRpb24uIERlY2F5IGhlYXQgaXMgYmVpbmcgcmVtb3ZlZCB2aWEgc3RlYW0gZHVtcHMgdG8gYXRtb3NwaGVyZS4gVGhlcmUgaXMgbm8ga25vd24gcHJpbWFyeSB0byBzZWNvbmRhcnkgbGVha2FnZS4gPGJyIC8+CjxiciAvPgpUaGUgbGljZW5zZWUgaGFzIG5vdGlmaWVkIHRoZSBTdGF0ZSBvZiBBcmthbnNhcywgbG9jYWwgYXV0aG9yaXRpZXMsIE9TSEEgYW5kIHRoZSBOUkMgUmVzaWRlbnQgSW5zcGVjdG9yLiA8YnIgLz4KPGJyIC8+Ck5vdGlmaWVkIERIUyBTV08sIERIUyBOSUNDLCBGRU1BIGFuZCBOdWNsZWFyIE5TU0EgKHZpYSBlbWFpbCkuJm5ic3A7PGJyIC8+CiZuYnNwOzxiciAvPgpUaGUgbGljZW5zZWUgdGVybWluYXRlZCB0aGUgTk9VRSBhdCAxODIxIENEVC4gVGhlIGJhc2lzIGZvciB0ZXJtaW5hdGlvbiB3YXMgdGhhdCB0aGUgYWZmZWN0ZWQgYnVzICgyQTIpIGlzIGRlLWVuZXJnaXplZCBhbmQgbm8gb3RoZXIgZXF1aXBtZW50IG9uIFVuaXQgMiB3YXMgZGFtYWdlZC4gPC9zcGFuPmRkAhkPDxYCHwNlZGQCHQ8PFgIfA2VkZAIhDw8WAh8DZWRkAiUPDxYCHwNlZGQCKQ8WAh8CZmQCKw8WAh8CZmQCNw8WAh8CAgEWAmYPZBYCAgEPDxYCHwMFAjAxZGQCOQ8WAh8CAgEWAmYPZBYCAgEPDxYCHwMFIVNldmVyZSBvciB1bnVzdWFsIHBsYW50IHRyYW5zaWVudGRkAj0PFgIfAgICFgRmD2QWAgIBDw8WAh8DBQIwNGRkAgIPZBYCAgEPDxYCHwMFAjA3ZGQCPw8WAh8CAgIWBGYPZBYCAgEPDxYCHwMFHURlZ3JhZGF0aW9uIG9mIHNhZmV0eSBzeXN0ZW1zZGQCAg9kFgICAQ8PFgIfAwURUGVyc29uYWwgaW5qdXJpZXNkZAJDDxYCHwICAxYGZg9kFgICAQ8PFgIfAwUDMzM1ZGQCAg9kFgICAQ8PFgIfAwUDNDIwZGQCBA9kFgICAQ8PFgIfAwUDNDUwZGQCRQ8WAh8CAgMWBmYPZBYCAgEPDxYCHwMFNlNwZW50IGZ1ZWwgcG9vbCBvciByZWZ1ZWxsaW5nIHBvb2wgY29vbGluZyBhbmQgY2xlYW51cGRkAgIPZBYCAgEPDxYCHwMFIk1lZGl1bSB2b2x0YWdlIEFDICg2MDAgViB0byAxNSBrVilkZAIED2QWAgIBDw8WAh8DBSpFbWVyZ2VuY3kgcG93ZXIgZ2VuZXJhdGlvbiBhbmQgYXV4aWxpYXJpZXNkZAJJDxYCHwICAxYGZg9kFgICAQ8PFgIfAwUDNDEwZGQCAg9kFgICAQ8PFgIfAwUDNDIwZGQCBA9kFgICAQ8PFgIfAwUDNTAwZGQCSw8WAh8CAgMWBmYPZBYCAgEPDxYCHwMFW1N3aXRjaHlhcmQgZXF1aXBtZW50IChTd2l0Y2hnZWFyLCBUcmFuc2Zvcm1lcnMsIEJ1c2VzLCByZWFjdG9ycywgYXJyZXN0ZXJzLCBsaW5lIGlzb2xhdG9ycylkZAICD2QWAgIBDw8WAh8DBSdDaXJjdWl0IGJyZWFrZXJzLCBwb3dlciBicmVha2VycywgRnVzZXNkZAIED2QWAgIBDw8WAh8DBQ9MSUZUSU5HIERFVklDRVNkZAJPDw8WAh8DBQMxNjBkZAJRDw8WAh8DBUBSZWZ1ZWxsaW5nIE9wZXJhdGlvbnMgb3IgT3BlbiBWZXNzZWwgLSBBbGwgc29tZSBmdWVsIGluc2lkZSBjb3JlZGQCVQ8PFgIfAwUCOTlkZAJXDw8WAh8DBR5PdGhlciAocGxlYXNlIHNwZWNpZnkgaW4gdGV4dClkZAJbDxYCHwICAxYGZg9kFgICAQ8PFgIfAwUDMjAwZGQCAg9kFgICAQ8PFgIfAwUDMzkwZGQCBA9kFgICAQ8PFgIfAwUDNDIwZGQCXQ8WAh8CAgMWBmYPZBYCAgEPDxYCHwMFCk9QRVJBVElPTlNkZAICD2QWAgIBDw8WAh8DBRFJbmR1c3RyaWFsIFNhZmV0eWRkAgQPZBYCAgEPDxYCHwMFC0NvbnRyYWN0b3JzZGQCYQ8PFgIfAwUEMDEwMGRkAmMPDxYCHwMFFU1FQ0hBTklDQUwgREVGSUNJRU5DWWRkAmcPFgIfAmZkAmkPFgIfAmZkAm0PFgIfAmZkAm8PFgIfAmZkAgcPD2QPEBYCZgIBFgIWAh4OUGFyYW1ldGVyVmFsdWUFBTE2MDMyFgIfBWQWAgIEAgRkZAIJDw9kDxAWAWYWARYCHwUFBTE2MDMyFgECBGRkZNZ/hqojbGIVJqlaWu6OB/6k/7ftCBYVZWTReqc579Md" />

</div>

<div class="aspNetHidden">

<input type="hidden" name="__EVENTVALIDATION" id="__EVENTVALIDATION" value="/wEWAwK6jMnLBgLoksbkCgKvj+SBDhoQNYA7pMh0hXm68HfOUMQQJ5VjTXB2JHZlj+JKNqGy" />

</div>

<div>

<div class="main_body">

<input type="hidden" name="ctl00$cphBody$URIToCopy" id="ctl00_cphBody_URIToCopy" value="http://www.wano.org/OperatingExperience/OE_Database_2012/Pages/EventReportDetail.aspx?&amp;ids=16032&amp;bt=" />

<input type="hidden" name="ctl00$cphBody$rptReports$ctl00$hfReportIdentifier" id="ctl00_cphBody_rptReports_ctl00_hfReportIdentifier" value="WER ATL 13-0179" />

<table class="reportDetail_Header" style="width: 100%;">

<tbody style="width: 100%">

<tr>

<td class="reportDetail_TopLeft">

<p>

<span id="ctl00_cphBody_rptReports_ctl00_lblReportFullType">WANO Event Report</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblReportCentreFullName">WANO Atlanta Centre</span>,&nbsp;<span id="ctl00_cphBody_rptReports_ctl00_lblReportYear">2013</span>-<span id="ctl00_cphBody_rptReports_ctl00_lblReportNumber">0179</span>

</p>

</td>

<td class="reportDetail_TopMiddle">

<p>

<span id="ctl00_cphBody_rptReports_ctl00_lblFullTitle">Notification of Unusual Event Declared Because of Breaker Explosion in the Protected Area</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblReportFullUnitName">Arkansas Nuclear One 1</span>,

<span id="ctl00_cphBody_rptReports_ctl00_lblEventDate">31.03.2013</span>

</p>

</td>

<td class="reportDetail_TopRight">

<p>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextRevisionNo">Revision Number</span>

<span id="ctl00_cphBody_rptReports_ctl00_lblReportRevision">00</span>

-

<span id="ctl00_cphBody_rptReports_ctl00_lblTextPosted">Posted date</span>

<span id="ctl00_cphBody_rptReports_ctl00_lblReportPostingDate">01.04.2013</span>

<br />

</p>

</td>

</tr>

</tbody>

</table>

<div class="reportDetail_ReportNote">

<span id="ctl00_cphBody_rptReports_ctl00_lblReportNote">None</span>

</div>

<hr />

<table class="reportDetail_EventInformationTable">

<tr>

<td>

<table class="reportDetailEventInformation_block">

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextUnitAndYear">Unit (Year)</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblUnit">Arkansas Nuclear One 1</span>

(<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblYear">1974</span>)

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblAdditionalTextUnits">Additional Units</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblAdditionalUnits">Arkansas Nuclear One 2</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextReactorType">Reactor Type</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblReactorType">PWR</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextReactorManufacturer">Reactor Manufacturer</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblReactorManufacturer">Babcock & Wilcox (B&W)</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextPlantDesigner">Plant Designer</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblPlantDesigner">Bechtel</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextEventDate">Event Date</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblEventDate">31.03.2013</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextINESLevel">INES</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblINESLevel">N/A</span>

</td>

</tr>

</table>

</td>

<td class="reportDetail_OECTMembreInformation">

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextOEInformationContact" class="reportDetail_InformationContact">OE Station Information Contact</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblOEInformationContact"></span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_lblTextWanoInformationContact" class="reportDetail_InformationContact">WANO Information Contact</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_rpEvents_ctl00_Label5"> Name :  Bob Ciminel , Email :  ciminelrj@wano.org , Phone :  + 1 770 644 8310

Fax : +1 770 644 85 </span>

</td>

</tr>

</table>

<table>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextReference">Reference</span>

:

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblReference">USNRC Event Report 48869</span>

</td>

</tr>

</table>

<hr />

<br />

<br />

<br />

<br />

<div id="ctl00_cphBody_rptReports_ctl00_divOECT" class="accordion">

<div class="accordion_header" style="display:none;">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTInformation" class="reportDetail_header" style="display:none;">OECT Information</span><hr />

</div>

<div class="accordion_content" style="display:none;">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTSummary" class="reportDetail_lvl2header" style="display:none;">Summary</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTSummary" style="display:none;">N/A</span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTCauses" class="reportDetail_lvl2header" style="display:none;">Causes</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTCauses" style="display:none;">N/A</span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTKeywords" class="reportDetail_lvl2header" style="display:none;">Keywords</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTKEYWORDS" style="display:none;">N/A</span>

<br />

<br />

<span id="ctl00_cphBody_rptReports_ctl00_lblTextOECTReferences" class="reportDetail_lvl2header" style="display:none;">References</span><br />

<span id="ctl00_cphBody_rptReports_ctl00_lblOECTReferences" style="display:none;">N/A</span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextSummary" class="reportDetail_header">Summary</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_lblReportSummary"><span style="font-family: verdana,sans-serif; font-size: 9pt;">At 0750 [local time] on 3/31/2013, during movement of the Unit 1 Main Turbine Generator Stator (~500 tons), the Unit 1 turbine temporary lift device failed. This caused a loss of all off-site power on Unit 1. The ANO Unit 1 #1 and #2 EDG [Emergency Diesel Generator] have started and are supplying A-3 4160V switchgear and A-4 4160V switchgear. P-4A Service Water pump and P-4C Service Water pump has been verified running. Unit 1 has entered [procedures] 1202.007 - Degraded Power, 1203.028 - Loss of Decay Heat, and 1203.050 - Spent Fuel Emergencies. Unit 1 is in MODE 6 [Refueling].&nbsp;<br />

&nbsp;<br />

ANO-1 entered TS [technical specification]&nbsp;3.8.2 A, 'One Required Offsite Circuit Inoperable'. All required actions are complete. The event caused a loss of decay heat removal on ANO Unit 1 which was restored in 3 minutes and 50 seconds.&nbsp;<br />

&nbsp;<br />

Unit 2 tripped and is in MODE 3 [Hot Standby]. Emergency Feed Water was initiated on Unit 2 and Unit 2 was in [Technical Specification] 3.0.3 from 0817 [CDT] to 0848 [CDT] due to Emergency Feedwater. Unit 2 is being powered by off-site. Unit 2 Startup 3 [transformer] lock out at 0921 [CDT]. [Bus] 2A1 is on Start up 2 [transformer] and [bus] 2A3 is on #2 EDG.&nbsp;<br />

&nbsp;<br />

10CFR50.72 (b)(3)(iv)(A) - 4-hr. notification due to the ES [Engineered Safeguard Feature] actuation on both Unit 1 and Unit 2. <br />

10CFR50 72 (b)(2)(iv)(B) - 4-hr. notification due to RPS [Reactor Protection System] actuation on Unit 2. <br />

10CFR50.72 (b)(2)(xi) - 4-hr. notification due to Government Notification. <br />

29CFR1904.39a - [OSHA] 8-hr. notification due to death on site.&nbsp;<br />

&nbsp;<br />

At 1033 [CDT] on 3/31/2013, Unit 2 entered a Notification of Unusual Event based on EAL HU4 due to damage in 2A1 switchgear. Notification of the NUE will be made lAW [in accordance with] Emergency Plan requirements. Follow-up notifications will be made as appropriate." <br />

<br />

At this time, the full extent of structural damage on Unit 1 is not known. There was one known fatality and 4 known serious injuries to workers. The local coroner is on site for the fatality and the injured personnel have been transported offsite to local hospitals. Investigation into the cause of the failure and extent of damage is ongoing. <br />

<br />

On Unit 2, all rods inserted during the trip. The core is being cooled via natural circulation. Decay heat is being removed via steam dumps to atmosphere. There is no known primary to secondary leakage. <br />

<br />

The licensee has notified the State of Arkansas, local authorities, OSHA and the NRC Resident Inspector. <br />

<br />

Notified DHS SWO, DHS NICC, FEMA and Nuclear NSSA (via email).&nbsp;<br />

&nbsp;<br />

The licensee terminated the NOUE at 1821 CDT. The basis for termination was that the affected bus (2A2) is de-energized and no other equipment on Unit 2 was damaged. </span></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextDecription" class="reportDetail_header">Description</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label1"></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextConsequences" class="reportDetail_header">Consequences</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label2"></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextAnalysisComments" class="reportDetail_header">Analysis/Comments</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label3"></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCorrectiveActions" class="reportDetail_header">Corrective Actions</span><hr />

</div>

<div class="accordion_content">

<span id="ctl00_cphBody_rptReports_ctl00_Label4"></span>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextAttachments" class="reportDetail_header">Attachments</span><hr />

</div>

<div class="accordion_content">

<ul class="reportDetail_attachmentList">

</ul>

<ul class="reportDetail_attachmentList">

</ul>

<br />

</div>

<br />

<div class="accordion_header">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCoddedFields" class="reportDetail_header">Coded Fields</span><hr />

</div>

<div class="accordion_content">

<table style="text-align: left">

<tr style="text-align: center">

<th>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCdArrayField1" class="reportDetail_lvl2header">Field</span>

</th>

<th>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCdArrayField2" class="reportDetail_lvl2header">Code</span>

</th>

<th>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCdArrayField3" class="reportDetail_lvl2header">Description</span>

</th>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDCategory" class="reportDetail_lvl2header">Category</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptCategoryCodes_ctl00_lblCategoryCode">01</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptCategoryDescriptions_ctl00_lblCategoryDescription">Severe or unusual plant transient</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDConsequences" class="reportDetail_lvl2header">Consequences</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptConsequenceCodes_ctl00_lblConsequenceCode">04</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptConsequenceCodes_ctl02_lblConsequenceCode">07</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptConequenceDescriptions_ctl00_lblConsequenceDescription">Degradation of safety systems</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptConequenceDescriptions_ctl02_lblConsequenceDescription">Personal injuries</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDSystems" class="reportDetail_lvl2header">Systems</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemCodes_ctl00_lblSystemCode">335</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemCodes_ctl02_lblSystemCode">420</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemCodes_ctl04_lblSystemCode">450</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemDescrptions_ctl00_lblSystemDescription">Spent fuel pool or refuelling pool cooling and cleanup</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemDescrptions_ctl02_lblSystemDescription">Medium voltage AC (600 V to 15 kV)</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptSystemDescrptions_ctl04_lblSystemDescription">Emergency power generation and auxiliaries</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDComponents" class="reportDetail_lvl2header">Components</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentCodes_ctl00_lblSystemCode">410</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentCodes_ctl02_lblSystemCode">420</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentCodes_ctl04_lblSystemCode">500</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentDescriptions_ctl00_lblComponentDescription">Switchyard equipment (Switchgear, Transformers, Buses, reactors, arresters, line isolators)</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentDescriptions_ctl02_lblComponentDescription">Circuit breakers, power breakers, Fuses</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptComponentDescriptions_ctl04_lblComponentDescription">LIFTING DEVICES</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDStatus" class="reportDetail_lvl2header">Status</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblStatusCode">160</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblStatusDescription">Refuelling Operations or Open Vessel - All some fuel inside core</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDActivity" class="reportDetail_lvl2header">Activity</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblActivityCode">99</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblActivityDescription">Other (please specify in text)</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDGroup" class="reportDetail_lvl2header">Group</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupCodes_ctl00_lblGroupCode">200</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupCodes_ctl02_lblGroupCode">390</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupCodes_ctl04_lblGroupCode">420</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupDescriptions_ctl00_lblGroupDescription">OPERATIONS</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupDescriptions_ctl02_lblGroupDescription">Industrial Safety</span>

<br />

<span id="ctl00_cphBody_rptReports_ctl00_rptGroupDescriptions_ctl04_lblGroupDescription">Contractors</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDDirectCause" class="reportDetail_lvl2header">Direct Cause</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblDirectCauseCode">0100</span>

</td>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblDirectCauseDescription">MECHANICAL DEFICIENCY</span>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDRootCause" class="reportDetail_lvl2header">Root Cause</span>

</td>

<td>

</td>

<td>

</td>

</tr>

<tr>

<td>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextCDCausalFactor" class="reportDetail_lvl2header">Causal Factor</span>

</td>

<td>

</td>

<td>

</td>

</tr>

</table>

<br />

</div>

</div>

<div class="reportDetail_confidentialtyNotice">

<span id="ctl00_cphBody_rptReports_ctl00_lblTextConfidentialityNotice1">CONFIDENTIALITY NOTICE: Copyright  1987-2012 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale or commercial use. This document is protected as an unpublished work under the copyright laws of all countries which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. This document and its contents are confidential and shall be treated in strictest confidence. In particular, except with the prior written consent of the WANO Coordinating Centre, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations.<br/><br/>

LIABILITY DISCLAIMER NOTICE: This information was prepared in connection with work sponsored by the WANO. Neither WANO, WANO members, nor any person acting on the behalf of them (a) makes warranty or representation, expressed or implied, with respect to the accuracy, completeness, or usefulness of the information contained in this document, or that use of any information, apparatus, method or process disclosed in this document may not infringe on privately owned rights, or (b) assumes any liabilities with respect to the use of, or for damages resulting from the use of any information, apparatus, method, or process disclosed in this document.</span>

<span id="ctl00_cphBody_rptReports_ctl00_lblTextConfidentialityNotice2"></span>

</div>

</div>

</div>

</form>

</body>

</html>