## Significant
OE Reports
Event Summary (Monthly by Significance)
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 16-0079 | 2016-03-11 | 2016-03-15 11:59 | Kakrapar-1 | #PRELIMINARY# Reactor trip on ‘Pump Room pressure very high’ due to leakage from the Primary Heat Transport (PHT) System. | Significant | During normal operation, the reactor scrammed automatically on primary heat transport (PHT) pump room pressure very high condition. A reduction in PHT system pressure resulted in initiation of emergency core cooling system (ECCS) and both high pressure heavy water and medium pressure light water injection took place. Subsequently, long term recirculation mode of ECCS got established. The event is classified as Significant due to a small loss of coolant accident which resulted in a reactor scram and initiation of ECCS with declaration of plant emergency. | The cause was leakage of heavy water likely from a pressure tube in the PHT system. |  | 2 - Important lessons, automatic scram, emergency core cooling system, emergency plan, leak, loss of coolant accident, pressure tube | ER.4
WER TYO 15-0011 | 2014-12-26 | 2016-03-10 23:53 | Shin-Kori-3 | Mortality accident caused by Equipment Drain Tank cover gas (Nitrogen) leak | Significant | During plant construction, three contractor workers died of hypoxia (lack of oxygen) due to nitrogen leakage from an equipment drain tank (EDT) vent valve in the auxiliary building. This event is classified as Significant as it caused three fatalities. | The root causes include deficiency in the EDT valve manufacturing and assembling, lack of risk assessment in a confined space, improper access control and stopping of ventilation fans. The contributing causes were inadequate work control during construction and insufficient training of the health and safety environment team. |  | 2 - Important lessons, confined space, contractor, fatality, industrial safety, leak, management oversight, nitrogen, vent valve | ER.3 , IS.1
WER PAR 16-0185 | 2014-04-09 | 2016-03-16 08:33 | Fessenheim-1 | Reactor taken from power operations to cold shutdown conditions as a result of on-site flooding | Significant | During normal operation, a closed cooling water system tank overflowed flooding the switchgear rooms. This caused a number of faults on one train of reactor protection system (RPS) including unavailability of containment pressure sensor, ground fault on 125 V DC power system, failure of rod movement and unavailability of a rectifier. This resulted in entry into a combination of limiting conditions of operation (LCO). The reactor power was reduced using boron as the control rods were stuck. Average reactor coolant temperature dropped below its technical specification limit for power operation. The event is classified as Significant because it resulted in unavailability of one train of RPS, inability to move control rods, entry into a number of LCOs requiring reactor shutdown and potential for common mode failure of multiple trains of safety related equipment. (Note the manual scram function was not impacted.) | The cause was overflowing of a tank into a common manifold which was blocked by large amounts of debris due to corrosion inside the pipes. This caused pipes to fill up and resulted in water flooding the room housing the electrical building and control room main ventilation system. Openings that were designed to be leak tight failed and allowed water to flow from the control room level down to the electrical rooms. | SOER 2013-1 Rec 3 | 2 - Important lessons, control rod, cooling water, flood, limiting condition of operation, reactor protection system, reactor shutdown, switchgear, valve | ER.1 , OP.1
WER PAR 15-0617 | 2014-10-29 | 2016-03-23 05:21 | Almaraz-1 | Doubts regarding the safety function of the emergency Diesel generators associated with safeguards busbars | Significant | After checking emergency diesel generator (EDG) operability tests conducted during a previous outage, it was noticed that an instrument air compressor did not disconnect from a safety busbar before the diesel was coupled as designed while safety injection signal and undervoltage at the safety busbar were coincident. This resulted in EDG functional failure. This event is classified as Significant because all EDGs were inoperable due to the same cause and this was identified two months after the tests. | The direct cause was inadequate coordination between the activation times of the relays which coupled the diesel generators to the safeguards busbars, and the undervoltage relays of the power units that initiated load disconnections. The test results from 9 and 12 August were incorrectly analysed. |  | 2 - Important lessons, bus bar, design criteria / design basis, diesel generator | CM.1 , EN.1 , OP.2 , SC.1
WER ATL 15-0945 | 2015-05-21 | 2016-03-07 10:45 | Donald Cook-1 | Emergency Diesel Generator Bearing Failure Results in Technical Specification Required Shutdown | Significant | During a post maintenance test run following lube oil system maintenance, a diesel generator tripped due to high bearing temperature. This event is significant because it resulted in a technical specification required shutdown and an extended forced outage of 50 days to return the diesel engine to operable. | The direct cause was main bearing failure. The root cause was that the station failed to recognize the adverse impacts of leaving air within the lube oil system which degraded the hydrodynamic film wedge and resistive capacity of the #4 main bearing leaving it susceptible to electrical pitting and eventual wiping of the bearing babbitt material through shaft induced currents. Deficiencies in challenging the unknown and conservative decision making were contributors. | SOER 2002-2 Rec 2 | 2 - Important lessons, bearing, diesel engine, diesel generator, lube oil, reactor shutdown, safety culture, technical specification | EN.1 , MA.2

## Noteworthy
OE Reports
Event Summary (Monthly by Significance)
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 16-0072 | 2015-10-29 | 2016-03-02 19:07 | Karachi-1 | Sudden Forced Shutdown of Plant due to Minor Steam Generator Tube Leakage | Noteworthy | During normal operation, the increased concentration of tritium in the steam samples indicated suspected steam generator tube leakage. The unit was shut down and an unplanned outage of about 12 days was needed. This event is Noteworthy because of secondary barrier degradation and long duration of forced outage. | The cause was 4 leaky tubes in 2 SGs. The apparent cause was attributed to pitting and wastage wall thinning occurring under sludge above the tube sheet in the hot leg region. Sludge formation had been occurring for the last few years. Another possible reason was old tube plug welding techniques (welding of plug with tube) presented the risk of leakage. |  | 2 - Important lessons, ageing, chemical control, leak, plug, reactor shutdown, sludge, steam generator tube, weld | CY.2, ER.4, PI.2
WER TYO 16-0070 | 2015-11-12 | 2016-03-02 02:57 | Maanshan-2 | The Number 40th Reactor Vessel Closure Stud Stuck | Noteworthy | During an outage and while opening the reactor vessel head closure, a stud stuck while approximately half of the total length of thread engagement in the vessel flange remained in the hole. After removing of the stuck stud by sawing, drilling and CNC milling, and a review of damage threads form images, the number of damaged stud hole threads was determined. The event extended the outage by thirty days for repair and additional dose 133 mSv to fabrication crew members. This event is classified as Noteworthy due significant outage duration and collective dose received during the repair. | The cause was the collision damage of stud bottom thread and the first thread of the vessel flange hole. Threads wear gradually and accumulated severe abrasion caused the stud galling. There was a lack of visual inspection for stud thread abrasion. |  | 2 - Important lessons, reactor vessel head | ER.1, MA.1
WER PAR 16-0168 | 2015-10-19 | 2016-03-03 08:28 | Olkiluoto-1 | Open Penetrations in Containment during work on Recirculation Pumps | Noteworthy | During an outage and while carrying out repair and replacement projects for penetrations located in the containment, the risk related to open penetrations was not taken into account as concerns of potential bottom leaks in the reactor pressure vessel. A leak that could not have been isolated had it occurred below the upper level of the fuel. This event is Noteworthy as the risk of losing primary coolant was unnoticed in the project design. | The requirement is that penetrations must be closed in connection with the maintenance of recirculation pumps, and when leak-tightness is based on one seal; has not been taken into account and incorporated into procedures and maintenance work practices. |  | 2 - Important lessons, configuration control, flood, penetration, seal, technical specification | EN.1, OF.2, WM.1
WER PAR 16-0148 | 2015-04-21 | 2016-03-01 08:50 | Asco-2 | Unprogrammed shutdown due to anomalies in some of the support plate bolts in the air intake piping to the Emergency Diesel Generators | Noteworthy | During normal operation, 21 anchor bolts on the train A emergency diesel generator (EDG) and 12 bolts on the train B EDG were found not to comply with the required tightening torque acceptance criterion. This might affect the EDG capacity to meet its safety function in the case of an earthquake. Both EDGs were declared inoperable but available and the unit shutdown sequence was initiated. This event is classified as Noteworthy due to inoperability on both EDGs. | The root cause was the bolt installation instructions were not followed during original construction. A contributing cause was the documentation for use of expansion bolts was not updated and inadequate to meet the current specification. |  | 2 - Important lessons, bolt, diesel generator, procedure adherence, procedure inadequacy | ER.2, MA.1
WER PAR 16-0145 | 2015-12-01 | 2016-03-01 07:07 | Cruas-2 | Unavailability of spent fuel cooling system PTR due to an isolated heat exchanger | Noteworthy | During a refuelling outage and while changing the line-up of spent fuel pool cooling heat exchangers from parallel to series configuration, a component cooling system valve was not opened by mistake. Wile field operator was making line-up when he was about to operate valve RRI200VN, he heard a public address message from the control room. He interrupted his activity and called the control room. When he resumed his activity and the line-up procedure, he was convinced that he had opened valve RRI200VN, which he marked as open in the line-up procedure. This resulted in loss of spent fuel pool cooling for about six hours and increase in the pool temperature to 36.6 degree C. This event is classified as Noteworthy because of loss of cooling of the spent fuel. | The causes were inadequate use of error reduction tools, lack of pre-job brief, procedure deficiency (the line-up procedure did not stipulate that a physical parameter representative of the presence of component cooling flow on the heat exchangers should be checked) and lack of communication. | SOER 2013-1 Rec 3 | 1 - For information only, configuration control, fuel pool cooling, human error, procedure inadequacy, valve | CM.2, OP.1, OP.2
WER PAR 15-0321 | 2015-02-03 | 2016-03-02 | Vandellòs-II-2 | Unplanned automatic actuation of the Reactor Protection System due to the loss of the 400 kV line | Noteworthy | During normal operation, the grid transient due to a strong wind caused the single phase trip of the 400 kV line and led to a current phase unbalance which was compensated by current going through the main transformer neutral. The current caused an induction in the control cables which led to the actuation of the unit auxiliary transformer's Buchholz relay. This caused 400 kV breakers to open and the turbine to trip and the reactor to scram. Similar events has occurred in the past. This event is Noteworthy because at least four reactor scrams have resulted from one problem. | The direct cause for the reactor scram was the automatic actuation of the electrical protection system. The ground fault associated with the trip channel circuit of the Buchholz relay was considered to be the most likely root cause. Lack of shielding of the control and protection cables of the main transformers and the unit auxiliary transformer and incompletely performed condition expansion of a prior root cause analysis were the other root causes. | SOER 1999-1 Rec 5 | 2 - Important lessons, automatic scram, grid, ground fault, relay, transformer, turbine trip | ER.1, ER.3, PI.3
WER PAR 15-0247 | 2014-08-13 | 2016-03-02 07:38 | Asco-2 | Shutdown sequence started due to inoperability of charging pump "A" | Noteworthy | During normal operation, the pressure at the discharge of the operating charging pump decreased progressively. The charging pump was declared inoperable and, since another charging pump had been inoperable for more than a year, the reactor was shutdown in accordance to technical specifications. This event is classified as Noteworthy because it resulted in a 25 day reactor shutdown for repair and redundancy of safety injection was degraded. | The direct cause was a crack in the shaft area between the last stage impeller and the balance drum whilst due to high cycle stress fatigue. The root causes were failure to use operating experience. The shaft had been installed in the pump for 22 years, and had been in operation intermittently (1 out of every 3 months). It was identified the existence of three external operating experience reports, where the shaft failures of several similar charging pumps were analysed. These documents concluded that the shafts had failed as a result of having been subjected to an overload exceeding the design value, and recommended they be replaced with a new design shaft made from a different material, providing higher fatigue strength. | SOER 2003-2 Rec 3b | 2 - Important lessons, charging pump, crack, impeller, limiting condition of operation, pump shaft, reactor shutdown, technical specification | OE.1, OF.2, OP.2
WER ATL 16-0281 | 2016-02-13 | 2016-03-22 15:03 | Pickering-B8 | Failure of Fuel Transfer Mechanism Unloading Ram to Fully Extend at Elevator Resulting in Pair of Irradiated Fuel Bundles in Air for Short Period | Noteworthy | During normal operation and while sending the first pair of irradiated fuel bundles to the irradiated fuel bay (IFB), the fuel transfer mechanism (TM) unloading ram stalled. The event resulted in a pair of fuel bundles in air for approximately 14 minutes. The event is classified as Noteworthy because of potential for fuel damage due to loss of cooling. | The cause was incorrect throttled position of the ram bleed off valves. The apparent causes were lack of monitoring and testing of the fuel TM unloading ram (after the initial set-up, the Ram is not monitored for the bleed off valve positions or speeds during normal operation or after Fuel TM maintenance) and inadequate operations and maintenance procedures (the procedures for setting up the Fuel TM Unloading Ram hydraulic system and speeds contained inconsistent and lacking information). |  | 2 - Important lessons, fuel handling, procedure inadequacy, refuelling, valve misposition | FA.1
WER ATL 16-0262 | 2015-04-24 | 2016-03-16 13:12 | Sequoyah-1 | Surveillance Capsule Failure | Noteworthy | During an outage and while searching for loose parts in the core, two irradiated specimen capsules were found broken and debris was identified on the bottom nozzles of fuel assemblies, on the lower core plate and in the lower plenum of the reactor pressure vessel. The loose part alarm had been activated in the previous operating cycle. This event is Noteworthy as the damaged components in the core increase the risk of fuel damage. | The direct cause was that the irradiated specimen capsules were not properly seated in their storage baskets during the relocation in the previous outage. The root cause was inadequate workmanship and vendor procedures. Contributing causes were insufficient oversight and risk assessment. |  | 2 - Important lessons, alarm, foreign material, installation, procedure inadequacy, vendor | MA.1, MA.2
WER ATL 16-0261 | 2016-03-06 | 2016-03-15 15:49 | Oconee-1 | #PRELIMINARY# Unit 1 Main Transformer Fire - Emergency Classification | Noteworthy | During normal operation, a fire on the main step-up transformer resulted in opening of the power circuit breakers and reactor scrammed automatically. The fire was extinguished in 30 minutes with the help of an offsite fire department. An alert was declared when it was discovered that an overhead transmission line had contacted a switchyard emergency bus line. The event is classified as Noteworthy because it resulted in damage to the main transformer, automatic reactor scram and declaration of emergency. | The cause is under investigation. |  | 2 - Important lessons, automatic scram, emergency plan, fire, transformer | ER.1
WER ATL 16-0254 | 2015-11-23 | 2016-03-14 13:39 | Darlington-3 | Odd Shutoff Rod Bank Drove 5% Out of Core during Moderator Refill | Noteworthy | During an outage and while performing the moderator filling procedure, the operator incorrectly selected the auto drive mode for the hand switch of a shutoff control rod bank instead of the required manual drive mode. This caused a bank of 16 shutoff rods to drive out of core by 5% and a reactivity management event. The event is Noteworthy because it led to unexpected extraction of 16 out of 32 shutoff rods and the error was not identified immediately but only while manipulating another rod. | The direct cause was human error. The apparent causes were deficiencies in the conduct of just in time training, procedure adherence and supervisory oversight. Inadequate training documents, insufficient use of human performance tools and procedure deficiencies contributed to the event. | SOER 2007-1 Rec 1, 2; SOER 2013-1 Rec 3 | 1 - For information only, control rod, human error, management oversight, procedure adherence, procedure inadequacy, reactivity management | OP.1, OP.2, TR.1
WER ATL 16-0233 | 2015-04-06 | 2016-03-07 14:20 | Prairie Island-1 | Maintenance Outage for Reactor Coolant Pump Seal Repairs | Noteworthy | During normal operation and after a second outage due to external leakage from a reactor coolant pump (RCP) seal, pressure was found decreasing across a RCP seal. The unit was shut down to investigate. The event is classified as Noteworthy because a 34-day outage was required to rectify the problem. See also WER ATL 16-0232 and WER ATL 15-0401. | The cause was foreign material contamination due to inadequate foreign material exclusion strategy. The other cause was inadequate design of the seal, susceptible to debris intrusion. |  | 2 - Important lessons, design criteria / design basis, FME, foreign material, reactor coolant pump seal | ER.3, MA.2, PI.2
WER ATL 16-0232 | 2015-01-26 | 2016-03-07 14:13 | Prairie Island-1 | Planned Outage Required Due to Reactor Coolant Pump Seal Leakage | Noteworthy | The unit was shut down due to external leakage from a reactor coolant pump (RCP) seal. This event is Noteworthy because repair resulted in an 18-day outage. There were previous outage required 17 days caused by an RCP seal failure (WER ATL15-0401 and see also WER ATL 16-0233) | The direct cause was foreign material in all three stages in the RCP seal. The root cause was failing to implement foreign material intrusion prevention, and no flush activity and inspections were performed following the fabrication and installation of a new seal bypass line. A contributing cause was a flow path for foreign material was generated due to the RCP Motor axial movement during start-up. |  | 2 - Important lessons, bypass valve, debris / crud, foreign material, leak, modification, reactor coolant pump, seal | MA.1, PI.2

## Trending
OE Reports
Event Summary (Monthly by Significance)
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 16-0093 | 2015-11-10 | 2016-03-24 00:36 | Kaiga 1 | Manual reactor trip due to inoperability of Secondary Shutdown System solenoid valves | Trending | During operation at 70% power after startup and while performing the secondary shutdown system test, two solenoid valves did not close. The reactor was manually scrammed. | The cause was boron deposits on the valve seat due to minor passing of the valves because of degradation of plunger assembly elastomers. The root cause was lack of preventive maintenance programme on elastomers. |  | 1 - For information only, leak, manual scram, preventive maintenance, reactor protection system, solenoid valve | ER.2
WER TYO 16-0092 | 2015-06-05 | 2016-03-23 04:05 | Tarapur-2 | Reactor scram on Power Range Monitor high flux during startup | Trending | During startup after an outage, the reactor scrammed on power range monitor (PRM) high flux. As a consequence, the startup was delayed for about one day. | The cause was the spurious PRM signals due to noise pick up during operation of insert/withdraw switch and certain selector switches of the control rod drives. |  | 1 - For information only, automatic scram, monitor, neutron flux | ER.3
WER TYO 16-0091 | 2016-01-26 | 2016-03-23 03:39 | Shin-Wolsong-2 | Digital Plant Protection System Trip due to Fail Low of the Ex-core Neutron Flux Monitoring System Output Power | Trending | During normal operation, linear power and log power of the ex-core neutron flux monitoring system(ENFMS) channel C suddenly failed to low power resulting in actuation of four trip functions in the digital plant protection system. The same failure occurred again 25 days later. The event resulted in entry into a limiting condition of operation. | The root cause was loose connection in the pin connector of the safety channel drawer. The contributing cause was inadequate inspection procedure for the pin connector after surveillance test for the ENFMS. |  | 1 - For information only, digital control system / digital components , inspection, limiting condition of operation, neutron flux, neutron monitor, procedure inadequacy, reactor protection system | ER.2 , ER.3
WER TYO 16-0090 | 2016-01-19 | 2016-03-23 01:53 | Hanul-1 | Unplanned reactor shut down during functional test for emergency shutdown logic | Trending | During normal operation and while performing safety feature functional test, the abnormal safety injection signal occurred due to an unexpected main seam isolation valve (MSIV) closure. This resulted in the turbine trip and an automatic reactor scram. | The direct cause was a short-circuit between internal contacts of 48 VDC monitoring relay due to a manufacturing defect, causing the relay actuation and closing signal of MSIV. There was no preventive maintenance regarding the insulation resistance measurement and inspection between internal contacts of relay. |  | 1 - For information only, automatic scram, insulation, main steam isolation valve, preventive maintenance, relay, short circuit, turbine trip, vendor | ER.2 , ER.3
WER TYO 16-0089 | 2016-01-22 | 2016-03-23 01:33 | Shin-Kori-1 | Failure of Auxiliary Feedwater Pump Surveillance Test | Trending | During normal operation and while performing a surveillance test, the differential pressure across a turbine driven auxiliary feedwater pump (TDAFP) was found less than the technical specification limit. The event resulted in entry into a limiting conditions for operation. | The direct cause was inappropriate adjustment of the governor of the TDAFP. The root cause was absence of step about the adjustment of governor link in the maintenance procedure. |  | 1 - For information only, auxiliary feedwater pump, limiting condition of operation, procedure inadequacy | MA.2
WER TYO 16-0088 | 2016-01-07 | 2016-03-22 20:54 | Maanshan-2 | The Leakage on Core Exit Thermocouple Columns Penetration #G3 | Trending | During startup and while performing the leakage inspection for core exit thermocouples (CET), leakage was identified at a CET penetration. The outage delayed for 55 hours for the repairs. | The direct cause was the cleanness of major sealing surface of the CET was not confirmed. The training received by the maintenance technician had been insufficient. |  | 1 - For information only, foreign material, leak, penetration, reactor vessel, seal, thermocouple | MA.1
WER TYO 16-0078 | 2015-12-13 | 2016-03-11 03:49 | Hanul-2 | Power Reduction for Maintenance on Sea Water Pipe for Condenser Tube Cleaning System | Trending | During normal operation, differential pressure in one of the six strainers of the condenser tube cleaning system increased due to foreign material. The power was reduced to 60% for repairs. | The cause was the detachment of anti-corrosive rubber linings. A rubber's life span was reached due to the long term usage of it (25 years). |  | 1 - For information only, ageing, circulating water, condenser, corrosion, foreign material, power reduction, strainer | ER.3
WER TYO 16-0074 | 2015-12-24 | 2016-03-08 03:04 | Hanbit-6 | CO2 spray of the fire protection system in the EDG-A room | Trending | During an outage and while performing an emergency diesel generator (EDG) test, fire alarm was activated by the malfunction of the CO2 spray manual switch of fire protection system. CO2 sprayed in the EDG oil day tank room and the EDG shut down automatically. | The cause was malfunction of a control card due to external electronic noise. |  | 1 - For information only, carbon dioxide, circuit card, diesel generator, fire alarm, fire detector | ER.1
WER PAR 16-0186 | 2016-02-20 | 2016-03-18 09:10 | Ringhals-1 | Tripping of the turbine generator unit 12 due to failure to maintain the house load operation. | Trending | During normal operation, the distance protection for 400kV power lines was disconnected due to a short circuit, causing the unit being isolated from the grid and switched over to house load. Shortly after, the generator tripped on over frequency. The emergency diesel generators started. | The cause of tripping the generator was the settings of the frequency limit in the generator control system had a narrow bandwidth. The vendor had used their own standard that did not meet the current requirements. |  | 1 - For information only, diesel generator, setpoint, short circuit, turbine generator, turbine trip, vendor | CM.1
WER PAR 16-0181 | 2015-11-07 | 2016-03-10 06:57 | Hongyanhe-1 | Severe Weather Caused Unavailability of 500kV Outgoing Lines and 220kV Auxiliary Offsite Power Incoming Lines | Trending | While Unit 1 and 3 were operating at 76% power with Unit 2 in shutdown and Unit 4 in commissioning phase without fuel loading, freezing rain caused fracture of some transmission lines. This resulted in tripping of all 220 kV lines and one 500 kV line. Unit 1, 2 and 3 lost auxiliary offsite power and entered limiting condition of operation. The power supplies for Unit 1, 2 and 3 remained available through main transformers. Unit 4 lost offsite power because its main transformer was in maintenance. | The cause was covering of transmission lines with ice due to freezing rain and strong wind, which resulted in broken lines. No de-icing/ice melting devices were provided on the lines and all the lines were under the same external environment conditions. The risk for common mode failure existed. | SOER 1999-1 Rec 1, SOER 2002-1 Rec 1 | 2 - Important lessons, common mode failure, design criteria / design basis, ice, limiting condition of operation, loss of offsite power, transmission line | CM.1 , OE.1
WER PAR 16-0180 | 2015-11-03 | 2016-03-10 05:27 | Ringhals-2 | External fuel leakage due to crack in fuel leakage return pipes of one Emergency Diesel | Trending | During an outage, the test run of an emergency diesel generator (EDG) identified an external fuel leakage from one of the leakage return pipes. During the exchange of the tube, the EDG was declared inoperable. | The cause was wrong method had been used to install the pipe which consequently led to the crack and fuel leakage. | SOER 2002-2 Rec 2 and 6 | 1 - For information only, crack, diesel generator, leak | MA.1
WER PAR 16-0178 | 2015-09-14 | 2016-03-09 11:22 | Dungeness-B2 | Unplanned Unavailability of Essential Diesel Generator (EDG) 21 | Trending | During normal operation, and while performing an essential diesel generator (EDG) test, the EDG failed in two occasions. It resulted in entry into a limiting condition of operations. The EDG was unavailable for 40 days. | The first test failed due to a problem with a turbocharger. Subsequently numerous faults were identified. The direct cause was a faulty capacitor within the DC Power Supply Unit. The root causes were inadequate design and ageing of equipment. |  | 1 - For information only, ageing, capacitor, design criteria / design basis, diesel generator | CM.1 , ER.3 , MA.1
WER PAR 16-0176 | 2015-09-15 | 2016-03-09 04:56 | Olkiluoto-1 | Performance of Periodic Testing required in Technical Specifications on an Inactive System, version 2 | Trending | During a modification, a sampling pump for the iodine activity monitoring was shut and the flow to the sampling filters were interrupted. This condition was not noticed by the laboratory technician, resulting in three consecutive weekly samples without flow passing through. As a consequence, the technical specification requirements were not met. | The cause was chemistry procedures were not accurately updated during the modification review and approval process. Additionally technicians failed to check pressure prior to the laboratory sampling. | SER 2005-3 | 1 - For information only, chemistry, iodine, modification, procedure adherence, technical specification | CM.2 , CM.3 , CY.1
WER PAR 16-0165 | 2015-12-06 | 2016-03-03 07:32 | Dungeness-B2 | Fire Alarms on Back-up Diesel unavailable but not tracked via the Central Control Room (CCR) | Trending | The water spray fire system for a back up diesel generator was found isolated as part of a fuel tank isolation without entry into the required technical specification limiting condition of operation. | The direct cause was deficiency in safety document as the requirement for entry into a limiting condition of operation was not included. The root cause was ineffective independent check. The contributing cause was unclear wording in the safety document. |  | 1 - For information only, fire protection, human error, procedure inadequacy, technical specification | OP.1 , OP.2
WER PAR 16-0161 | 2016-01-02 | 2016-03-03 05:18 | Doel-1 | Scram Doel 1 due to loss of excitation alternator. | Trending | During normal operation after a long shutdown, the excitation current of the alternator decreased and the MVAR production varied appreciably (about 3 minutes within approximately + 70 MVAR to - 86 MVAR). This resulted in activation of protection on asynchronous operation of the alternator and consequently the turbine tripped. The reactor scrammed automatically. | The root cause was a wiring error made during replacement of a transmitter (the polarity was reversed from the output signal of the inverter towards the excitation control system). The contributing cause was deficiency in implementation of modification process. The initial design was changed by one person without independent check. | SER 2005-3 | 1 - For information only, automatic scram, exciter, human error, modification, turbine trip, wiring | CM.3 , MA.1
WER PAR 16-0159 | 2015-10-29 | 2016-03-03 04:36 | Olkiluoto-2 | Subsystem C DieseI Busbar Voltage loss during Synchronisation 29/10/2015 | Trending | During normal operation and while performing a test, a diesel generator breaker was synchronised with the busbar at the wrong generator frequency. This resulted in opening of the generator breaker and both transformer supply breakers. A 6.6 KV bus bar had no voltage for about 1.5 hours and the systems effected were restored manually from other bus bar. | The cause was human error during synchronisation, which caused a high-current fault at the generator and activated generator differential protection and 6.6 KV bus bar overcurrent protection. The contributing cause was entry of a person in the control room just before synchronisation, which disturbed the concentration of the operator. |  | 1 - For information only, diesel generator, emergency bus, human error, synchroscope | OP.1
WER PAR 16-0156 | 2015-12-25 | 2016-03-01 11:02 | Heysham-B1 | Decay Store Testing – Technical Specification Non Compliance | Trending | While performing decay store (DCS) CO2 make-up valve testing, 5 irradiated fuel assemblies presented in the DCS with a decay heat above technical specification (TS) limit (20kW). | The cause was the work instruction and quality plan did not include any references to technical specification compliance. The plant modification in 2011 did not robustly identify any TS compliance issues and the training was not provided. | SER 2005-3 | 1 - For information only, technical specification, test | CM.3 , MA.2
WER PAR 16-0154 | 2015-12-20 | 2016-03-01 10:48 | Heysham-A1 | Turbine 1 Spurious Trip on Generator Protection | Trending | During startup from 88 MWe following an automatic scram, the turbine generator tripped on the generator differential protection actuation. | The cause was a crimped connector associated with a current transformer connected to the differential protection circuit failed. The crimp failed with a crack due to high cycle fatigue caused by vibration transmitted along the wire to which it was attached. Actions to address previous similar failure were not effective. |  | 1 - For information only, connector, differential relay, fatigue cracking, transformer, turbine trip, vibration | CM.3 , PI.2
WER PAR 16-0153 | 2015-12-18 | 2016-03-01 10:35 | Forsmark-1 | Wrong type of gas was connected | Trending | A hydrogen gas cylinder connected to the gas connector for Formier 10 gas (consists of 90 % nitrogen and 10 % hydrogen) was discovered. This could have catastrophic consequences if hydrogen gas was used as welding gas. | The direct cause was error due to mental image of operators that formier 10 had been ordered and transported out to the containers. The other cause was that both formier 10 and hydrogen have the same red chemical marking and same connector standard. The contributing cause was lack of procedure use and adherence. |  | 2 - Important lessons, configuration control, human error, hydrogen, industrial safety, procedure adherence, weld | CM.2 , IS.1
WER PAR 16-0151 | 2015-12-12 | 2016-03-01 10:12 | Tricastin-1 | Reactor Coolant System pressure rises above 70 bar abs for two minutes with the Safety Injection System (RIS) accumulators isolated. | Trending | During shutdown with steam generators connected, safety injection system (RIS) accumulators were isolated when the reactor coolant pressure exceeded the technical specification limit. This resulted in violation of technical specification. | The cause was human error as the operator did not check the reactor coolant system pressure before isolating the safety system injection accumulators. The contributing cause was deficiency in procedure. | SOER 2013-1 Rec 3 | 1 - For information only, human error, procedure inadequacy, safety injection, technical specification | OP.1 , OP.2
WER PAR 16-0149 | 2015-12-04 | 2016-03-01 09:57 | Cruas-2 | Main transformer de-energised due to fault on high-voltage bushing | Trending | Unit transitioned from refuelling outage mode to cold shutdown mode without results of dissolved gas analyses (had taken earlier) of the dielectric fluid in the high-voltage bushing for the main transformer. The main transformer was re-energised. High traces of combustion gas acetylene and other hydrocarbon were discovered in the high-voltage bushing of the main transformer. This was a symptom of an internal arc fault in the bushing with a high risk of explosion. The main transformer was de-energised and the unit was taken into refuelling shutdown mode. | The causes include inadequate work package, lack of questioning attitude and lack of data collection for system and component health reporting. | SOER 2011-1 Rec 1, 2, 4 | 1 - For information only, bushing, gas, procedure inadequacy, transformer. | ER.2 , MA.2 , WM.1
WER PAR 16-0146 | 2015-12-04 | 2016-03-01 07:28 | Gravelines-4 | Unavailability of sodium injection function associated with work on a containment spray system valve | Trending | During normal operations, a containment spray (CTS) system valve was stuck to the bottom of the valve body, resulting in high sodium concentration being identified above a technical specifications limit in the CTS tank. A group 2 limiting condition of operations was entered. | The cause was the failure to refit a bushing and stripper ring during the last outage in 2014. The causes were deficiencies in work planning and work file preparation. Inadequate communication and a lack of questioning attitude contributed to the event. |  | 1 - For information only, containment spray, human error, limiting condition of operation, valve, work control | MA.1 , WM.1
WER PAR 16-0144 | 2015-09-11 | 2016-03-01 05:57 | Doel-4 | Replacement reactor vessel head D4: floaters in weld ventpipe vessel head | Trending | During the replacement of the reactor vessel head (RVH), indications (floaters) in the weld of the RVH vent pipe was discovered via non-destructive test. The indications consist of portions of Aluminium Oxide that encompass a volume of unaffected material. An in-depth evaluation resulted in 7 days delay on the work scheme was actually detected much earlier during the project. | The direct cause is under the contractor's investigation. Subcontractor response to questions about indications was slow during fabrication phase. The communication between the station and the design company was not adequate. Due to the unknown impact of the indications no communications were made to NPPDoel on this issue. In addition the subcontractor then replied that they had no justifications for the found indications. | SER 2005-3 | 2 - Important lessons, contractor, modification, reactor vessel head, vendor, weld | PM.1
WER PAR 16-0143 | 2015-09-08 | 2016-03-01 05:43 | Vandellòs-II-2 | Condition not allowed by the Technical Specifications due to an inadvertent inoperability of the orifice isolation valves in the letdown line | Trending | During startup, flow rates greater than expected were detected in the letdown line of the chemical and volume control system. After inspection, three orifice isolation valves were declared inoperable. As these valves function as containment isolation valves, the limiting condition for operation (LCO) for containment isolation was not being complied with in the required time frame. | The direct cause was that the actions associated with the LCO were not applied on time. The root causes include appropriate settings for the spring rate not included in maintenance instructions, change in the scope of the work performed not notified and non-compliance with the tests required by the in-service inspection manual. |  | 1 - For information only, containment isolation, human error, limiting condition of operation, procedure inadequacy | OP.1 , OP.2
WER PAR 16-0142 | 2015-09-01 | 2016-03-01 04:46 | Vandellòs-II-2 | Value of as-found test of Pressuriser Safety Valve outside of required ±3% range | Trending | The setpoint pressure verification of the one of the three (3) pressuriser safety valves, removed during the last outage, was found to be outside of the plus and minus 3% acceptance criteria during the as-found test. Hence, the plant had been in a condition prohibited by the technical specifications although this did not prevent the safety valves from complying with the safety function. | Anomalies during the as-found test may have been a contributor. |  | 2 - Important lessons, limiting condition of operation, pressure relief valve, safety relief valve, setpoint, technical specification, test | ER.2
WER PAR 15-0649 | 2015-06-09 | 2016-03-23 05:15 | Forsmark-2 | Automatic relief path for filtered pressure relief of the reactor containment not ready for operation | Trending | During normal operation and while performing reactor containment integrity test, a rupture disk ruptured at too low pressure. This resulted in an increased risk for inadequate margin to loss of net positive suction head for containment spray system and emergency core cooling system | The direct cause was installation of a rupture disk with incorrect burst pressure. The contributing cause was misinterpretation of burst pressure requirement for the rupture disk by the supplier. The underlying cause was lack of quality assurance on the procurement documentation. |  | 1 - For information only, procurement, rupture disc, spare part, vendor | ER.3
WER PAR 15-0633 | 2015-07-04 | 2016-03-23 05:10 | Forsmark-2 | Control rod drive R45 not ready for operation | Trending | While operating at 54% power and during rod movement in conjunction with flux tilting, a control rod could not be completely withdrawn. | The direct cause was foreign material, a small metal pin, had caused the control rod drive to seize. The origin of the pin is under investigation. |  | 1 - For information only, control rod drive, flux tilt, FME | MA.2
WER PAR 15-0095 | 2014-10-10 | 2016-03-02 07:37 | Vandellòs-II-2 | Non-programmed automatic actuation of the Reactor Protection System due to loss of the 400 kV line | Trending | During the recovery to a loss of off-site power event and while performing the shut down procedure for the emergency diesel generator (EDG), the EDG lever was inadvertently moved to the start position before quickly being moved back to the shutdown position. The EDG restarted for 10 minutes without connection to station bus. | The root cause was human error. There was inadequate self-checking when the EDG actuating lever was manipulated. |  | 1 - For information only, diesel generator, human error | OP.1
WER PAR 14-0003 | 2013-03-07 | 2016-03-21 07:56 | Lingao-4 | Defect Existing in Power Supply Circuit of Main Feedwater System Flow Meter ARE049/050/051MD of LNPS-II | Trending | During the analysis of an anticipated transient without scram (ATWS), logic was found that the power supply circuits of flow meters of the main feedwater systems on units 3 and 4 had a design defect. The three signals were supplied by the same power supply switch. Single failure of the power supply might trigger the actuation of ATWS. | The root cause was inadequate original design. |  | 1 - For information only, feedwater control system, flow transmitter, modification, power supply | CM.1
WER MOW 16-0051 | 2016-03-21 | 2016-03-22 07:53 | Beloyarsk-4 | #PRELIMINARY# Beloyarsk Unit 4 Tripped Off Line by Ground Fault Protection Actuation During Low Power Testing | Trending | During commissioning and while operating at 44% power, a ground fault protection on generator rotor winding actuated and tripped the turbine generator. The reactor scrammed automatically. | The cause is under investigation. |  | 1 - For information only, automatic scram, ground fault, insulation electrical, turbine trip | ER.1
WER MOW 16-0050 | 2016-03-21 | 2016-03-22 07:47 | Beloyarsk-4 | #PRELIMINARY# Beloyarsk Unit 4 Tripped Off Line During Low Power Testing | Trending | While at 71% and increasing the reactor thermal power, the turbine generator tripped on low main steam temperature at turbine inlet. The reactor automatically scrammed. | The cause was a human error. An action to erase memory during protection system testing was not taken as expected. The event is under further investigation. |  | 1 - For information only, automatic scram, human error, turbine trip | OP.1
WER MOW 16-0048 | 2015-10-20 | 2016-03-11 06:07 | Kalinin-4 | A Circulating Water Pump Tripped on Low Traveling Water Screen Flushing Efficiency and Coarse Strainer Rotor Sticking Due to a Huge Influx of Zebra Mussels | Trending | During normal operation, a circulating water pump was tripped to address the high pressure difference on an intake coarse strainer column due to a large influx of zebra mussels. The unit power was reduced with a loss of 2.8 equivalent generation days. | The root causes were increased growth of mussel in the adjacent lake and deficient design of the plant cooling pond levels. The readings of fouling sensors were not correct due to an insufficient flushing water flow, which was not addressed adequately with prompt actions. | SOER 2007-2 Rec 2, 3, 5 | 1 - For information only, design criteria / design basis, environment, intake, power reduction, strainer, travelling screen | CM.1 , OP.1
WER MOW 16-0046 | 2015-09-14 | 2016-03-11 05:54 | Kola-1 | 330 kV Circuit Breaker Inadvertently Tripped from a Failure of an Output Relay Associated with the 330 kV High Voltage Overhead Line Protections | Trending | While operating at 85% power, phase A of a circuit breaker (CB) associated with high voltage 330 kV overhead line tripped. Other CB phases also tripped due to failing to switch over, resulting in a partial loss of offsite power event. | The cause of the CB phase A trip was due to low insulation resistance on a normally open contact in a backup protective relay. The cause of the CB phase B and C trips were protection actuation on circuit breaker phase failures to switch over. |  | 1 - For information only, circuit breaker, loss of offsite power, relay | ER.3
WER MOW 16-0045 | 2015-11-06 | 2016-03-11 05:48 | Kursk-1 | A Turbine Generator Had to Be Tripped to Address a HigF51:K52h Babbitt Temperature on Stuffing Box Bearing No. 11 | Trending | During normal operation, one of the two turbine generators was tripped to rectify the problem of increase in babbitt temperature on the turbine generator stuffing box bearing. The event resulted in unit downpower to 50% for about two days. | The direct cause was degradation of rubber material on the bearing due to shelf life expiration causing the sealing cord size to change. The root cause was not replacing the rubber sealing cord promptly due to inadequate monitoring. |  | 1 - For information only, ageing, bearing, power reduction, spare part, turbine generator, turbine trip | ER.2 , ER.3
WER MOW 16-0044 | 2015-09-07 | 2016-03-11 05:40 | Leningrad-1 | Loss of generator/gas cooler sealing rubber gasket integrity caused a hydrogen pressure drop in the generator being in cold standby. | Trending | During operation at 50% power and while returning one of two generators from cold standby to service, a generator hydrogen pressure drop occurred due to a leak. As a consequence, a 91.5- hour maintenance shutdown of one generator was required for repairs. | The direct cause was a through defect of the generator gas cooler sealing rubber gasket. The root cause is under investigation. |  | 1 - For information only, gasket, hydrogen, leak, procedure inadequacy, seal, turbine generator | ER.1 , MA.2
WER MOW 16-0042 | 2015-10-14 | 2016-03-11 05:26 | Novovoronezh-5 | Novovoronezh Unit 5’s RTP Had to be Reduced to 95 MWt per Urgent Request to Address a Spurious Signal Induced Deficient CRDM 03-33 Power Control | Trending | During normal operation, a control rod drive mechanism (CRDM) was in the off-spec position due to a short-term spurious signal. The power was reduced by about 10% to address the issue. | The cause was a faulty module in an associated CRDM power control circuit due to deficient fabrication or software. |  | 1 - For information only, control circuit, control rod drive, power reduction | ER.3
WER MOW 16-0040 | 2015-11-05 | 2016-03-08 23:16 | Loviisa-2 | Unit Shutdown due to Control Rod Drive Mechanism Motor Failure | Trending | During normal operation, one control rod dropped to its lower position in the reactor core due to the loss of the holding current. All control rod drives (CRDMs) were checked and the same symptoms were identified on other three CRDMs. The reactor was shut down for about 4 days. | The cause was the intermediate cooling water system leak entering into the CRDM motor compartment causing coil short circuit. The similar events had occurred previously and one of the actions was all new CRDMs undergo a leak test. |  | 2 - Important lessons, component cooling water, control rod drive, control rod drop, leak, pressure relief valve, reactor shutdown, short circuit, test | PI.2
WER MOW 16-0038 | 2015-11-10 | 2016-03-02 12:05 | Temelin-2 | Spurious activation of the Limitation System | Trending | During normal operation and when one of the three feedwater pumps (FWPs) was under maintenance, power supply to the cards that provide control for one of the two in-service feedwater pump failed, resulting in an automatic power reduction below 40%. The data transmitted from the cards to the information system was lost and the control room operator did not have the indication of the in-service FWP parameters. The FWP was tripped manually. | The direct cause was a fault in the output part of an associated inverter. |  | 1 - For information only, feedwater pump, Instrumentation and control, inverter, power reduction, power supply | ER.3
WER MOW 16-0037 | 2015-11-10 | 2016-03-02 11:17 | Dukovany-2 | Fall of the Refueling Machine Camera into the Spent Fuel Storage Pool | Trending | While checking cleanliness of the spent fuel storage pool (SFSP) and a pit using external camera mounted on the refuelling machine, the camera fell into the SFSP. There was a potential for damage to the refuelling machine and fuel in the pool. | The direct cause was deviation of the camera rod positioning and hitting the camera to the corridor edge of the SFSP. The root causes include inadequate mark of the zero position on the camera rod, lack of questioning attitude and non conservative approach. |  | 2 - Important lessons, foreign material, fuel pool, human error, spent fuel storage | MA.1
WER MOW 16-0020 | 2016-01-20 | 2016-03-02 13:19 | Rovno-3 | The Unit underwent a shutdown due to poor worker practices. | Trending | During operation at 85% power and while replacing the safety features in the reactor coolant pump (RCP) process protection, a normal feeder breaker on one bus tripped, leading to deenergization of both the bus and all its loads. This actuated the process protection and closed a turbine generator stop valve. Consequently, the turbine generator tripped and reactor automatically scrammed. | The cause was poor worker practices when performing the electrical lineups. The root cause was a lack (deterioration) of a barrier between adjustment terminals in the terminal block due to degradation and insufficient lighting while performing complex work. |  | 1 - For information only, automatic scram, bus, environment, human error, turbine stop valve, turbine trip | ER.3 , MA.1 , OP.1
WER MOW 15-0222 | 2015-10-26 | 2016-03-08 23:22 | Mochovce-2 | The Superemergency Feed Water Pump unavailability | Trending | During nominal operation, a failure occurred on the protection and control terminal for the outlet for the actuator of the high-pressure auxiliary feedwater pump (AFP). This resulted in the AFP unable to be switched on remotely. The AFP was declared inoperable. | Auto diagnostics identified that the terminal functions were blocked. The root cause was the modification which would allow the control of the actuators, in case of a failure on the protection terminal, had not been implemented yet. |  | 1 - For information only, emergency feedwater, feedwater pump, technical specification | ER.1 , PI.3
WER MOW 15-0208 | 2015-10-14 | 2016-03-09 01:04 | Mochovce-2 | Steam dumps to the atmosphere failure during unit startup | Trending | During startup and while performing tests, at four out of twelve steam dump valves (SDVs), the torque breaker was activated leading to the SDVs loss of control and thus into their inoperability. | The direct cause was the more difficult movement on a SDV of steam generator No. 5 was while actuation of the torque breaker. The associated SDVs of steam generator No.1 ,4 and 5 was inadequate setting of the end-positions under cold conditions. The root cause was corrective measures not being executed and possible shift of the end-positions after warming up had not been anticipated. |  | 1 - For information only, breaker, steam dump valve, test | ER.1 , PI.3
WER MOW 15-0201 | 2015-09-25 | 2016-03-11 01:59 | Mochovce-2 | Steam dump to the atmosphere and SG safety valve failure | Trending | While shutting down for an outage and at 90% power, a steam dump valve to atmosphere failed to open during a test. Later in another test, safety valve of a steam generator failed to open from main control room. | The direct cause was activation of torque protection of servo drive due to break off of the valve from the closed position and failure of remote control of the steam generator safety valve. The root cause was not implementing corrective actions from a similar event from 2014. |  | 1 - For information only, control circuit, safety relief valve, steam dump valve, steam generator / boiler | ER.1 , PI.3
WER ATL 16-0327 | 2015-09-30 | 2016-03-29 15:54 | Comanche Peak-1 | Emergency Diesel Generator Failed to Load | Trending | During normal operation and while performing routine test, an emergency diesel generator (EDG) could not be loaded more than 2 MW. This resulted in entry into a limiting condition of operation. | The direct cause was invalid voltage input to the governor, causing a higher startup frequency which did not allow the EDG to be loaded greater than 2 MW. The apparent cause was a faulty generator load sensor. Failure analysis will determine if corrective actions are needed. |  | 1 - For information only, diesel generator, limiting condition of operation | ER.1
WER ATL 16-0326 | 2015-08-27 | 2016-03-29 15:44 | Donald Cook-1 | Unplanned Limiting Condition of Operations Entry While Taking Voltage Measurements On Radiation Monitoring System | Trending | During normal operation and while performing preventive maintenance on an auxiliary building area radiation monitor, an electrical arc occurred, causing the monitor to send a control room pressurization signal to the control room. As a consequence, a limiting condition of operations (LCO) was entered. | The cause was human error. It is likely that a 12VDC pin was shorted to ground by mistake due to very small pins. |  | 1 - For information only, arc strike, ground fault, human error, limiting condition of operation, short circuit | MA.1
WER ATL 16-0322 | 2015-06-25 | 2016-03-29 13:30 | Diablo Canyon-2 | Unplanned Dilution of the Spent Fuel Pool | Trending | During normal operation, a manual demineralized makeup water to the spent fuel pool (SFP) valve was open adding pure water to the pool. It resulted in the SFP level being above the alarm level and dilution of the SFP. | The direct cause was the unauthorized re-positioning of the valve by an unknown party. |  | 1 - For information only, fuel pool, makeup water, misposition, valve | CM.2
WER ATL 16-0319 | 2014-11-07 | 2016-03-29 11:03 | Mcguire-1 | Reactor Coolant System to Safety Injection Isolation Boundary Valve Leakage Results in Outage Delay | Trending | During shutdown and while performing pressure isolation valve testing, excessive back leakage was found from a check valve between reactor coolant system and safety injection. This resulted in extension of outage for 5.5 days to rectify the problem. | The direct cause was wear on the valve bracket, shaft and disc due to increased residual heat removal flow for longer periods of time than previous refueling outages. The root cause was a legacy design issue with the piping configuration upstream of the valve. The contributing cause was not taking into account the increased wear due to higher flow rates and duration. |  | 2 - Important lessons, check valve, design criteria / design basis, isolation valve, leak | CM.1 , ER.2
WER ATL 16-0317 | 2014-12-31 | 2016-03-29 10:27 | Diablo Canyon-1 | Cracked Weld on Residual Heat Removal Piping Relief Valve Inlet Line Inside Containment | Trending | During hot standby mode after an outage, a cracked socket weld on the residual heat removal (RHR) relief valve suction line caused a 30-drop per minute leakage. This resulted in both trains of the RHR system declared inoperable. The unit was placed in hot shutdown mode to rectify the problem. | The root cause was a containment fan cooler unit (CFCU) vibration exciting a resonant condition that generated stresses, resulting in fatigue failure of the weld. The contributing causes were inadequate analysis of the CFCU inlet damper modification and insufficient identification and implementation of corrective actions from a similar event in the past. The leak occurred at a weld that was previously repaired following a similar crack and leak in June 2013 | SER 2005-3 | 2 - Important lessons, fatigue cracking, leak, modification, relief valve, residual heat removal, vibration, weld | CM.3 , OF.2 , PI.2
WER ATL 16-0315 | 2015-09-29 | 2016-03-29 09:14 | Fermi-2 | Temporary Shielding Placement Prevents Valve Operation | Trending | During shutdown, reactor water cleanup outboard containment isolation valve could not be closed from main control room. This resulted in entry into a limiting condition for operation. | The cause was human error as a contract worker placed a temporary shielding on the valves declutch lever, which prevented its remote operation. |  | 1 - For information only, containment isolation, contractor, human error, limiting condition of operation, reactor water cleanup, valve | CM.2
WER ATL 16-0314 | 2015-06-26 | 2016-03-29 08:50 | Diablo Canyon-2 | Reactor Coolant Pump Seal Injection Flow Resistance is Low | Trending | During normal operation and while performing a surveillance test, reactor coolant pump seal water injection flow resistance was declared inoperable due to low flow resistance, resulting in entry into a limiting condition for operations. | The cause was likely to be the dislodging of debris trapped in the seal injection throttle valve. |  | 1 - For information only, debris / crud, limiting condition of operation, reactor coolant pump seal, throttle valve | ER.1
WER ATL 16-0313 | 2015-03-09 | 2016-03-29 08:40 | Fermi-2 | Failure of Swing Bus Automatic Throwover Results in Unplanned Shutdown Limiting Condition for Operation Entry and Downpower | Trending | During normal operation and while performing surveillance testing on the 480 V swing bus, the automatic throwover failed. This resulted in entry into a limiting condition of operation and unplanned downpower of 19%. | The direct cause was oxidation on the contacts of the throwover relay. The apparent cause was inadequate preventive maintenance of the relay. |  | 1 - For information only, limiting condition of operation, preventive maintenance, relay | ER.2
WER ATL 16-0310 | 2015-12-20 | 2016-03-29 08:20 | South Texas-1 | Low Power Transient from Closing Feedwater Pump Recirculation Valve Leading to Unplanned Technical Specification Entries and Equipment Actuations | Trending | While ascending power at 20%, an operator closed a feedwater pump to increase the feedwater flow to the steam generators (SGs). This resulted in doubling the feedwater flow to the SGs. The reactor coolant system temperature went below the technical specification limit, letdown isolated due to low pressurizer level response and a pressuriser relief valve lifted during the subsequent heat-up. The unit power was reduced to 14%. | The cause was operator fundamentals weaknesses. The unit supervisor failed to consider other options and did not demonstrate proficiency in decision making. Inadequate procedure was a contributor. | SOER 2013-1 Rec 3 | 1 - For information only, feedwater, human error, limiting condition of operation, power reduction, pressure relief valve, procedure inadequacy | OP.1 , OP.2
WER ATL 16-0309 | 2015-08-25 | 2016-03-28 15:54 | Arkansas-2 | Emergency Feedwater Pump Oil Level Sight-glass Found Installed Incorrectly Causing Low Oil Level | Trending | During normal operation, emergency feedwater pump was found with the pump outboard bearing oil level sight glass upside down and no oil in the bearing. The pump was declared inoperable, resulting in entry into a limiting condition of operation. | The cause was movement of sight glass connected to the bearing via a threaded connection, allowing the sight glass to invert and drain the oil out of the bearing through the sight glass vent hole. The apparent cause was configuration change made to the oil reservoir sight glass without sufficient analysis. |  | 1 - For information only, auxiliary feedwater pump, bearing, design change, leak, limiting condition of operation, modification, oil, oil level | CM.3
WER ATL 16-0304 | 2015-09-10 | 2016-03-28 14:35 | Salem-2 | Loss of Component Cooling Water Motor Operated Valve Control Power and Position Indication | Trending | During normal operation, loss of control power and position indication for a motor operated valve (MOV) for the component cooling suction header inlet occurred during a functional stroke in response to several alarms for the loss of voltage of the valve. As a result, a 72-hour shutdown technical specification action statement was entered. | The most probable cause was a failure to fix an intermittent contact between the primary power stabs and female connections on the vertical bus identified in 2011. The work order had been moved out several times due to resources. |  | 1 - For information only, component cooling water, limiting condition of operation, motor operated valve, power supply | ER.1 , PI.2 , WM.1
WER ATL 16-0303 | 2015-10-05 | 2016-03-28 14:24 | Braidwood-2 | Containment Emergency Hatch Not Operating Properly | Trending | During a refuelling outage, the emergency hatch inner door failed to open, preventing the outer door from opening. The emergency hatch was declared inoperable, resulting in entry into a limiting condition of operation. | The cause was inappropriate operation of the inner door containment-side handwheel due to the outer door handwheel being turned at the same time. This caused binding of the door interlocks and a nut inside the gearbox sheared off under the counteracting loads. |  | 1 - For information only, containment hatch, human error, limiting condition of operation | OP.1
WER ATL 16-0302 | 2015-12-05 | 2016-03-28 14:19 | Surry-1 | Fuel Cooling Pump Failed Due to Auxiliary Latching Contact in Pump Motor | Trending | During normal operation, the running spent fuel cooling pump was no longer running, resulting in a momentary loss of decay heat removal. | The cause was abnormally high resistance on the auxiliary latching contact for the motor starter contactor caused by debris contamination from extensive chattering of the contactor. The chattering condition was caused by detachment of the secondary coils from the contactor coil assembly. |  | 1 - For information only, debris / crud, fuel pool cooling, preventive maintenance, pump motor, spent fuel storage | ER.2
WER ATL 16-0299 | 2015-08-14 | 2016-03-28 14:00 | Byron-2 | Through-wall leak of essential service water strainer backwash line causes entry into 72 hour shutdown clock | Trending | During normal operation, a through-wall leakage was found in an essential service water (SX) pump discharge strainer backwash line. The SX pump was isolated to carry out repair. This resulted in entry into a limiting condition of operation. | The cause was pitting in the pipe elbow due to microbiologically induced corrosion (MIC). The stagnant raw water in carbon steel pipe created ideal conditions for MIC. The contributing cause was inadequate preventive maintenance. |  | 1 - For information only, carbon steel, essential service water, leak, limiting condition of operation, microbiologically induced corrosion, preventive maintenance | ER.2 , ER.4
WER ATL 16-0297 | 2015-12-21 | 2016-03-28 11:04 | South Texas-1 | Turbine Trip and Subsequent Manual Reactor Trip due to Governor Valve Oscillations | Trending | During startup and at 48% power, oscillations in a governor valve resulted in excessive load swings on the main turbine. The turbine was manually tripped. The steam dump valves did not respond as expected resulting in increase in steam generator level, which caused a feedwater isolation and opening of main steam relief valves. The reactor was scrammed manually. | The cause was an intermittent ground fault on a control wire of the governor valve due to a small cut in the insulation during initial installation. The steam dump valves failed when spring clips became loose from fluctuations of steam flow caused by oscillations of the governor valve. |  | 1 - For information only, governor valve, ground fault, insulation electrical, manual scram, relief valve, steam dump valve, turbine trip | ER.1 , MA.1
WER ATL 16-0295 | 2015-12-01 | 2016-03-28 10:21 | Calvert Cliffs-2 | Manual Reactor Trip Initiated due to Loss of One Operating Steam Generator Feed Pump | Trending | During normal operation, a steam generator feed pump (SGFP) tripped. The reactor was scrammed manually. | The direct cause was failure of the SGFP coupling. This resulted from loss of alignment due to inadequate torqueing of pump casing to pedestal studs. The root cause was inadequate engineering review for use of a different tool for installation of studs in lieu of cap screws for the feed pump. |  | 1 - For information only, coupling, design change, feedwater pump, manual scram, torque | EN.1 , MA.1
WER ATL 16-0292 | 2015-10-23 | 2016-03-24 13:55 | Donald Cook-1 | Accumulator Fill Resulted in an Unexpected Boron Dilution Due to Leaking Check Valve | Trending | During normal operation and while increasing boron concentration in a safety injection accumulator, the concentration actually decreased, resulting in the inoperability of the accumulator. A 72-hour technical specification action was entered. | The cause was attributed to minor reactor coolant system fluids leaking past a primary circuit system pressure isolation check valve into a safety injection (SI) header for approximately 41 days. The flush of the SI header was not performed prior to refilling the accumulator due to inadequate communication. |  | 1 - For information only, accumulator, boron dilution, check valve, leak, limiting condition of operation, procedure inadequacy, safety injection, work control | OP.1 , OP.2
WER ATL 16-0283 | 2015-11-09 | 2016-03-24 10:06 | Bruce-A4 | Lessons Learned from Low Pressure Service Water Pump Failures at End of Unit Outage | Trending | During an outage and while trying to start two low pressure service water (LPSW) pumps after being rebuilt, accumulation of debris in the pumps resulted in extension of outage for two days to rectify the problem. | The cause was blockage of water flow paths to the LPSW pumps by sand and sediment that entered the bearings of the pump. The procedure used to return an LPSW pump to service did not have a requirement to flush the water lines. |  | 1 - For information only, debris / crud, foreign material, procedure inadequacy, pump, service water | MA.2 , OP.2
WER ATL 16-0282 | 2015-10-26 | 2016-03-22 15:48 | Watts Bar-1 | Control Rod Drive Vent Plug Leakage Causes Dropped Rod and Subsequent Maintenance Outage | Trending | During normal operation and following an alarm for abnormal radiation level in the containment, a control rod dropped into the core, resulting in an immediate power reduction to 98.5%. Operators reduced power to 70 % in accordance with station guidance. Subsequently, a maintenance outage was needed for investigation. | The cause was a leaking control rod drive mechanism (CRDM) vent plug adjacent to the dropped control rod, which wetted a CRDM connection. Preventive actions from previous operating experience were ineffective (operating experience from a 1999 occurrence at the Kori Nuclear Power Plant in South Korea). |  | 2 - Important lessons, control rod drive, control rod drop, ground fault, leak, modification, power reduction, reactor shutdown, water intrusion | ER.2 , PI.2
WER ATL 16-0278 | 2016-01-13 | 2016-03-22 14:25 | Seabrook-1 | Main Steam Isolation Valve to Emergency Feedwater Pump Failed Stroke Time During Surveillance | Trending | During normal operation and while performing the turbine driven emergency feedwater pump (EFP) surveillance, the main steam isolation valve to the EFP also serves as a containment isolation valve, failed to close within the allowed time. The valve was declared inoperable and an entry into a less than 72 hour shutdown action was needed. | The cause was a degraded regulator on the backup nitrogen supply. The failed part was returned to the vendor for detailed analysis. |  | 1 - For information only, containment isolation, isolation valve, limiting condition of operation, regulating valve, steam dump valve | ER.3
WER ATL 16-0276 | 2015-12-15 | 2016-03-22 11:59 | Barakah-4 | Personnel Injury during Concrete Pour due to Pipe Falling | Trending | During construction phase and while restarting a concrete pump for pouring operation, vibrations caused a stationary pipe to move and the pipe fell from a height of approximately 40 cm. The pipe struck the right leg of a worker, resulting in leg fracture requiring hospitalisation. | The direct cause was vibrations due to the pressure surge when restarting the concrete pump and the pipe was not secured properly. The apparent causes were insufficient situational awareness, improper handover of task and inadequate sequence and method for securing stationary pipeline in the work document. |  | 1 - For information only, fall, human error, industrial safety, injury, procedure inadequacy, vibration | IS.1
WER ATL 16-0272 | 2015-12-17 | 2016-03-22 09:49 | Point Beach-2 | Component Cooling Water Pump Motor Failed | Trending | During normal operation, a component cooling (CC) water pump motor stator winding shorted to ground and progressed to a phase-to-phase short circuit. As a result, a 72-hour shutdown limiting condition of operations was entered. | The apparent cause was an age related degradation of the motor initiated by adjacent winding turn abrasion. There was no rewind maintenance since installation. The motor had been in service since the original plant startup. |  | 1 - For information only, ageing, breaker, component cooling water, ground fault, limiting condition of operation, preventive maintenance, short circuit | ER.2 , ER.3
WER ATL 16-0271 | 2015-07-28 | 2016-03-22 09:47 | North Anna-2 | Emergency Diesel Generator Coolant Leak from Cylinder Liner Jacket | Trending | During normal operation and while performing a surveillance test of an emergency diesel generator (EDG), coolant was found leaking from an engine cylinder. The EDG was unavailable for 12 days to rectify the problem. | The direct cause was a through wall crack in the cylinder liner jacket. The apparent cause was degradation of coating on the cylinder liner jackets due to use of chemical incompatible with the coating. |  | 1 - For information only, chemical control, chemistry, corrosion, diesel cooling water, diesel generator, leak | CY.1 , ER.1
WER ATL 16-0269 | 2016-02-07 | 2016-03-21 08:17 | Bruce-B-5 | Unit 5 Fueling Machine West Bridge causes forced outage | Trending | During normal operation, a reactor area bridge (RAB) stopped while driving the fuelling machine down to drop off position. The reactor was shutdown for three days to rectify the problem. | The cause was a friction disc fracture on one of the brakes of the RAB. The other cause was inadequate design of the brake hub, which caused the friction discs to fracture. |  | 1 - For information only, design criteria / design basis, reactor shutdown, refuelling | FA.1
WER ATL 16-0265 | 2015-12-14 | 2016-03-17 10:31 | Surry-2 | High Pressure Heater Drain Pump Trip | Trending | While operating at 90% power, a high pressure heater drain pump tripped on the heater drain tank low level. The reactor power was reduced to 75% to rectify the problem. | The cause was internal binding of the high pressure heater drain tank level control valve. The valve had an internal subcomponent composed of a material not in accordance with the specification and thermal expansion characteristics that caused internal binding. |  | 1 - For information only, control valve, heater drain, power reduction, spare part, vendor | ER.3
WER ATL 16-0264 | 2015-12-22 | 2016-03-16 14:40 | Cooper-1 | Downpower to Repair on a Grounded Steam Tunnel Fan Coil Unit | Trending | During normal operation, a ground developed on one of the steam tunnel (ST) fan coil units (FCUs), resulting in the ST FCU to be removed from service. The reactor power was reduced to approximately 30% to fix the ST FCU. | The apparent cause was the motor leads contacted the bottom of the connection box causing ground faults. A contributing cause was elevated vibration levels. |  | 1 - For information only, ageing, fan, ground fault, heating ventilating and air conditioning, lead, power reduction, short circuit, vibration | ER.1
WER ATL 16-0258 | 2015-12-08 | 2016-03-15 10:48 | Oyster Creek-1 | Security Officer Received Laceration to the Head from Contact with a Circuit Breaker | Trending | A security officer made contact with the bottom of a circuit breaker box on the wall while standing up from a lower position, causing head injury. An off-site medical attention for staples was needed. | The cause was lack of situational awareness and inadequate risk perception. |  | 1 - For information only, industrial safety, injury | IS.1
WER ATL 16-0257 | 2015-03-19 | 2016-03-15 10:15 | Fermi-2 | Cooling Water Leak in Drywell Results in Unplanned Downpower and Single Loop Operations | Trending | During normal operation, the reactor building closed cooling water (RBCCW) leaked in the drywell resulting in a reactor recirculation (RR) pump seal cooling flow low alarm. RBCCW was isolated and emergency equipment cooling water was placed into service. The RR pump was shut down. The event resulted in single loop operation and reactor power was reduced to 61%. | The cause was leakage from the RR pump seal cooling water low flow switch due to glass indicating tube being broken. The flow induced vibration of the RR pump rotameter steel float impacted the glass tube. |  | 1 - For information only, cooling water, flow induced vibration, leak, reactor building, reactor recirculation pump, switch | ER.1
WER ATL 16-0256 | 2015-03-27 | 2016-03-15 09:52 | Hatch-1 | Feedwater Heater Level Control Valve Packing Failure | Trending | During normal operation, steam leak was identified at a drain valve of a moisture separator reheater (MSR) drain tank to a feedwater heater. A downpower to 17% was needed and turbine generator was shut down for repairs. | The direct cause was packing nuts failure on the drain valve. The apparent cause was excessive vibration that caused the packing nuts to become loose. The contributing causes were the outdated control of the feedwater heater level control system (the current Unit 1 performance with higher temperatures and flows has stressed the system to where it is now operating at the extreme edge of reliable performance) and design deficiencies of the second stage MSR drain tank high level dump valves. | SER 2005-3 | 2 - Important lessons, control valve, design criteria / design basis, feedwater heater, leak, power reduction, power uprate, steam, vibration | CM.1 , CM.3
WER ATL 16-0255 | 2016-01-31 | 2016-03-14 13:47 | Pickering-A1 | Stalling of a Digital Control Computer and Loss of Both Command Monitors Resulted in Loss of Redundancy in Reactivity Management and Control Functions | Trending | During normal operation, digital control computer 1 (DCC1) stalled and a loss of both channel 1 and channel 2 command monitors took place. This resulted in loss of monitoring function and loss of redundancy in reactivity management and control functions. | The apparent cause was electro static discharge resulting from contact/friction, aggravated by low relative humidity in the main control room. Static electricity can adversely impact ageing components. The contributing cause was not completing the recommended actions from previous assessments. |  | 1 - For information only, ageing, computer, control room, environment, heating ventilating and air conditioning | ER.3 , PI.3
WER ATL 16-0251 | 2015-10-27 | 2016-03-14 11:03 | Darlington-3 | Inadequate Control of Turbine Hall Crane Access | Trending | While accessing a turbine hall crane for repair, a worker accessed another crane at off-park position by climbing over a handrail and ascending an emergency access ladder. This exposed the worker to a potential fall of 20 metres. | The root cause was inadequate access control to the turbine hall cranes. The contributing causes include lack of use of error prevention tools and inadequate reinforcement of risk assessment expectations to station personnel. This is similar to WER ATL 2014-0123. |  | 1 - For information only, crane, fall protection, human error, industrial safety, management oversight | IS.1 , MA.1 , PI.2
WER ATL 16-0240 | 2015-12-21 | 2016-03-08 10:56 | St. Lucie-1 | Downpower Due to Control Element Assembly Inserted into the Core | Trending | During normal operation, a control element assembly inserted into the core unexpectedly. A downpower to 70% was required to recover the dropped control rod. | The cause was failure of the upper gripper power switch due to a silver migration on the circuit board. |  | 1 - For information only, circuit card, control rod drop, power reduction, prejob brief, switch | ER.1
WER ATL 16-0239 | 2015-12-07 | 2016-03-08 10:24 | Arkansas-2 | Safety Related 4160 Volt Alternating Current Containment Spray Pump Breaker Failed to Close | Trending | During normal operation, the supply breaker for a containment spray pump failed to close when given a close command from the control room. The containment spray pump was declared inoperable, resulting in entry into a 72 hour shutdown limiting condition of operation. | The cause was a degraded pawl roller safety clip, which was found detached from its respective shaft. This was due to inadequate quality control by the vendor. |  | 1 - For information only, circuit breaker, containment spray, limiting condition of operation, preventive maintenance, pump, vendor | ER.3 , MA.2
WER ATL 16-0237 | 2015-09-04 | 2016-03-08 09:13 | Nine Mile Point-1 | Unplanned Reactor SCRAM Due to Main Steam Isolation Valve Not Reopening During Partial Closure Testing | Trending | During normal operation and while conducting partial closure surveillance on the outboard main steam isolation valve (MSIV), the valve did not automatically reopen as expected but continued to close. This condition caused a higher than normal flow rate in the opposite steam line, which caused a reactor protection system main steam line isolation signal and consequently triggered automatic reactor scram. | The direct cause was failure of the MSIV pilot operated valve. The root cause was inadequate pilot valve design susceptible to foreign material related binding. The contributing causes were manufacturing defects and binding of the pilot valve spring caused side loading on the spool which generated internal foreign material. |  | 1 - For information only, automatic scram, debris / crud, design criteria / design basis, foreign material, main steam isolation valve, pilot valve | ER.3 , MA.2
WER ATL 16-0234 | 2015-10-26 | 2016-03-07 14:56 | Vogtle-1 | Feedwater Heater Manway Leakage Caused Forced Outage | Trending | During startup after an outage, a manway on a feed water heater developed a steam leak. A forced outage was needed for repairs because the system could not be isolated due to a passing preheater isolating valve. | The apparent cause was that manway torque frequency did not account for fastener thermal cycling impact on the gasket. The previous corrective actions did not address manway leakage properly. A contributing cause was that the recurrent manway cover hot torques was not implemented due to inadequate work process management. |  | 1 - For information only, feedwater heater, leak, reactor shutdown, steam, torque | PI.2 , PI.3 , WM.1
WER ATL 16-0231 | 2015-10-20 | 2016-03-07 10:22 | Fermi-2 | Rigging Near Miss | Trending | A contractor worker after lowering the load moved the turbine building crane without direction from the signal man. This resulted in breaking of a sling and a 6000 pound capacity chainfall dropped 15 feet to the floor and landed near workers. | The cause was human error as the crane operator did not ensure that the rigging was disconnected prior to moving the crane and did not communicate with the signal man. | SOER 2008-1 Rec 2 | 2 - Important lessons, contractor, crane, human error, industrial safety, rigging | IS.1 , MA.1
WER ATL 16-0229 | 2015-10-27 | 2016-03-04 14:44 | Pickering-B6 | High Conductivity of Moderator Heavy Water Resulted in Delays to the Unit Outage | Trending | During an outage, a new guaranteed shutdown state (GSS) was achieved by draining moderator heavy water (D2O). While refilling the moderator, D2O conductivity was found elevated. The outage was extended by 5 days to rectify the problem. | The direct cause was nitric acid yielded from reaction of ozone and nitrogen oxides arising from air radiolysis in the calandria. The root cause was inadequate review process for new alignment in GSS. The contributing cause was lack of sensitivity to potential chemistry impacts and not involving chemistry group in the review process. | SER 2005-3 | 2 - Important lessons, chemistry, conductivity, heavy water, management oversight, moderator | CM.3 , EN.1
WER ATL 16-0228 | 2015-11-23 | 2016-03-04 14:22 | Monticello-1 | Reactor Trip due to Hydraulic Transient Pressure Surge | Trending | During normal operation, a loose wire caused a reactor recirculation pump trip, which coincided with a large spike in steam flow in one main steam lines. As a result, an isolation logic initiated, resulting in all eight main steam isolation valves to close. The reactor scrammed automatically. | The cause of the steam flow spike was foreign material in the form of a carbon steel nut in the common high pressure sensing instrument line. The most likely source for a nut in this location was that it occurred during original construction. |  | automatic scram, FME, instrumentation, main steam isolation valve, reactor recirculation pump, wiring | ER.1
WER ATL 16-0227 | 2015-09-28 | 2016-03-04 10:19 | Fermi-2 | Supplemental Worker Hand Injury While Using High Torque Wrench | Trending | While attempting to dislodge a hydraulic wrench from a crossover pipe flange bolt on the turbine deck, a supplemental workers thumb was struck by the tool. The worker was sent off-site for medical treatment and he received surgery to the hand. | The direct cause was inadequate strategy to release the bound hydraulic wrench. The apparent cause was lack of sufficient training of contractor workers to safely complete the task. |  | 1 - For information only, contractor, human error, industrial safety, injury, training | IS.1 , MA.1
WER ATL 16-0226 | 2015-07-24 | 2016-03-04 09:43 | Sequoyah-1 | Actuation Of The Generator Backup Relay Leads to Multiple Reactor Trips | Trending | During power operation, the main generator voltage fluctuations resulted in two sequential automatic scrams. | The direct cause was an improperly terminated wire for the protective drawer and control room null meter common power circuit. (The bottom of the three ring lugs was not captured by the terminal screw and was held in place by a combination of compression with the other two lugs. Unsecured wire 'sprang' from the bundle, dislocating and electrically disconnecting itself from the other two common wires). The root cause was inadequate standards about multi-wire terminations. Contributing was inadequacies in communication, troubleshooting plan and monitoring plan (problem investigation of first event was less than adequate but the decision to commence start up was made). |  | automatic scram, troubleshooting, turbine generator, voltage regulator, wiring | ER.1 , MA.1 , OP.1
WER ATL 16-0225 | 2015-07-07 | 2016-03-04 08:49 | Quad-Cities-1 | Core Spray Pipe Flaws Result in Outage Extension | Trending | During a refuelling outage, flaws indications were identified by ultrasonic testing in the core spray piping welds. This resulted in an outage extension of 26 hours. | The cause was lack of core spray piping flaws identification and trending programme combined with personnel turnover. Planned corrective actions were not implemented based on the conclusion that flaws were stable and not actively growing. |  | 1 - For information only, core spray, corrective maintenance, crack, weld | ER.4 , PI.3
WER ATL 16-0221 | 2015-12-03 | 2016-03-01 12:59 | North-Anna-1 | Incorrect 480 Volt Cable Cut During Cable Replacement | Trending | During replacement of a cable, an incorrect 480V cable was partially cut resulting in trip of the associated breaker and deenergisation of an intake structure heat trace panel. There was a potential for severe personnel injury or fatality. | The cause was inadequate management oversight. This resulted in lack of procedure use and adherence and inadequate risk assessment. |  | 1 - For information only, human error, industrial safety, management oversight, procedure adherence | IS.1 , MA.1 , WM.1
WER ATL 16-0218 | 2016-01-16 | 2016-03-01 10:54 | Darlington-4 | Primary Heat Transport System Leak at Shutdown Cooling Heat Exchanger | Trending | During normal operation and while cooling down the shutdown cooling (SDC) system after a unit maintenance (WER ATL 2016-0103), a leak was discovered at the channel cover on one of the two SDC heat exchange. The affected SDC heat exchanger had to be out of service for a repair, resulting in reduction of the SDC system redundancy. | The possible cause was the SDC heat exchanger channel-side gaskets were misaligned during re-installation in 2003 after repairs of a similar leak. |  | 1 - For information only, gasket, heat exchanger, heavy water, installation, leak, misalignment, residual heat removal | MA.1
WER ATL 16-0215 | 2015-12-31 | 2016-03-01 08:12 | Barakah-1 | Prime Contractor Failed to Comply with Licensing Commitments in Construction of Unit | Trending | During construction and while reviewing the licensing committed actions, it was identified that the contractor had failed to add height to certain seismic category 1 manholes of the four units. This resulted in a violation of the Unit 1 and 2 amended construction license and was reportable to the regulatory agency. | The cause was lack of understanding by the contractor regarding compliance with the licensing requirements for the design change. The changes were not incorporated in the existing drawings. Procedures did not contain adequate cautions to ensure licensing commitments were implemented. | SER 2005-3 | 1 - For information only, contractor, design change, drawing, procedure inadequacy | CM.3 , EN.1
WER ATL 16-0122 | 2016-02-01 | 2016-03-18 10:54 | Bruce-B-8 | Hydrogen discovered while drilling turbine rotor plug | Trending | During an outage and while performing generator rotor turbine end bore plug drilling activities and removing the generator rotor assembly from the main generator, unexpected hydrogen gas (H2) presence caused a H2 fire. A worker suffered burns to his arms, chest, and face requiring offsite medical attention. These activities occur when the generator rotor assembly is removed from the main generator and is located in an adjacent area in the Turbine hall. The presence of H2 in the bore of the generator rotor assembly was not expected | The root cause was that the design of the generator rotor chevron seals could not prevent all hydrogen ingress. The contributing causes were inadequate guidance, use of new OPEX and not proactive sharing of proprietary information from the vendor. |  | 2 - Important lessons, burn, design criteria / design basis, explosion, fire, hydrogen, industrial safety, turbine generator, vendor | IS.1 , OE.1 , WM.1

## Other
OE Reports
Event Summary (Monthly by Significance)
Report Identifier (click to view report) | Event Date | Published Date | Reference Unit | Event Title | Significance | OECT Summary | OECT Cause | OECT References | Keywords | PO and CS
WER TYO 16-0087 | 2016-01-18 | 2016-03-20 02:20 | Fukushima Daiichi-1 | Worker’s injury on site | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0086 | 2015-11-30 | 2016-03-20 02:09 | Fukushima Daiichi-1 | Injury of a worker on site | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0085 | 2015-12-09 | 2016-03-20 01:56 | Kashiwazaki Kariwa-7 | Loss of power supply to residual heat removal system shutdown cooling external isolation valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0084 | 2015-12-02 | 2016-03-20 01:46 | Kashiwazaki Kariwa-3 | A manually operated smoke ventilation window on the building external wall fail to open | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0083 | 2015-11-25 | 2016-03-20 01:35 | Fukushima Daiichi-1 | Leakage of cleaning liquid from the high-performance multi-nuclide removal equipment absorption tower | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0082 | 2015-11-19 | 2016-03-20 01:24 | Fukushima Daiichi-1 | Smoke generation in transformer primary high voltage panel | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0081 | 2016-01-15 | 2016-03-18 01:09 | Shin-Kori-1 | Smoke generation from compound building humidifier | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0080 | 2016-01-21 | 2016-03-16 16:18 | Hanul-4 | Smoke from Air Supply Fan at Chemical Laboratory in the Secondary Auxiliary Building | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0077 | 2016-01-14 | 2016-03-09 19:55 | Shin-Kori-1 | Fire Alarm due to Alternate Alternating Current Diesel Generator CO2 Storage Tank High-High Pressure Signal | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0076 | 2015-12-27 | 2016-03-09 18:54 | Hanul-6 | Plant Control System Remote #18 Chassis A/B Network Failure | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER TYO 16-0075 | 2015-11-11 | 2016-03-09 00:39 | Maanshan-2 | Main Feed Water Pump A governor valve was stuck during outage maintenance | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0073 | 2016-01-19 | 2016-03-04 01:43 | Hanul-4 | High-Pressure Feed Water Heater Drain Valve Positioner Failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER TYO 16-0071 | 2015-11-16 | 2016-03-02 03:10 | Maanshan-2 | The Control Rod Drive Mechanism drive rod bowed during setting of the reactor vessel head | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0189 | 2016-02-06 | 2016-03-18 09:01 | Heysham-A2 | Sodium hypochlorite bulk tank road tanker connection failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0188 | 2015-11-26 | 2016-03-18 08:17 | Atucha-2 | New Fuel Element damaged | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER PAR 16-0187 | 2015-11-26 | 2016-03-18 07:59 | Doel-4 | Spillage of HCl during discharge | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER PAR 16-0184 | 2015-11-10 | 2016-03-15 08:35 | Atucha-1 | Complex Access to a "new permanent plant modification" Documentation in Control Room | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0183 | 2016-01-14 | 2016-03-15 08:21 | Torness-2 | Turbine generator 2 trip block protection channel 1 failure | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0182 | 2015-10-17 | 2016-03-15 07:56 | Dungeness-B-1 | No isolation in place prior to work commencing | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0179 | 2015-10-15 | 2016-03-10 04:41 | Hongyanhe-3 | The concentrations of Oxygen in H8REA001, 002BA (demineralized water storage tank of Reactor Boron and Water Makeup system) exceed the limit for several times | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0177 | 2016-01-18 | 2016-03-09 10:40 | Heysham-A1 | Personal contamination following work on fuelling machine grab seal exchange | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER PAR 16-0175 | 2016-01-20 | 2016-03-08 08:34 | Heysham-A1 | Plastic Bag found on Fuelling Machine Nose Unit | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0174 | 2016-01-18 | 2016-03-08 08:27 | Heysham-A2 | Contamination spread associated with movement of a Short Shield Plug on Pile Cap | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0173 | 2015-11-16 | 2016-03-08 04:55 | Fangchenggang-1 | Wrong cutting led to water leakage from pipe downstream F1JPH562VE in Turbine Oil Tank Fire Protection System | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0172 | 2015-11-04 | 2016-03-08 04:30 | Fangchenggang-1 | Wrong spray of fire fighting water from pipe downstream of Turbine Oil Tank Fire Protection | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0171 | 2015-10-14 | 2016-03-08 03:43 | Fangchenggang-1 | Seizure of detectors of the In core instrumentation | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0170 | 2015-10-13 | 2016-03-07 09:17 | Cofrentes-1 | Unplanned LOCA signal in Div I when testing the logic of the valves of the automatic depressurisation system | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0169 | 2016-01-20 | 2016-03-03 08:38 | Brokdorf-1 | Shortfall in closed-direction of a primary circuit isolation valve via normal operations | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0167 | 2016-01-15 | 2016-03-03 08:09 | Heysham-A2 | Access in Water Box Unit 2 CW17B not suitable for use | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0166 | 2015-12-13 | 2016-03-03 07:42 | Doel-3 | Contamination of the floor around the main sewer drain sump of the tank room RR06 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0164 | 2016-01-08 | 2016-03-03 07:24 | Hunterston-B-1 | Reactor 3 Statutory Outage Work Window Performance | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0163 | 2016-01-06 | 2016-03-03 05:48 | Neckar-2 | Trip of the circulating fan SAL20 AN002 | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0162 | 2016-01-06 | 2016-03-03 05:40 | Heysham-A2 | Wetting of switchgear room due to broken pipe | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0160 | 2015-12-31 | 2016-03-03 04:45 | Torness-1 | Incorrect disposal of Tritiated Oil Samples from Radiochemistry Laboratory | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0158 | 2015-07-10 | 2016-03-03 04:12 | Almaraz-2 | As-found tests on a pressuriser safety valve performed in the laboratory with the result below the -3% required. | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER PAR 16-0157 | 2015-12-31 | 2016-03-01 11:34 | Tihange-3 | Erroneous Transfert of boric Acid | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0155 | 2015-12-22 | 2016-03-01 10:54 | Heysham-B2 | Adverse Trend – Overdue Assignments in Corrective Action Programme | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0152 | 2015-12-14 | 2016-03-01 10:22 | Doel-1 | Floor contamination as a result of the overflow of a liquid radwaste tank. | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0150 | 2015-12-09 | 2016-03-01 10:02 | Heysham-B1 | Reactor 7 Loss of Reactor Gas | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 16-0147 | 2015-10-21 | 2016-03-01 08:25 | Embalse-1 | Improper alignmentof one Ionic Exchanger (IX) Columns of the Primary Heat Transport System | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 15-0651 | 2015-06-13 | 2016-03-23 05:14 | Forsmark-2 | Ground fault in 110V DC system | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 15-0586 | 2015-05-30 | 2016-03-23 05:40 | Brokdorf-1 | Damage of a draining pipe in the main steam system during a periodic test within the shutdown-phase of the plant | Other | See summary below. | See causes below. |  | 1 - For information only
WER PAR 14-0308 | 2014-01-09 | 2016-03-23 06:23 | Neckar-1 | No connection of the transformer 3CT32 at a periodic testing | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 16-0049 | 2015-09-17 | 2016-03-21 23:58 | Beloyarsk-4 | With Beloyarsk Unit 4 in a Shutdown Condition, Gate Seal Degradation was Observed on Steam Generator Pilot and Safety Valves | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 16-0047 | 2015-11-17 | 2016-03-11 06:00 | Kalinin-1 | A Failure of the Control Circuit for Turbine Control System with Turbine Revolution Adjustment Switch Due to a Loss of Electrical Connection Between Panels | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 16-0043 | 2015-10-31 | 2016-03-11 05:31 | Novovoronezh-4 | Main Stop Valve Cover Sleeves Had to be Replaced Due to Sleeve Overlay Defects Identified During In-service Inspection Conducted During the 2015 Outage | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 16-0041 | 2015-10-12 | 2016-03-11 05:20 | Novovoronezh-3 | 500/220 kV Autotransformer No.2 Tripped from Transformer Differential Protection Actuation on a Spurious Signal | Other | See summary below. | See causes below. |  | 1 - For information only
WER MOW 16-0039 | 2015-12-28 | 2016-03-08 23:08 | Temelin-1 | Glowing in Wiring of Steam Developer | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0325 | 2015-10-13 | 2016-03-29 15:37 | Catawba-1 | Breakers Not Placed in Off Position When Placing a Clearance | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0324 | 2015-06-20 | 2016-03-29 14:03 | Diablo Canyon-1 | 4KV Vital Switchgear Supply Fan Taken Out of Service for Repair due to High Vibration | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0323 | 2015-08-07 | 2016-03-29 13:34 | Fermi-2 | Motor Control Center Position Disconnect Found in Off Position | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0321 | 2015-10-29 | 2016-03-29 13:03 | Comanche Peak-2 | Individual Received Dose Rate Alarm While Removing a 55 Gallon Drum from Reactor Cavity | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0320 | 2015-08-30 | 2016-03-29 12:55 | Comanche Peak-1 | Operator Failed to Close Isolation Valve for an Eyewash Station During Clearance Placement | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0318 | 2015-11-14 | 2016-03-29 10:38 | Arkansas-Nuclear-One-2 | Improperly Initialized Rhodium Number Densities in the Physics Code led to Errors in the Incore Detector Signal to Power Conversion | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0316 | 2016-01-29 | 2016-03-29 10:09 | Cernavoda-1 | Failure to place Shutdown System #1 Channel F in Test due to Relay Failure | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 16-0312 | 2015-10-12 | 2016-03-29 08:33 | Comanche Peak-2 | Nitrogen Supply Vent Valve That Was Required To Be Closed Was Found Open On A Clearance Release | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0311 | 2015-12-15 | 2016-03-29 08:28 | Perry-1 | Misposition of Service Water Chlorination Valve Results in a Violation | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0308 | 2015-11-07 | 2016-03-28 15:48 | South-Texas-1 | Reactor Coolant System Drain Valve Found Out Of Position | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0307 | 2015-12-31 | 2016-03-28 15:32 | Catawba-1 | Boric Acid Transfer Pump Suction Valve Found Closed | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0306 | 2015-08-06 | 2016-03-28 15:21 | Fermi-2 | Ground on Combustion Turbine Generator Output Transformer | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0305 | 2015-10-08 | 2016-03-28 14:42 | Calvert-Cliffs-1 | Unexpected Krypton Release during Spent Fuel Canister Vacuum Drying Process | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0301 | 2015-12-17 | 2016-03-28 14:09 | Calvert-Cliffs-1 | Resin Misclassified as Solid in Radioactive Waste Shipping Documents | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0300 | 2015-10-02 | 2016-03-28 14:03 | Calvert-Cliffs-2 | Level 3 Misposition – Zinc Add Valve Found Closed | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0298 | 2015-06-17 | 2016-03-28 13:11 | Braidwood-2 | Service Air Compressor Emergency Shutoff Switch Bumped | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0294 | 2016-02-06 | 2016-03-28 08:48 | Darlington-2 | West Reactor Area Bridge Unavailable | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0293 | 2015-09-29 | 2016-03-24 14:02 | Callaway-1 | Relay Replacement Tagout Did Not Identify All Power Supplies | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0291 | 2015-10-21 | 2016-03-24 13:49 | Oconee-3 | Service Water Piping Defect Created During Line Stop Installation | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0290 | 2015-10-26 | 2016-03-24 13:37 | Mcguire-2 | Steam Generator Blowdown Pump Seal Water Supply Discovered Isolated | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0289 | 2015-11-03 | 2016-03-24 13:33 | Three Mile Island-1 | Non-compliant Pre-outage Staging of Equipment Inside Containment | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0288 | 2015-11-04 | 2016-03-24 13:27 | Fermi-2 | Spurious Oil Flow Alarms on 13.8kV Transformer due to Improper Phasing of Emergency Power Source | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0287 | 2015-11-18 | 2016-03-24 10:59 | Palo-Verde-2 | Inadequate Post-outage Valve Lineup Results in Lifting an Auxiliary Steam Relief Valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0285 | 2016-03-04 | 2016-03-24 10:24 | Bruce-A2 | Incorrect Boiler Steam Relief Valve Opened Due to Error-Likely Design of Handswitch | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0284 | 2016-02-09 | 2016-03-24 10:12 | Bruce-A4 | Outage Lessons Learned – Spacer Location and Relocation Campaign During Unit 4 Planned Outage | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0280 | 2015-12-01 | 2016-03-22 14:44 | Beaver-Valley-1 | Maintenance Service Valves Closed on Chilled Water Unit to Isolate Freon Leak Results in Mispositioning Event | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0279 | 2015-12-11 | 2016-03-22 14:31 | South-Texas-1 | Misaligned Open Condensate Drain Valve Found During System Fill After Outage | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0277 | 2016-02-17 | 2016-03-22 12:13 | Koeberg-1 | Specification requirements for Radiation Waste Material 210 liter steel drums not met | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0275 | 2015-11-23 | 2016-03-22 11:53 | Fermi-2 | Distribution Panel Supply Breaker Tripped While Restoring from Surveillance | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0273 | 2016-01-13 | 2016-03-22 09:50 | Susquehanna-1 | Component Mispositioning During Reactor Recirculation Flow Transmitter Calibration Surveillance | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0270 | 2016-03-08 | 2016-03-22 09:02 | Point Lepreau-1 | Wrong Pushbutton Depressed During Control Room Testing | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0267 | 2016-02-03 | 2016-03-18 12:09 | Bruce-B-7 | Unit 7 Class III Transformer tripped on sudden pressure protection | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0266 | 2016-01-27 | 2016-03-18 12:06 | Bruce-B-8 | Incorrect installation of temporary water valve isolation | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0263 | 2016-01-08 | 2016-03-16 14:03 | Cernavoda-1 | Repetitive trip of 1-68231-ROPT-11F loop during “ROPT detector calibration checks” routine execution | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0260 | 2015-06-13 | 2016-03-15 13:32 | Harris-1 | Moisture Separator Reheater Temperature Control Valves Shut Due To Improperly Calibrated Voltage To Pressure Transducer | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0253 | 2015-11-18 | 2016-03-14 13:27 | Darlington-3 | Outage Work Protection Violation | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0252 | 2016-01-26 | 2016-03-14 13:22 | Darlington-1 | Hydraulic Circuit Unable to Pressurize Results in Level 3 Impairment of Emergency Coolant Injection System | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0250 | 2015-11-03 | 2016-03-10 09:59 | Cook-1 | Spent Fuel Pool Building Ventilation Charcoal Filter Failed Efficiency Test | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0249 | 2016-02-12 | 2016-03-10 09:14 | Cernavoda-1 | Pneumatic valve 1-7169-PV103 fails to open due to isolation of the air supply | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0248 | 2016-02-01 | 2016-03-10 09:03 | Cernavoda-1 | The isolation valve of level transmitter 1-63470-LT1 found blocked in the closed position due to excessive force used during valve maneuvering | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0247 | 2016-01-11 | 2016-03-10 08:56 | Cernavoda-1 | Defect of the “cascade” pressure control loop of the pegging steam system | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0246 | 2015-10-22 | 2016-03-09 13:51 | Oconee-3 | Depressurization of Unit 3 Auxiliary Steam (AS) Header | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0245 | 2015-10-08 | 2016-03-09 13:41 | St.-Lucie-2 | Hot Chemistry Lab Smoke Due to Exothermic Chemical Reaction | Other | See summary below. | See causes below. |  | 2 - Important lessons
WER ATL 16-0244 | 2015-11-06 | 2016-03-09 13:35 | Turkey-Point-3 | Smoking Bucket in the Paint Storage Facility | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0243 | 2015-10-21 | 2016-03-09 13:27 | Prairie-Island-2 | Containment Sump Pump Switches Mispositioned | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0242 | 2015-12-26 | 2016-03-09 13:11 | Susquehanna-1 | Entry into a High Radiation Area Boundary | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0241 | 2016-01-01 | 2016-03-09 13:03 | Davis-Besse-1 | Clean Waste Monitor Tank Valves Out of Position While Performing Clean Waste System Operating Procedure | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0236 | 2015-11-29 | 2016-03-08 08:54 | Salem-2 | Wrong Shim Installed on Main Steam Valve | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0235 | 2015-11-05 | 2016-03-07 15:32 | Millstone-2 | Red Tagged Boundary Valves Failed to Maintain Isolation | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0230 | 2016-01-15 | 2016-03-04 14:49 | Pickering-A4 | Inadequate Isolation of Fire Protection Sprinkler System Piping Resulted in a Work Protection Violation | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0224 | 2016-02-09 | 2016-03-02 15:42 | Point Lepreau-1 | Transport Truck Load Struck and Disconnected Low Voltage Overhead Communication Wire | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0223 | 2014-08-07 | 2016-03-01 14:09 | Fermi-2 | Pressure Control System on Unitized Actuator Fails to Maintain PressurePressure Control System on Unitized Actuator Fails to Maintain Pressure | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0220 | 2015-12-04 | 2016-03-01 11:59 | Perry-1 | Supplemental Employee Performing Demolition Activities as part of a Bathroom Upgrade Received an Injury that Required Medical Treatment. | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0219 | 2015-12-11 | 2016-03-01 11:15 | Perry-1 | Clearance Event during Condensate Filter B Work - Inadequate Equipment Label | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0217 | 2016-02-08 | 2016-03-01 10:49 | Koeberg-1 | The Unit 1 Circulating Water Filtration System number 2 screening drum was inadvertently stopped as a result of the associated emergency stop push button being activated. | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0216 | 2016-02-02 | 2016-03-01 08:15 | Barakah-1 | Personnel Injury in Office Area | Other | See summary below. | See causes below. |  | 1 - For information only
WER ATL 16-0203 | 2016-01-24 | 2016-03-16 14:51 | Bruce-B5 | Maintenance Shop – Lathe Medically Treated Injury | Other | See summary below. | See causes below. |  | 1 - For information only