| On Behalf of Customer |  | On Behalf of Customer |
| --- | --- | --- |
| BNPP-1 «____» ______________2018 |  | NPPD «____» ______________2018 |
| On Behalf of Contractor |  | On Behalf of Manufacturer |
| JSC «TVEL» Vice-President on Scientific and Technological Activities A.V. Ugryumov «____» ______________2018 |  | Deputy Director on nuclear power and nuclear technologies, NRC «Kurchatov Institute» Yu.M. Semchenkov «____» ______________2018 |

INSPECTION PROGRAM

Subject of the work:

Inspection of the In-Core Instrumentation System (ICIS) of the Bushehr NPP unit 1 to initiate upgrading of the Software-hardware complex.

- Inspection objective: identification of the ICIS upgrading scope. The scope of work on the development of documentation for the ICIS upgrading, as well as the scope of upgrade will be determined based on the results of inspection.

- General information about the inspection

| Inspection site | Site of Bushehr NPP, the Islamic Republic of Iran |
| --- | --- |
| Time period for execution of the work | Till 11.04.2018 |
| Manufacturer and executor of the work to inspect ICIS system | NRC :Kurchatov Institute” |
| Supplier of ICIS Software-hardware complex (SHC) to the Customer (End User) | JSC “Tvel” |
| Customer (End User) | NPPD, Bushehr NPP |
| Number of specialists necessary for inspection | 2 specialists |
| Time necessary for inspection | 5 working days at the site of Bushehr NPP |
| Maximum time period of the visit to the Bushehr NPP site | No more than 14 calendar days since the day of arrival to the Islamic Republic of Iran |
| Tools and equipment necessary for the inspection will be given by the End User | Tape-measure, electric flash-light. |

- Scope of inspection

In the frames of this work it is necessary: to develop the scope of inspection with indication of the monitoring methods, to identify the list of auxiliary equipment to perform the inspection, on the results of which the reporting document will be developed.

| Stage of work | Type of work |
| --- | --- |
| Preparatory work, study of documents | - Identification of components, completeness of ICIS equipment for inspection |
|  | - Identification of the scope of documentation presented for inspection, listing of the documents, presented for inspection. During inspection it is necessary to use operating documents supplied with the item, as well as electric diagrams and cable records. |
| Direct inspection of ICIS equipment а) in ZK2 building б) in ZK1 building в) in ZE building | Assessment of the ICIS equipment physical state in buildings ZK2, ZK1, ZE. |
|  | Identification of the possibility of putting new equipment in the existing standard locations without additional adaptation. |
|  | Assessment of the state of power supply cables, grounding. |
|  | Study of the state of optical and wire communication lines from the standpoint of re-using them, possibility of replacement (if necessary), analysis of the amount of additional cables. |
|  | - Presence of the cable length slack, necessary for replacement of equipment. |
|  | - Checking of the state of terminal pairs, detachable connections from the standpoint of reliable coupling. |
| Contacts with Bushehr NPP personnel | - Review of proposals made by Bushehr NPP operating personnel: - Including into ICIS of additional workstations, other equipment, connection of them to standard equipment, laying of additional cable communication lines |
| Preparation of report based on inspection results | Preparation of report based on inspection results. Amount of data in the report shall be sufficient to identify the scope of upgrading of ICIS SHC based on the results of inspection |

- Required assistance from the Customer (End User) to the specialists of Manufacturer:

•	Reception of the entrance vise (letter of invitation);

•	Transfer from the International Imam Khomeini airport (Islamic Republic of Iran, Teheran) to the town of Bushehr, to the place of residence of the Manufacturer specialists in the village of the Bushehr NPP and back;

•	Provision of suitable accommodation in the village of the Bushehr NPP, as well as daily transportation of the Manufacturer specialists from the place of residence to the Bushehr NPP site, unit 1 and back;

•	Ensuring access of the Manufacturer specialists to the Bushehr NPP site in order to perform the work;

•	Ensuring rendering of other potential services related to performing the work by the Manufacturer specialists.