Enclosure №1

to letter No.________________

dd. «____» ___________ 2018

TECHNICAL ASSIGNMENT

for works performance on topic:

«Elaboration and implementation of emergency response documentation for Bushehr NPP power unit No.1 in symptom-based emergency operating instruction form (SBEOI)»

- Description of works

Elaboration and implementation of emergency response documentation set for Bushehr NPP power unit No.1 in symptom-based emergency operating instruction form.

- Purposes and goals

The purpose of the works is elaboration and implementation of emergency response documentation set for Bushehr NPP power unit No.1 in symptom-based emergency operating instruction form for BNPP-1 safety assurance at design basis and beyond design basis accidents elimination at the power unit all initial states based on the spent fuel pool state, severe accidents included.

- Works performance deadlines

The dates of commencement and completion of the works shall meet the Time program (Appendix 1).

- Executive

Joint Stock Company Atomtechexport (JSC ATEX).

Co-executives: NRC Kurchatov Institute, OKB “GIDROPRESS”, JSC “Atomenergoproject” and other companies of the branch.

- Works performance input data

5.1 Bushehr NPP Unit No.1 design documentation with accounted amendments and supplements.

5.2 Final Safety Analysis Report (FSAR).49.BU.1 0.0.ОО.FSAR.RDR001.

5.3 Requirements of regulatory documentation in effect in Russia used during commissioning and operation of VVER-1000 NPP.

5.4 IAEA Safety regulations requirements «Programs on severe accidents management at the nuclear power plants. Safety Guide. No. NS-G-2.15».

5.5 BNPP-1 probabilistic safety analysis of the 1st and 2nd level.

5.6 Technical Specification of Safe Operation.52.BU.1 0.00.AB.WI.ATEX.001.

5.7 Design and manufacturer’s documentation to equipment and APCS components to that equipment with accounted amendments and supplements.

5.8 Updated operating documentation (accounted new norms and regulations, NPP modifications, alterations in organizational structure, operation experience etc.).

The Principal shall provide access to the materials, as well as render assistance to the Executive in the required technical documentation selection in compliance with items 5.1÷5.8 of this Technical Assignment within the scope required for work performance. Should the required technical documentation is in the English language or in Farsi, the Principal shall perform its translation into the Russian language at its own expense.

- Stages and phases of works

| StageNo. | Description of works | Deadlines |  | List of reporting documentation | Executive |
| --- | --- | --- | --- | --- | --- |
|  |  | startup date | end date |  |  |
| 1 | Elaboration of Manual for writing of emergency response documentation set procedures and instructions | Т0 | Т0+5 months | - Manual for writing of emergency response documentation set procedures and instructions. Performed works certificate | ATEX |
| 2 | Database formation for accidents substantiating calculations performance | Т0 | Т0+5 months | - Report “Database formation for accidents substantiating calculations performance”. - Performed works certificate | ATEX TAVANA |
| 3 | Elaboration of emergency response documentation set for Bushehr NPP power unit No.1 (Rev.0) |  |  |  |  |
| 3.1 | Elaboration of an accident elimination instruction (AEI) for all states of the power unit (Rev.0) | Т2 | Т2+12 months | - AEI (Rev.0) Performed services certificate | ATEX |
| 3.2 | Elaboration of beyond-design basis accident management guide (BDBAMG) for all states of the power unit (Rev.0) | Т2 | Т2+12 months | - BDBAMG (Rev.0) Performed services certificate | ATEX |
| 3.3 | Elaboration of severe accident management guide (SAMG) for all states of the power unit | Т2 | Т2+12 months | - SAMG (Rev.0) Rendered services certificate | ATEX |
| 4 | Elaboration of feasibility study |  |  |  |  |
| 4.1 | Elaboration of AEI feasibility study | Т2 | Т2+9 months | - AEI feasibility study. Performed services certificate | ATEX FTC |
| 4.2 | Elaboration of BDBAMG feasibility study | Т2 | Т2+12 months | - BDBAMG feasibility study. Performed services certificate | ATEX FTC |
| 4.3 | Elaboration of SAMG feasibility study | Т2 | Т2+14 months | - SAMG feasibility study. Performed services certificate | ATEX FTC |
| 5 | Elaborated documents verification and validation performance | Т3.3 | Т3.3+4 months | - Report with recommendations on emergency operation documentation set modification. Performed services certificate | ATEX |
| 6 | Emergency documentation agreeing by NPP and RP design developers, BNPP, NNSD |  |  |  |  |
| 6.1 | AEI agreeing by NPP&RP design developers. AEI amendment | Т5 | Т5+7 months | - Agreed AEI with copies of letters on agreeing by NPP and RP design developers. Performed services certificate | ATEX FTC OKB HP AEP |
| 6.2 | BDBAMG agreeing by NPP&RP design developers. BDBAMG amendment | Т5 | Т5+7 months | - Agreed BDBAMG with copies of letters on agreeing by NPP and RP design developers. Performed services certificate | ATEX FTC OKB HP AEP |
| 6.3 | SAMG agreeing by NPP&RP design developers. SAMG amendment | Т5 | Т5+7 months | - Agreed SAMG with copies of letters on agreeing by NPP and RP design developers. Performed services certificate | ATEX FTC OKB HP AEP |
| 6.4 | AEI agreeing by BNPP, NNSD. AEI amendment | Т6.1 | Т6.1+6 months | - Agreed AEI. Performed services certificate | ATEX BNPP NNSD |
| 6.5 | BDBAMG agreeing by BNPP, NNSD. BDBAMG amendment | Т6.2 | Т6.2+6 months | - Agreed BDBAMG. Performed services certificate | ATEX BNPP NNSD |
| 6.6 | SAMG agreeing by BNPP, NNSD. SAMG amendment | Т6.3 | Т6.3+6 months | - Approved SAMG. Performed services certificate | ATEX BNPP NNSD |
| 7 | BNPP personnel training | Т6.6 | Т6.6+6 months | - BNPP personnel is trained | ATEX |
| 8 | Translation of the elaborated documentation into English | Т1 | Т7 | - Documents translated into English Performed services certificate | ATEX |
| 9 | Amendment of FSAR. Amended portion approval by the NPP and RP design developers | Т6.6 | Т6.6+6 months | - Amendment notifications are approved by the NPP and RP design developers. Performed services certificate | ATEX FTC OKB HP AEP |

- Description of works

If any problem areas are revealed during work performance, which require modernization works performance, as well as the project drawbacks, such problems shall be mentioned in the reports.

7.1 Elaboration of Manual for writing of emergency response documentation set procedures and instructions

Manual for writing of emergency response documentation set procedures and instructions shall contain the following tentative list of sections:

1) Approaches to elaboration of accident management instructions.

2) Methods of accident management procedures and instructions elaboration.

3) Requirements to structure and content of the accident management procedures and instructions set.

4) Requirements to database formation for accidents substantiating calculations performance.

5) The main principles for emergency response documentation elaboration.

6) General principles of AEI, BDBAMG, SAMG organizational aspects (assessment, decisions taking and implementation).

7) Justification of using "symptom-based" approach on methodological basis adopted by Westinghouse (USA) at elaboration of “Function Restoration Guideline” (FRG) comprised into “Emergency Response Guideline”  (ERG) for BNPP-1.

The final document shall be «Manual for writing of emergency response documentation set procedures and instructions for Bushehr NPP power unit No.1.».

This document shall be agreed upon by the Principal.

The work will be carried out by JSC ATEX personnel.

7.2 Database formation for accidents substantiating calculations performance

This stage works performance shall be based on the following requirements:

1) while elaborating the database for accidents substantiating calculations performance one shall rely on the basic data of Bushehr NPP Unit No.1 parameters in the framework of the existing design;

2) in order to meet the project design, data on the reactor plant operating equipment, secondary circuit, containment, auxiliary systems including normal operation systems, protective, isolating, supporting systems shall be provided;

3) equipment and systems parameters and performances shall be described;

4) the database for accidents substantiating calculations shall also contain the following information (the information is approximate, it may be supplemented during the information accumulation):

- neutron-physical characteristics;

- geometrical information on the reactor plant, secondary circuit and containment within the scope required for thermal hydraulic calculations and severe accidents calculations;

- weights of equipment components; weights of fuel in the fuel element and fuel element casing, weights of fuel assembly steel components, weights of internals (especially important for severe accidents analysis);

- tolerance and response time of metering facilities;

- primary and secondary circuits valves;

- flow charts (may be simplified);

- algorithms of controllers, valves, safety valves, protections and interlocks operation;

- algorithms of level gages (PRZ, SG) indices generation by differential pressure gages etc.

The works shall be carried out based on the information contained in the design and operational documentation as well as on the data obtained at the power unit.

The final document shall be Report «Database for Bushehr NPP power unit No.1 accidents substantiating calculations performance».

This document shall be agreed upon by the Principal.

The works are carried out by JSC ATEX and TAVANA Co. personnel. For these works performance,  JSC ATEX shall dispatch to BNPP Site one 6B grade specialist for 1 month’s period. TAVANA Co. will assign two specialists (to be subordinated to Russian specialist) qualified as at least reactor compartment shift supervisor and turbine compartment shift supervisor.

7.3 Elaboration of emergency response documentation set for Bushehr NPP unit No.1 (Rev.0)

Sets of AEI, BDBAMG, SAMG emergency response documentation shall be elaborated in symptom-based emergency operating instruction format on Westinghouse methods.

The sequence of personnel actions shall be produced in a two-column form maximum briefly and understandable:

- in the left column named as «Action/Expectation», “the simplest” actions to reach the  objective are entered;

- in the right column named as “No result” alternative actions are offered for the case the left column action is for some reason impossible to be performed.

Conclusions and results of AEI, BDBAMG, SAMG justifying calculations shall be included into the AEI, BDBAMG, SAMG procedures and instructions as a basis for control actions decisions taking.

The emergency response documentation text shall be highly human-readable. The content shall be logically consistent and unambiguous.

AEI, BDBAMG, SAMG text shall contain specific ways of parameters monitoring on which control actions decisions are taken.

AEI, BDBAMG and SAMG texts content shall clearly define decisions taking by SSU (emergency director) related to changeover from one instruction to another (AEI, BDBAMG, SAMG)

AEI, BDBAMG, SAMG text shall be analyzed in terms of the information sufficiency, errors probability decrease and invariability of understanding. In so doing the following criteria shall be used:

- specificity, shortness, narration concreteness and information sufficiency;

- accuracy of technical information presentation from the source documents;

- logical presentation of personnel actions during operations performance.

BNPP-1 AEI, BDBAMG, SAMG shall take into consideration Bushehr NPP organizational structure peculiarities, distribution of officials and subdivisions’ functions.

Cost of each document development (AEI, BDBAMG, SAMG) is a sum of the following components:

70% - document (AEI, BDBAMG, SAMG) elaboration for all Power Unit conditions (Rev.0);

20% - document (AEI, BDBAMG, SAMG) amendment by results of agreeing with NPP and RP design developers;

10% - document (AEI, BDBAMG, SAMG) amendment by results of agreeing with BNPP, NNSD.

The final documents shall be the following:

«Accident elimination instruction (AEI) for all power unit states (Rev.0)».

«Beyond-design basis management guide (BDBAMG) for all power unit states (Rev.0)».

«Severe accident management guide (SAMG) for all power unit states (Rev.0)».

The works shall be carried out by JSC ATEX personnel.

7.4 Feasibility study elaboration

7.4.1 The feasibility study shall prove the following:

- accuracy of steps sequence (reached objectives);

- substantiation of the main and alternative strategies application;

- actuality of required conditions formation for the steps implementation, success in results achievement within the acceptable time limits.

- survivability of the equipment and instrumentation in severe accident conditions;

- accessibility and habitability of the physical locations of the personnel teams as well as of the emergency director under severe accident conditions in NPP premises;

- availability of possibility for associated reduction of risks at NPP and dominant scenarios mitigation at severe accidents.

Calculations shall be carried out using software tools certified for application in the established sequence.

The final documents shall be the following:

«AEI feasibility study».

«BDBAMG feasibility study».

«SAMG feasibility study».

The feasibility study of all emergency instructions under elaboration shall incorporate the technical basis (substantiation), including analyses, calculations and engineering assessments.

The works shall be carried out by JSC ATEX personnel, personnel of NRC Kurchatov Institute, OKB "GIDROPRESS", JSC "Atomenergoproject" involved.

7.5 The elaborated documents verification and validation performance

7.5.1 The main definitions:

1. According to article 3.8.4. of GOST R ISO 9000-2001, term «Verification» means confirmation that the established requirements have been satisfied based on objective evidences submission.

Verification is determination whether the developed product quality meets the declared requirements of the regulatory documents for this product.

2. According to article 3.8.5. of GOST R ISO 9000-2001, term  «validation» means confirmation, based on objective evidences submission,  that the requirements intended for specific use or application are predetermined exactly and in the full scope.

Validation is CORRECTNESS confirmation for a document, method, procedure, calculation and etc. The main meaning of adjective “valid” is "having legal force".

7.5.2 The verification principle covers consideration of the criteria specifying the following:

1. that the input conditions or symptoms causing employment of the emergency response documentation set are correct, sufficient for the emergency response documentation set necessity identification and at the same time void of excess information.

2. that the content and allocation of the response documentation set section steps, warnings and comments are implemented in compliance with the source documents. (at the SBEOI writing stage inadmissible deletion, transposition or alteration of the information as compared with that contained in the source documents may occur. That is why in this part accuracy of source documents information entered for SBEOI is under strict supervision).

3. accuracy of rated and converted quantitative values. (Quantitative values are obtained through mathematical operations to the predetermined design values or equations. These numerical values shall be subject to accuracy assessment - both source values and mathematical operations to them. Source value of the variable is taken from the source document and the supervisor shall make sure that during different mathematical operations no error was committed).

4. whether the hardware (control elements, I&C) and equipment mentioned in the emergency response documentation set correspond to their actual state at Bushehr NPP-1.

7.5.3 The validation principle covers consideration of the criteria which enable:

1. to confirm accuracy of the information on the power unit hardware operation in emergency situation and information accuracy by the systems and equipment response to operator’s actions, set forth in the emergency response documentation set.

2. to confirm the document compatibility with the operating personnel shift manning and with administrative policy at Bushehr NPP in terms of the operating personnel’s individual responsibility and duties.

In the course of AEI, BDBAMG and SAMG verification and validation it will be required to perform substantiating analysis of the elaborated documents for correspondence to the established requirements.

In case of FSS non-readiness related to considered modes simulation for the moment of validation performance, it is allowed to perform validation using calculation and analytical method at MCR, ECR.

Upon verification and validation stage completion, introduction of amendments  to the documents (AEI, BDBAMG, SAMG) related to accounting of new norms and rules, NPP modifications, changes in the organizational structure, operation experience and etc. shall be terminated. Further amendments related to accounting of new norms and rules, NPP modifications, changes in the organizational structure, operation experience and etc. shall not be introduced.

The final document shall be a report with recommendations on the emergency response documentation set amendment.

The works shall be carried out by JSC ATEX personnel with involvement of the personnel from the outside companies certified for these works performance. To perform these works, JSC ATEX shall dispatch to BNPP one specialist of 6В grade for 3 months period, two specialists of 7В grade for 3 months period and one specialist of 9В grade for 2 months period.

7.6 Emergency response documentation approval by NPP and RP design developers, BNPP and NNSD

7.6.1 Emergency response documentation approval by NPP&RP design developers

The works shall be carried out in compliance with the RF norms and regulations in effect in the atomic energy industry (NP-001-15, NP-082-07 etc.) and approved regulatory documents as well as taking into consideration IAEA safety regulations «Programs on severe accidents management at nuclear power plants. Safety Guide. No. NS-G-2.15».

Documents «Accident elimination instruction (AEI) for all power unit states (Rev.0)», «Beyond-design basis management guide (BDBAMG) for all power unit states (Rev.0)», «Severe accident management guide (SAMG) for all power unit states (Rev.0)» amended by results of considering recommendations provided in the report on verification and validation   shall be submitted to NPP&RP design developers for approval along with respective feasibility studies.

The documentation signed by the developers shall be submitted for approval in PDF and editable MS Word formats.

The documents amended according to comments shall be forwarded for repeated approval with summary of replies to comments attached. All alterations introduced to the amended documents shall be color highlighted.

The final documents shall be the following, approved by NPP&RP design developers:

«Accident elimination instruction (AEI) for all power unit states».

«Beyond-design basis management guide (BDBAMG) for all power unit states».

«Severe accident management guide (SAMG) for all power unit states».

The works shall be carried out by JSC ATEX personnel, JSC “Fizika Toplivnykh Ciklov”, OKB Gidropress, JSC Atomenergoproekt personnel involved.

7.6.2 Emergency response documentation agreeing by BNPP, NNSD

Documents «Accident elimination instruction (AEI) for all power unit states (Rev.0)», «Beyond-design basis management guide (BDBAMG) for all power unit states (Rev.0)», « Severe accident management guide (SAMG) for all power unit states (Rev.0)» in the Russian and English languages agreed by NPP&RP design developers along with copies of letters of agreement shall be submitted to BNPP and NNSD for approval.

The Principal may involve an independent organization having required permitting certificates and licenses for the emergency documentation reviewing.

The final documents shall be the following, approved by BNPP, NNSD:

«Accident elimination instruction (AEI) for all power unit states».

«Beyond-design basis management guide (BDBAMG) for all power unit states».

«Severe accident management guide (SAMG) for all power unit states».

Official comments of BNPP, NNSD (enclosed to the covering letter) provided in the English language will be accepted for consideration.

A summary of replies shall be drawn up by results of reviewing the comments, which may be reviewed at the consensus meeting.

The works shall be carried out by JSC ATEX, BNPP, NNSD personnel.

7.7 Training of BNPP personnel including operating, engineering, maintenance, technical support group, TC personnel

Specialists of the following categories shall be trained to the accident management using tutorials developed by JSC ATEX (in the form of programs with different degrees of training breakdown):

- managerial staff for prevention and elimination of emergency situations at NPP;

- accident management group engineers who shall directly use emergency response documentation set if required;

- licensed personnel, MCR personnel and power unit shift supervisors;

- members of ES prevention and elimination system group associated with accident management strategy elaboration and emergency response actions implementation, who do not participate directly in the emergency response documentation set employment.

Different categories of specialists and personnel require training courses with different degrees of training depth and breakdown. In the whole, each training course can be divided into the following topic groups:

- accident phenomenology (acquisition and consolidation of accidents source information);

- basis for emergency response documentation use;

- detailed study of MCR emergency response documentation set instructions;

- detailed study of the emergency response documentation set elements employed by accident management group.

At this stage works performance includes the following:

1 Educational materials compilation (textbooks, programs for theoretical and practical training provision).

2. BNPP personnel theoretical training.

3 BNPP personnel training at MCR or ECR (FSS related to considered modes simulation) by way of operating personnel actions simulation.

The Russian language shall be working (spoken) language at this stage of works. Translation inot English or Persian shall be ensured by the Principal.

The works shall be carried out by JSC ATEX personnel with involvement of the personnel from the outside companies certified for these works performance. To perform these works, JSC ATEX shall dispatch to BNPP four specialist of 8В grade for 2,5 months period.

7.8 Translation of the elaborated documentation into the English language

Work performance at this stage includes translation of the following documents into the English language:

«Manual for writing of emergency response documentation set procedures and instructions».

Report “Database for performing substantiating calculations of BNPP-1 emergencies”

«Accident elimination instruction (AEI) for all states of the power unit».

«Beyond-design basis accident management guide (BDBAMG) for all states of the power unit».

«Severe accident management guide (SAMG) for all states of the power unit».

«AEI feasibility study».

«BDBAMG feasibility study».

«SAMG feasibility study».

Report on verification and validation results with recommendations related to the emergency response documentation set amendment.

Educational materials (textbooks, programs on theoretical and practical training provision).

The abovementioned documents revised by results of emergency documentation agreement with NPP and RP design developers, BNPP, NNSD will be also translated into the English language.

The works shall be performed by JSC ATEX personnel.

7.9 FSAR amendment

In order to bring design documentation (FSAR) and emergency response documentation set into compliance, necessary amendments will be entered into Bushehr NPP FSAR Chapter 15 (in the form of notifications).

The information to be entered into Bushehr NPP FSAR Chapter 15 will be approved by the NPP and RP design developers.

The works shall be carried out by JSC ATEX personnel with NRC Kurchatov Institute, JSC OKB Gidropress, JSC Atomenergoporekt personnel involved.

- Requirements to the reporting documentation

Upon completion of the relevant stage of rendering services under this technical assignment,   the Executive shall draw up the performed works Certificate and submit it to the Principal attaching the reporting documents for this stage  :

Stage 1: Manual for writing of emergency response documentation set procedures and instructions as a hard copy in two copies in the Russian language and in two copies in the English language as well as in soft copy (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 2: Time Sheet, Report «Database for performing substantiating calculations of BNPP-1 emergencies» as a hard copy in two copies in the Russian language and in two copies in the English language as well as in soft copy (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 3.1: «Accident elimination instruction (AEI) for all states of the power unit (Rev.0)» in soft copy in the Russian language (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 3.2: «Beyond-design basis accident management guide (BDBAMG) for all states of the power unit (Rev.0)» in soft copy in the Russian language (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 3.3: «Severe accident management guide (SAMG) for all states of the power unit (Rev.0)» in soft copy in the Russian language (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 4.1: AEI feasibility study in soft copy in the Russian language (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 4.2: BDBAMG feasibility study in soft copy in the Russian language (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 4.3: SAMG feasibility study in soft copy in the Russian language (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 5: Time Sheet, Report on verification and validation results with recommendations related to the emergency response documentation set amendment as a hard copy in two copies in the Russian language and in two copies in the English language as well as in soft copy (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 6.1: Accident elimination instruction (AEI) for all states of the power unit agreed upon by NPP and RP design developers in a hard copy in one copy in the Russian language and in one copy in the English language and in the soft copy as well (with signatures of designers in PDF editable MS Word formats) + copies of letters of agreements on CD media.

Stage 6.2: Beyond-design basis accident management guide (BDBAMG) for all states of the power unit agreed upon by NPP and RP design developers in a hard copy in one copy in the Russian language and in one copy in the English language and in the soft copy as well (with signatures of designers in PDF editable MS Word formats) + copies of letters of agreements on CD media.

Stage 6.3: Severe accident management guide (SAMG) for all states of the power unit agreed upon by NPP and RP design developers in a hard copy in one copy in the Russian language and in one copy in the English language and in the soft copy as well (with signatures of designers in PDF editable MS Word formats) + copies of letters of agreements on CD media.

Stage 6.4: Accident elimination instruction (AEI) for all states of the power unit approved by BNPP, NNSD + AEI feasibility study in a hard copy in two copies in the Russian language and in two copies in the English language, as well as in the soft copy (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 6.5: Beyond-design basis accident management guide (BDBAMG) for all states of the power unit  approved by BNPP, NNSD + BDBAMG feasibility study in a hard copy in two copies in the Russian language and in two copies in the English language, as well as in the soft copy (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 6.6: Severe accident management guide (SAMG) for all states of the power unit approved by BNPP, NNSD + SAMG feasibility study in a hard copy in two copies in the Russian language and in two copies in the English language, as well as in the soft copy (with signatures of designers in PDF editable MS Word formats) on CD media.

Stage 7: Time sheet, educational materials in a hard copy in two copies in the Russian language and in two copies in the English language, as well as in the soft copy (with signatures of designers in PDF editable MS Word formats) on CD media D.

Stage 9: The notifications of the amendments having been entered into the FSAR Chapter 15, approved by NPP and RP design developers, two hard copies in Russian and two hard copies in English, as well as in electronic version (signed by developers and designers in PDF format and in editable MS Word) + copies of letters of approval on CD disk.

The electronic copy shall be identical to the hard original copy.

The place of the Executive’s reporting documentation submission to the operating company is BNPP Site.

- Sequence of works consideration and acceptance

The Executive’s work acceptance shall be performed on the basis of the performed works Certificate according to the time program.

The documented results and performed services Certificates shall be handed over to the Principal. The Principal shall accept the scope and quality of the rendered services, sign the documents or (if unsatisfactory result is revealed) send justified refusal to the Executive. The Principal’s refusal to accept the results shall be drawn up in the written form and contain the list of required modifications of scopes of services, as well as the deadlines for their implementation. Modification due to revealed unsatisfactory services rendering under this technical assignment shall be performed at the expense of the Executive.

- Economic potential of work results implementation

Technical and economic effect consists in BNPP-1 safety improvement.

- Special requirements to the work executive

Availability of the license issued by Federal agency on environmental, technological and nuclear surveillance for the right to render services to an operating company related to operational documentation development.

Appendix No.1

to Technical Assignment

TIME PROGRAM

for work performance by topic:

«Elaboration of emergency documentation set for BNPP-1 in the symptom-based emergency operating instructions format (SBEOI)»

| Stage No. | Work description | Completion period |  | List of reporting documentation | Stage cost, EURO |
| --- | --- | --- | --- | --- | --- |
|  |  | start | end |  |  |
| 1 | 2 | 3 | 4 | - 5 | - 6 |
| 1 | Elaboration of Manual for writing of emergency response documentation set procedures and instructions | Т0 | Т0+5 months | - Manual for writing of emergency response documentation set procedures and instructions. Performed works certificate | - 77 908,08 |
| 2 | Database formation for accidents substantiating calculations performance | Т0 | Т0+5 months |  | - 39 070,00 |
|  |  |  |  | - Report «Database for BNPP accidents substantiating calculations performance». - Performed services certificate | - 18 329,00 |
|  |  |  |  | - Time Sheet. Performed services certificate | - 20 741,00 |
| 3 | Elaboration of emergency response documentation set for Bushehr NPP power unit No.1 (Rev.0) |  |  |  | 1 229 117,73 |
| 3.1 | Elaboration of an accident elimination instruction (AEI) for all states of the power unit (Rev.0) | Т2 | Т2+12 months | - AEI for all states of the power unit (Rev.0) Certificate of performed services | 409 705,91 |
| 3.2 | Elaboration of beyond-design basis accident management guide (BDBAMG) for all states of the power unit (Rev.0) | Т2 | Т2+12 months | - BDBAMG for all states of the power unit (Rev.0) Certificate of performed services | 409 705,91 |
| 3.3 | Elaboration of severe accident management guide (SAMG) for all states of the power unit | Т2 | Т2+12 months | - SAMG (Rev.0) for all states of the power unit Certificate of performed services | 409 705,91 |
| 4 | Elaboration of feasibility study |  |  |  | 1 446 933,87 |
| 4.1 | Elaboration of AEI feasibility study | Т2 | Т2+9 months | - AEI feasibility study. Certificate of performed services | 479 052,43 |
| 4.2 | Elaboration of BDBAMG feasibility study | Т2 | Т2+12 months | - BDBAMG feasibility study. Certificate of performed services | 537 711,91 |

| 1 | 2 | 3 | 4 | - 5 | - 6 |
| --- | --- | --- | --- | --- | --- |
| 4.3 | Elaboration of SAMG feasibility study | Т2 | Т2+14 months | - SAMG feasibility study. Certificate of performed services | 430 169,53 |
| 5 | Elaborated documents verification and validation performance | Т3.3 | Т3.3+4 months |  | 276 800,00 |
|  |  |  |  | - Report on verification and validation results with recommendations on emergency response documentation set amendment - Certificate of performed services | 38 312,00 |
|  |  |  |  | - Time Sheet - Certificate of performed services | 238 488,00 |
| 6 | Emergency response documentation agreeing with NPP and RP design developers, BNPP, NNSD |  |  |  | 921 106,69 |
| 6.1 | AEI agreement by NPP&RP design developers. AEI amendment | Т5 | Т5+7 months | - Agreed AEI with copies of letters on the design agreement by NPP&RP developers. Performed works certificate | 308 146,54 |
|  | AEI amendment by results of agreement with NPP&RP design developers |  |  |  | 117 058,83 |
|  | Agreement by NRC Kurchatov Institute |  |  |  | 48 882,90 |
|  | Agreement by OKB "Gidropress" |  |  |  | 95 543,85 |
|  | Agreement by JSC "Atomenergoproject" |  |  |  | - 46 660,95 |
| 6.2 | BDBAMG agreement by NPP&RP design developers. BDBAMG amendment | Т5 | Т5+7 months | - Agreed BDBAMG with copies of letters on the design agreement by NPP&RP developers. Performed works certificate | - 308 146,54 |
|  | BDBAMG amendment by results of agreement with NPP&RP design developers |  |  |  | 117 058,83 |
|  | Agreement by NRC Kurchatov Institute |  |  |  | 48 882,90 |
|  | Agreement by OKB "Gidropress" |  |  |  | 95 543,85 |
|  | Agreement by JSC "Atomenergoproject" |  |  |  | 46 660,95 |

| 1 | 2 | 3 | 4 | - 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| 6.3 | SAMG agreement by NPP&RP design developers. BDBAMG amendment | Т5 | Т5+7 months | - Agreed SAMG. - Performed works certificate | 304 813,61 |
|  | SAMG amendment by results of agreement with NPP&RP design developers |  |  |  | 117 058,83 |
|  | Agreement by NRC Kurchatov Institute |  |  |  | 57 770,70 |
|  | Agreement by OKB "Gidropress" |  |  |  | 81 101,18 |
|  | Agreement by JSC "Atomenergoproject" |  |  |  | 48 882,90 |
| 6.4 | AEI approval by BNPP, NNSD. AEI amendment | Т6.1 | Т6.1+6 months | - Approved AEI. Certificate of performed services | 58 529,42 |
| 6.5 | BDBAMG approval by BNPP, NNSD. BDBAMG amendment | Т6.2 | Т6.2+6 months | - Approved BDBAMG. Certificate of performed services | 58 529,42 |
| 6.6 | SAMG approval by BNPP, NNSD. SAMG amendment | Т6.3 | Т6.3+6 months | - Approved SAMG. Certificate of performed services | 58 529,42 |
| 7 | Training of BNPP personnel | Т6.6 | Т6.6+6 months |  | 485 974,10 |
|  |  |  |  | - Educational materials. Certificate of performed services | 300 504,10 |
|  |  |  |  | - Time Sheet. Certificate of performed services | 185 470,00 |
| 8 | Translation of the elaborated documentation into the English language | Т0 | Т7 |  | 314 501,27 |
|  |  |  | Т0+5 months | - Documentation for stage 1 translated into English. Certificate of performed services | 15 725,06 |
|  |  |  | Т0+5 months | - Documentation for stage 2 translated into English. Certificate of performed services | 15 725,06 |
|  |  |  | Т2+12 months | - Documentation for stage 3.1 translated into English. Certificate of performed services | 41 933,50 |
|  |  |  | Т2+12 months | - Documentation for stage 3.2 translated into English. Certificate of performed services | 41 933,50 |
|  |  |  | Т2+12 months | - Documentation for stage 3.3 translated into English. Certificate of performed services | 41 933,50 |

| 1 | 2 | 3 | 4 | - 5 | - 6 |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Т2+9 months | - Documentation for stage 4.1 translated into English. Certificate of performed services | 41 933,50 |
|  |  |  | Т2+12 months | - Documentation for stage 4.2 translated into English. Certificate of performed services | 41 933,50 |
|  |  |  | Т2+14 months | - Documentation for stage 4.3 translated into English. Certificate of performed services | 41 933,50 |
|  |  |  | Т3.3+4 months | - Documentation for stage 5 translated into English. Certificate of performed services | 15 725,06 |
|  |  |  | Т6.6+6 months | - Documentation for stage 7 translated into English. Certificate of performed services | 15 725,09 |
| 9 | FSAR amendment | Т6.6 | Т6.6+6 мес. | - Amendment notifications have been approved by the NPP and RP design developers. Certificate of performed services | - 33 000,00 |
|  | TOTAL: | Т0 | Т0+40 months |  | 5 000 000,00 |

Т0  - Work-Order receipt date + 3 months for preparation of documents (visas, contractor’s contracts and etc.)