| Vice President of AEOI and NPPD Managing Director | NNSD Managing Director | INRA Director |
| --- | --- | --- |
| _________Mr. M. Ahmadian | _________Mr. Sepanloo | ___________Mr. Rastkhah |

Protocol

on NPPD Preparedness for Obtaining the Bushehr NPP No.1 Operation License

Протокол

о готовности NPPD в получении лицензии на эксплуатацию

для блока №1 АЭС «Бушер»

The Managers of the Project Parties have considered the current status of obtaining the 
License for BNPP-1 operation, application of which NPPD had submitted to NNSD by letter No.LTR-4100-9477203 dd. 24.01.2016. Following the consideration, the Parties have agreed/emphasized the following: / Руководители Сторон Проекта рассмотрели состояние дел на получение лицензии на эксплуатацию блока №1 АЭС «Бушер» запрошенную у NNSD письмом NPPD № LTR-4100-9477203 от 24.01.2016г, по результатам которого было согласовано/подчеркнуто следующее /:

- The Contractor shall render their assistance to the Principal in agreement upon the FSAR,rev.2 (17 chapters) and the Probabilistic Safety Analysis level 1, submitted to the Regulatory Body of Iran (NNSD), by implementing the comments on the documents when issued by NNSD. / Подрядчик окажет содействие Заказчику в согласовании направленных в надзорный орган Ирана (NNSD) FSAR ревизии 2 (17 глав) и вероятностный анализ безопасности 1-го уровня, и устранит замечания к ним в случае их выдачи от NNSD.

- The current status of implementation of items of BNPP-1 Commissioning License Validity Conditions (CLVC) is outlined in Table No.1: / Касательно выполнения пунктов Условия действия лицензии по вводу в эксплуатацию (УДЛ ВЭ) блока №1 АЭС «Бушер» состояние дел показано в Таблице №1:

Table No.1

| CLVC Item | Validity Conditions | Company responsible for implementation of CLVC item | Deadlines |
| --- | --- | --- | --- |
| 4.1 | In accordance with the requirements of Doc. INRA-NS-RE-051-10/01-1 and Doc. INRA-NS-RE-051-10/03-2-Nov.2009, NPPD shall, during BNPP-1 commissioning, obtain NNSD Permits for Stages В, С, as well as Special Permits from NNSD representative office at BNPP-1 site for sub-stages B1, B2, C1, C2, C3, and for the following activities performance: - Trial work; - Operation for training purposes; - repair works with welding of equipment and pipelines registered by NNSD; - re-construction works (modernization) of safety-related systems (components), as well as of equipment and pipelines registered by NNSD; - tests of safety-related systems and equipment, as well as of equipment and pipelines registered by NNSD, not envisaged for in the Process Regulations for BNPP-1 Safe Operation neither in operating instructions for BNPP-1 systems and equipment; - start-up of the Power Unit after its shutdown due to operation failures; start-up of the Power Unit after scheduled preventive repair. | DASE BNPP (submission of HT and external inspection Reports) | March 2016 |
| 4.2 | - Arrangement of changes introduction (correction) into the operational documents as per the established order in accordance with the effective procedure; As of 4th quarter of 2015, 338 in all are subject to correction. 338 operating instructions underwent correction by DATEX; 293 are agreed by BNPP (NPPD), 76 of them are agreed by NNSD. - The Preliminary Report on the results of activities at the previous stage (Substage) shall be presented to NNSD within 1 month from the date of the stage completion. The Final Report shall be presented within 3 months after completion of the respective stage" Report on C-3 Stage, rev.1 corrected as per the comments of NNSD / VO “Safety” will be submitted to the Principal after the Overhaul, the Unit attainment of 100% power and HPH-K tests which are to be carried out in 2016. | JSC ASE DATEX |  |
| 8.18 | Installation, pre-commissioning and commissioning of radwaste treatment and storage systems in ZC building shall be completed by the at Stage C. | JSC ASE | December 2016 |
| 8.19 | Communication facilities shall be installed and adjusted as per the design scope up to the end of Substage B1. - Certificates Н-1, Н-2 of МZ communication system are not signed. |  |  |
| 8.20 | "Pre-commissioning activities on transportation system of spent fuel assemblies using set TUK-13/1V shall be performed within a time period between RP cool-down and reactor depressurization during the first reload of reactor. All transport and process operations related to TUK-13/1 V transportation, its installation to the container cell, depressurization, sealing, transportation to the decontamination cell and outside the containment boundaries shall not be performed above the reactor and spent fuel pool. Pre-commissioning activities and tests of the system of spent nuclear fuel storage shall be performed only using dummy fuel assemblies. | JSC ASE BNPP | PCA and test of the transportation system of spent fuel assemblies using the container TK-13/1V shall be performed by 20.03.2019. |
| 8.28 | The problem of corrosion-active agents content monitoring (chlorides, sulfites, sulfur dioxide) in rooms with APCS equipment shall be solved before Stage C. | BNPP | Refer to item 2 of Table 2 |

- The Principal and the Contractor have reviewed twenty-two NNSD comments on BNPP-1 Project. The results of review of twenty-two NNSD comments are given in the following table № 2 / Заказчик и Подрядчик рассмотрели переданные от NNSD 22 замечания по проекту блока №1 АЭС «Бушер». Результаты рассмотрения 22 замечаний NNSD представлены в прилагаемой Таблице №2:

Таблица №2

| No. | Comment | Status | Corrective measures / Supporting documents | Organization responsible for comment removal | Comment-removal deadline |
| --- | --- | --- | --- | --- | --- |
| 1 | Water ingress in the cable channels (elevations at minus level). | Done. | All the cable ducts ZW01,02,03,04,08÷14,20,21,22,23,25,29,37,40,41,46,47,48,49,51,52,54,55,69 (29 ducts) are handed over to the Principal with signing of the respective H-8 Certificates. The information on completion of activities of signing of H-8 certificates of all the cable ducts (with the list of ducts, nos.of certificates and date of signing attached) were submitted to NNSD/VO “Safety” BNPP Site Representative through the Principal by letter No.007/20-04/02-8043 dd. 24.08.2014. NNSD letter dd. 02.09. 2014 № 88/93-06-461 was sent to BNPP. | BNPP |  |
| 2 | Presence of corrosive agents in APCS equipment premises (exceeding of the norms established by the manufacturers). Exceeding of the underestimated norms agreed upon with the manufacturers | Done. | 1. All the Manufacturing Plants of BNPP APCS equipment, that is FSUE VNIIA, FSUE NPP VNIIEM, FSUE FNTSh NIIIS, JSC SNIIP Systematom, FSUE PSZ, JSC KB Promengineering and JSC NPP AS, have agreed upon the changes in the permissible concentrations of corrosive agents of the equipment supplied to the Site, with the values of corrosive agents concentration being 2,0x10-3 mg/mЗ for chlorides, 3,0x10-3 mg/mЗ for sulfates. All the enumerated Plants, the Manufacturers of APCS equipment, have submitted the respective Notifications (forms) on changes in manufacturing documentation 2. JSC AEP introduced the necessary changes into the design and final revision of FSAR. | BNPP |  |
| 3 | Agreement in the prescribed order and submission to NNSD of the Guidelines on beyond-design basis accidents management | Done. |  |  |  |
| 4 | Overloading of cable routes | Done. | Technical Decision No. 65.BU.1.00.EM.RT.BAS0746 On laying of cable products in BNPP-1 buildings and structures is signed. |  |  |
| 5 | JBB automatic powder fire fighting systems. | Done. | H-10 Protocols of all the controllers and H-1 and H-2 Certificates of JBB systems are signed. AFPS system has been in operation since 2013. | BNPP |  |
| 6 | JBB automatic gas fire fighting systems. |  |  |  |  |
| 7 | Non-fulfillment of tests of emergency high-pressure injection (boric acid solution delivery) ТН15-45. (Safety system, class 23L, group B). | Done. | Technical Decision No. 65.BU.1 ZA.YD.ABC.RT.ATE1116 on cancellation of tests of TH15(25,35,45) subsystem according to Program on determination of efficiency and fast-response of emergency boron injection systems 53.BU.10.00.PN.PM.ATE031 is signed. |  |  |
| 8 | Readiness of radioactive wastes treatment and storage systems (TT and TQ). | Under removal. | TT, TQ & TR systems were commissioned and they are in operation. This issue was included into the list of disputable issues of H-3 certificates. A compromise decision was taken: the Contractor to supply 14 coaxial valves and the Principal to mount it. | JSC ASE / BNPP | Valve supply deadline is December 2016. Not determined. |
| 9 | Removal of the beam in the PRZ thrust ring support because of elevated temperature of concrete vault is performed without Technical Decision (changes in the design). | TD under consideration (at agreement stage). | The Contractor will remove the NNSD comments and submit the Technical Decision for the Principal’s agreement. | JSC ASE | March 2016 |
| 10 | Frequency of control and WC in ECCS HA-2 fail to meet the requirements of OKB Gidropress and FSAR | Done. | OKB GP has officially modified the document “Reactor Plant V-446. Norms of primary circuit water chemistry” 446 ДЗ. This document determines the water chemistry norms separately for ECCS HA 1 and 2, the frequency of tests for controlling the quality indices of boric acid solution in ECCS HA 2 has been changed. The copy of modified document Reactor Plant V-446. Norms of primary circuit water chemistry” 446 ДЗ was submitted to NNSD/VO “Safety” BNPP Site Representative through the Principal by letter No.007/20-03/02-10510 dd. 11.09.2013. The necessary changes were applied in i.1.10.12 of Appendix F of TSSO 51.BU.1 0.00.AB.WI.ATEX.001 AEP has introduced the required changes into Table 9.3.2.1.5.1-1, FSAR 49.BU.1 0.0.OO. RSAR.RDR001. | BNPP |  |
| 11 | Periodic spontaneous transfer of turbine control unit (TCU) from automatic mode to manual mode accompanied by load swigs on generator up to 150 MW. | Done. | The comments on TCU performance were implemented. The Certificate of technical acceptance after integrated tests of Turbine control system SJ and the system of automatic control protection and steam distribution SA1 per H-3 form No.60.BU.1 ZF.SJ.PN.AZT.ASE3219 dated of 09.09.2013 was signed. | BNPP |  |
| 12 | Registration of equipment and pipelines. | Under removal. | As of 02.02.2016: - to be registered by NNSD - 1024 passports - not registered – 26 passports. | JSC ASE | March 2016 |
| 13 | Unsatisfactory performance and condition of valves (jamming, scratching, bending of stems, etc.). | Done. | The comment is withdrawn by NNSD letter No. 88/92-06-694 dd. 28.09.13. |  |  |
| 14 | Failure of HPH (one out of two). | Done. | HPH-K (RF41B001) is repaired and installed at standard place. |  |  |
| 15 | Presence of a metal foreign object (fastening bolt of cowling with mass 1.9 kt) in the primary circuit (break of RCPS-1 impeller cowling on 25.05.12). | Done. | NNSD Representative Office at BNPP-1 via letter No. 88/94-10-947 dd. 09.01.16 agreed the final report on taken measures for final search for fragments of fastening elements of RCPS-1 impeller cowling during BNPP-1 overhaul in 2015. JSC OKB Gidropress letter No. 044/10-92/19766 dd. 24.12.2015 is received, which confirms further safe operation of BNPP-1 based on the results of review of the final report on taken measures for final search for fragments of fastening elements of RCPS-1 impeller cowling during BNPP-1 overhaul in 2015. NNSD letter No.88/94-10-947 of 09.01.2016 was sent to BNPP. |  |  |
| 16 | Problem with fastening LPC blades | Done. | The comment is withdrawn by NNSD letter No. 88/92-06-697 dd. 28.09.13. |  |  |
| 17 | Foreign object on FA is revealed upon RP loading. | Done. | The comment is withdrawn by NNSD letter No. 88/92-07-781 dd. 19.10.13. |  |  |
| I8 | Repair activities with welding on pipelines registered with NNSD. | Under removal. | At the stage of comment removal. The necessary reporting documents were signed for all the repair activities with welding, performed within the PPM-1 and Overhaul-2015. The remaining 16 sets of justifying documents are being compiled to be submitted to NNSD for approval. | DASE | March 2016 |
| 19 | Application of C group pipeline elements on B group pipeline (RA system). | Done. | Technical Decision No. 7717-03-08-175 On application of C group parts on B group pipelines of RA system (main pipelines) in ZB9 building of BNPP-1 is agreed. |  |  |
| 20 | Application of pumps with cast-iron bodies in the main condensate system (RM). | Under removal. | Done. The test with measuring the metal thickness at the points exposed to wear and tear is not stipulated in compensatory measures of Technical Decision No.СS.TAG.CRISM.1.00.572 on the use of cast iron in RM pumps. Notification No.BUSH 22-2013 dd. 29.05.13 on measuring the walls thickness in 5 points of RM11,12,13D001 pumps cases were submitted to DATEX by letter No.27/08-88 dd. 30.05.2013 OKBM. DATEX ML performed the measurements of metal thickness by ultrasonic method. Conclusion No.55-28-03/20/132-279-ТО-Т of 18.06.2013. The results were satisfactory. The next measurement of metal thickness of pumps cases walls metal by ultrasonic method was performed by BNPP ML on February 23,2014. The results were found satisfactory (S-satisf.). Conclusion No.14-1155/1278-УТ dd. 23.02.14 The copy of Conclusion No.14-1155/1278-УТ dd. 23.02.14 was sent to VO Safety in Moscow by letter 007/20-04/03-1742 dd. 02.03.14. BNPP shall provide the BNPP ML conclusions on TM pumps walls thickness tests for 2015. | BNPP | February 05 2016 |
| 21 | Failure of stator cooling system. | Done. | The comment is withdrawn by NNSD letter No. 88/93-01-56 dd. 15.04.14. |  |  |
| 22 | Failure of foundation support of exciter. | Done. | The comment is withdrawn by NNSD letter No. 88/92-09-940 dd. 27.11.13. |  |  |

- The Parties have agreed the status of CLVC and the twenty-two NNSD comments regarding to BNPP-1 Project and signed the present Protocol. / Стороны пришли к соглашению по состоянию дел указанных в УДЛ ВЭ и по 22 замечаниям от NNSD по проекту блока №1 АЭС «Бушер» и подписали настоящий протокол.

The Principal 			The Contractor 						NNSD

NPPD	BNPP