*Andrey Latchkov*

*MA-02-LA*

# 5 LOW PRESSURE FEED HEATER – 3,4 MAINTENANCE

## SCOPE OF OBSERVATION

Observation over maintenance has been performed in turbine hall of Unit 3 in course of 30 minutes. A workers group of contractor organization performed maintenance under the supervision of senior foreman.

## OBSERVATIONS

1. Maintenance documentation was missing at the work place of 5 LPFH-3,4 (turbine hall, level 0,0) maintenance. Failure to use the maintenance documentation at work place can cause human errors and low-quality maintenance. (*MA-02-LA-01-pr*)
2. Temporary scaffolding was installed to perform 5 LPFH-3,4 maintenance. The scaffolding missed marking table containing inventory number, date of installation and inspection, organization performed the installation of scaffolding, responsible persons etc. Missing needed information posted on the applied scaffolding can cause loss of control over arrangement of scaffolding installation/dismantling and it’s condition control and cause personnel injury. (*MA-02-LA-02-pr*)