FOLLOW-UP PEER REVIEW FINAL REPORT

WANO FOLLOW-UP PEER REVIEW

BUSHEHR

NUCLEAR POWER PLANT

NUCLEAR POWER AND DEVELOPMENT

COMPANY OF IRAN

EXECUTIVE SUMMARY OF THE FINAL REPORT

"CONFIDENTIALITY NOTICE: Copyright – 2013 World Association of Nuclear Operators (WANO). All rights reserved. Not for sale. This document is protected as an unpublished work under the copyright laws of all countries which are signatories to the Berne Convention and the Universal Copyright Convention. Unauthorised reproduction is a violation of applicable law. Translations are permitted. All copies of the report remain the exclusive property of WANO. This document and its contents are confidential and shall be treated in strictest confidence. In particular, without the permission of both the member and the applicable WANO Regional Governing Board, this document shall not be transferred or delivered to any third party and its contents shall not be disclosed to any third party or made public, unless such information comes into the public domain otherwise than in consequence of a breach of these obligations. Furthermore, the circulation of this document must be restricted to those personnel within the WANO member organisations who have a need to be informed of the contents of the document."

November 2013

CONTENTS

PURPOSE AND SCOPE	3

EXECUTIVE SUMMARY	4

# PURPOSE AND SCOPE

In the period of November 2 – 6, 2014, the Moscow Centre of WANO conducted a follow-up peer review of the Bushehr nuclear power plant (BNPP), Iran.

The purpose of the follow-up peer review was to assess the progress the station has made in fixing the areas for improvement (AFI) identified during the pre-startup peer review in November 2011.

The peer review included the following 9 review areas:

- Organizational effectiveness

- Operations

- Maintenance

- Operating experience + SOER recommendations

- Radiological protection

- Chemistry

- Training and qualification

- Fire protection

- Emergency preparedness.

The peer review experts were to assess the status of the areas for improvement at the plant. Information was assembled from observations of plant activities, review of documentation, discussions and interviews with the station personnel.

As a basis for the review, the team used the WANO Performance Objectives and Criteria (Revision 3, January 2005).

_______________________

EXECUTIVE SUMMARY

In November 2013 the Moscow Centre of the World Association of Nuclear Operators (WANO-MC) conducted a follow-up peer review of the Bushehr nuclear power plant (BNPP) in Iran. The peer review team was comprised of 8 experienced nuclear professionals from 6 countries (China, France, Hungary, Russia, Slovakia and Ukraine) representing WANO Moscow Centre, WANO Hong Kong Office and WANO London Office.

The Bushehr nuclear power plant is located on the shore of the Persian Gulf near the town of Bushehr in the south-west of Iran. Construction of the Bushehr NPP was started in 1975 by a German vendor. In 1980, construction of the plant was terminated.

In 1992 the governments of Russia and Iran signed an agreement to continue construction of the nuclear power plant in Bushehr. Actual construction activities were resumed in 1998 by the Russian AtomStroyExport company which was contracted as the General Contractor (Vendor) to complete construction, on the turnkey basis, of BNPP Unit 1 with a 1000 MWe VVER B-446 reactor. AtomStroyExport subcontracted commissioning and initial operation of BNPP Unit 1 to the Russian AtomTechExport Company (Contractor) which established its onsite administrative office (DATEX). An operating organization was established in Iran (Nuclear Power Production and Development Company, NPPD) which is the Principal in the contract with an onsite administrative office (BNPP).

The first core loading started in August 2010. In May 2011 the reactor achieved its first criticality. In September 2011 the Bushehr nuclear power plant was connected to the national power grid.

In November 2011, WANO conducted a pre-startup peer review of the Bushehr NPP. Due to certain organizational difficulties, the peer review was conducted at a time when the plant had already been operating at power for almost two months. The review was nevertheless considered as a pre-startup peer review. This was partly justified because the pre-startup context was still present in that the plant had not yet been handed over to the Principal and the Principal’s staff were acquiring knowledge and experience needed for independent operation of the plant

On August 30, 2012, the plant reached full power for the first time.

In September 2013, the NPPD and the AtomTechExport Company signed a Provisional Acceptance Agreement initiating a two-year handover process. The DATEX administrative office was closed down and its remaining staff of about 275 employees joined the BNPP staff on a temporary basis. By signing the Provisional Acceptance Agreement, the Iranian Principal formally took over management and operation of the Bushehr NPP, with the Contractor staff staying onsite to perform advisory functions and helping resolve the remaining issues as stipulated in the Provisional Acceptance Agreement.

The purpose of the follow-up peer review was to assess the current status of the 20 areas for improvement identified during the pre-startup peer review in November 2011.

In order to review the progress the station had made to fix the AFIs, the WANO team observed activities at Unit 1, conducted interviews with the station personnel and reviewed plant documentation.

In assessing the current status of the AFIs, the team used the following assessment scale:

Level D: Little or no change in the status of the AFI.

No improvement in the AFI status is observed. The level of performance has not changed since the previous peer review.

Level C: Enhanced management attention is required.

Enhanced management attention is required and efforts to improve performance in this AFI should continue. Though the corrective actions have brought some positive progress in this area, it is obvious that their effectiveness is insufficient or their scope does not resolve all the existing performance shortfalls.

Level B: Progress is being made and should continue.

Substantial efforts have been made and significant progress has been achieved to improve performance in this AFI; however, the plant management should maintain coordination and control of the efforts aimed at improvements in this area.

Level A: Satisfactory progress has been made.

Substantial progress has been achieved in this area for improvement and the peer review team considers the problem has been completely fixed.

The results of the assessments are presented in the following table and diagram:

| No. | Area for Improvement | Level |
| --- | --- | --- |
|  | Organizational Effectiveness (OR.2-1) | B |
|  | Conduct of Operations (OP.2-1) | B |
|  | Operations Procedures and Documentation (OP. 4-1) | C |
|  | Plant Status and Configuration Control (PS.1-1) | B |
|  | Conduct of Maintenance (МА.2-1) | C |
|  | Maintenance Procedures and Documentation (МА.4-1) | C |
|  | Work Management (WM.1-1) | C |
|  | Work Management (WM.1-2) | B |
|  | Radiological Protection Management and Leadership (RP.1-1) | B |
|  | Rad. Protection Personnel Knowledge and Skills (RP.2-1) | B |
|  | Operating Experience Management (OE.1-1) | B |
|  | Reporting (OE.2-1) | C |
|  | Screening (OE. 3-1) | B |
|  | Chemistry Measurement and Analysis (CY.4-1) | B |
|  | Chemical and Laboratory Safety (CY.5-1) | B |
|  | Training and Qualification Management and Leadership (TQ.1-1) | B |
|  | General Employee Knowledge in Fire Protection (FP.3-1) | A |
|  | Fire Protection Facilities and Equipment (FP.6-1) | B |
|  | Emergency Plan (EP.2-1) | C |
|  | Emergency Facilities, Equipment and Resources (EP.3-1) | B |

In other words, the follow-up peer review revealed the following:

One area for improvement is resolved; satisfactory progress has been made (Level A):

- Personnel’s knowledge of respiratory protection equipment and fire-fighting equipment is not sufficient. This can result in personnel’s incapability to use fire-fighting equipment and respiratory protection for fire fighting. (FP.3-1)

In thirteen areas for improvement progress is being made and should continue (Level B):

- There are areas where the levels of performance are not high enough. This is the case in procedure quality, procedure use and adherence, radiological protection, fire protection, emergency preparedness, operating experience, housekeeping, industrial safety, use of numerical indicators. (OR.2-1)

- Plant operations and tests are not always conducted in accordance with the approved procedures. This can result in operators making errors or actions being delayed or omitted. (OP.2-1)

- Implementation of plant and system status control is not always up to the best industry practices. There is no comprehensive process to ensure that all components are actually in the required position for each reactor mode. In some cases the operations personnel are not fully aware of the actual status of the systems and equipment. This can result in undetected safety system unavailability and violations of the Technical Specifications. (PS.1-1)

- Some necessary equipment and spare parts have not been provided. Deficiencies in supply and non-availability of a required stock of spare parts and equipment may reduce equipment availability and reliability. They can result in longer or forced outages. (WM.1-2)

- Personnel behaviours and condition of the Radiation Controlled Area (RCA) do not always comply with the established radiological protection standards. This can result in unplanned personnel exposure and/or spread of radioactivity beyond the established boundaries. (RP.1-1)

- Shift personnel of the Radiological Protection Department do not always possess sufficient knowledge and skills needed for high-quality conduct of RP-related activities. This can lead to RP personnel’s errors and unjustified exposure of personnel working in the RCA. (RP.2-1)

- Not all requirements for the use of operating experience are established and accurately communicated to the station’s technical departments. Not having an effective system and organizational documentation for the use of operating experience can result in repeat events. (OE.1-1)

- Apart from recommendations of the WANO SOER 2011-2 on the Fukushima accident that are in progress, the station has not yet conducted a review of SOER recommendations for identification of possible corrective or specific actions. So far, no self-assessment of the SOER recommendation implementation status has been carried out. (OE.3-1)

- Methods of internal laboratory control used at the station combined with a non-existent quality assurance program do not always ensure valid results of laboratory measurements, graphic parameter trending, analysis of deviations and corrective actions. Not having a correct quality assurance program, one cannot ensure accuracy of laboratory measurements to support safe operation of the plant. (CY.4-1)

- Chemical and laboratory safety is not always ensured. Not having correct labelling of chemicals and safety signs, not ensuring control of laboratory equipment, utensils and protective equipment can result in personal injury. (CY.5-1)

- Planning of the training process is not always optimal, and the contents of the training materials in some cases do not meet the up-to-date requirements. Deficiencies in planning and deficiencies in documentation used for training reduce the efficiency of training. (TQ.1-1)

- Deficiencies exist at the station in the upkeep of some fire suppression and fire detection equipment which can result in its reduced efficiency when used for fire extinguishing. (FP.6-1)

- The necessary amount of emergency facilities, equipment and resources for accident mitigation activities is not always ensured. Insufficient amount of emergency equipment can result in inefficient actions, delayed or omitted actions by the accident mitigation personnel. (EP.3-1)

In six areas for improvement Enhanced management attention is required (Level C):

- Procedures, drawings and alarm response cards used by the operations personnel are not always readily available, accessible or properly controlled. This may result in inappropriate actions being carried out or actions being improvised in infrequent evolutions. It also contributes to operators not using or not adhering to procedures and a tolerance for discrepancies in procedures. (OP.4-1)

- Conduct of maintenance is not always up to the established standards. This can lead to personnel errors while using maintenance documentation and preparing the workplace/tagouts, allow foreign material to enter open equipment and result in low quality of maintenance. (МА.2-1)

- Sets of maintenance documentation for some mechanical equipment do not contain all the necessary special-purpose work control documents. (МА.4-1)

- The current practice of manually updating the computerized equipment deficiency database and departmental equipment deficiency logbooks is not efficient enough. This can result in lost control of plant equipment condition and further degradation of equipment. (WM.1-1)

- The station has not completely established a system for reporting minor events and routine operational problems with trending and appropriate corrective actions. (OE.2-1)

- The existing Emergency Plan and its supporting documents do not provide clear and consistent requirements to effectively plan for emergency situations. (EP.2-1)

No areas for improvement were rated as Level D (Little or no change in the status of the AFI).

Appendix A shows the status of implementing SOER recommendations as assessed by the WANO team during the follow-up peer review.

The results of the follow-up peer review were presented to the BNPP and NPPD management, WANO-MC Director, WANO-MC Governing Board Chairman and WANO Chairman during the final briefing at Bushehr NPP on 6 November 2013.

This Final Report was handed over to the BNPP and NPPD management. Besides, one copy of the Final Report is kept at WANO-MC and one copy was sent to the WANO London Office.

___________________________