Protocol No. 11

Instructions under item 2 of PMM held on 28-29.09.2015

Date: 08.12.2015

Participants:

V.N. Pavlov, S.A. Ambartsumyan, V.I. Trachuk, V.V. Kuleshov, V.K. Druzhinin, A.Yu. Dubov, S.V. Gorokhov, V.V. Didenko,Mr. Vahdanifahr, Mr. Keshtkar, Mr. Safavi.

Current Status of Documentation Required for Obtaining the Operation License for BNPP-1 (as of 20.11.2015)

| Row | Required Documents | No. of letter |  | Implemented measures | Status of activity | Responsible body |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Outgoing | Inc |  |  |  |
| 1 | Report on Fulfillment of the Validity Conditions of BNPP-1 Commissioning № NNSD-BNPP-2CML |  |  | The report is submitted by V.K. Druzhinin on quarterly basis. The report for the period of October-November 2015 was submitted on 01.12.2015 dd. 007/20-04/02-6852. | completed | TheContractor LicensingDept. |
| 2 | BNPP-1 Safety Analysis Report (final version) corrected with account of the results of the first criticality (Stage B), power start up and ascension (Stage C) and a period of BNPP-1 warranty operation prior to submitting the Application for Operation License. | 4300-925623 05.03.2014 |  | Request for submission of new revisions of all the chapters of FSAR. All 17 FSAR chapters have been finalized with the Principal and submitted to NNSD. 14 of 17 FSAR Chapters were finalized by M.o.M. dd. 01.12.2015 in Tehran. | completed | Project Manager / ОСЕ The Contractor |
|  |  | 4300-946620 29,11,2015 |  |  |  |  |
|  |  | 4300-53690 03.12.2014 |  |  |  |  |
|  |  | 8000-195048 12.11.2008 |  |  |  |  |
|  |  | 8000-1887328 18.03.2014 |  |  |  |  |
| 3 | Final Environmental Report | 4300-946639 06.12.2015 |  | Final Environmental Report is submitted to the Nuclear Safety Department.It’s submitted to NNSD | completed | BNPP ETS |
| 4 | The followingdocuments corrected on the result of the first criticality, power startup and trial operation |  |  |  |  |  |
| 4-а | BNPP-1 Safety Analysis Report (final version) | 4300-925623 05.03.2014 |  | All 17 FSAR chapters have been finalized with the Principal and submitted to NNSD. 14 of 17 FSAR Chapters were finalized by M.o.M. dd. 01.12.2015 in Tehran.DocumentNo.1 | completed | BNPP The Contractor |
| 4-b | BNPP-1 Probabilistic Safety Analysis Level 1 – corrected according to trail operation results | 4300-946625 01.12.2015 |  | The final version of the PSA level 1was finalized by M.o.M. dd. 21-25.11.2015 in Tehran.Document No.2 | completed | Project Manager / ОСЕ The Contractor |
| 4-c | Technical Specification (of Safe Operation) 51.BU.1 0.00.AB.WI.ATEX.001 | 4300-925627 08.03.2014 |  | TheTSSO,rev. 2was finalizedbyBNPPand submitted to NNSD on 01.12.2015LTR-1050-129517.Document No.3 | completed | BNPP TheContractor |
| 4-d | List of Nuclear Hazardous Works 51.BU.1 0.00.AB.WI.ATEX.030 | 4300-925627 08.03.2014 |  | This document is approved byBNPPandNNSD. The new revision of Document52.BU.1 0.00.AB.WI.ATEX.030 is put into production. Validityperiod – by 01.09.2016. It was handed over and agreed upon by the Principal. Send to NNSD Document No.4 | completed | BNPP The Contractor |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-e | Reactor Plant Passport | 4300-925627 08.03.2014 |  | Atthe Contractor’sunder removalof comment given by Nuclear safety Department. Report by system TH15-45 send to NNSD #4300-946626 31.11.15 The BFR (Brittle fracture resistance) was submitted (on 20.10.2015). The Principal shall introduce some data into the passport. By 15.12.2015 Document No.5 |  | BNPP The Contractor |
| 4-f | Emergency operation Instruction for accident elimination on the BNPP-1 Reactor Plant51.BU.1 0.00.AB.WI.ATEX.003 | 4300-925627 08.03.2014 |  | This document was developed and approved by the Contractor.ThecorrectedInstruction on accidents eliminationat the Reactor Plant (ИЛАРУ), rev.2, was finalized by BNPPand submitted to NNSD on 01.12.2015 LTR-1050-129517. Document No.6 | completed | BNPP The Contractor |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-g | Test schedule for reactor installation systems important to safety 51.BU.1 0.00.AB.WI.ATEX.010 | 4300-925627 08.03.2014 |  | Rev.3 ofDocument 52.BU.1 0.00.AB.WI.ATEX.010 is put into production.It washanded over and agreed upon by the Principal. Document No.7 | completed | BNPP TheContractor |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-h | Regulations of the RP equipment maintenance and repair51.BU.1 0.00.AB.WI.ATEX.014 | 4300-925627 08.03.2014 |  | The corrected M&R regulation was finalized by BNPPand submitted to NNSD on 01.12.2015. Document No.8 | completed | BNPP The Contractor |
| 4-i | Radiation safety regulations51.BU.1 0.00.AB.WI.ATEX.016 | 4300-925627 08.03.2014 |  | Rev.2 of Document 52.BU.1 0.00.AB.WI.ATEX.016 has been put into production since 21.07.2014. It was handed over and agreed upon by the Principal. Document No.9 | completed | BNPP TheContractor |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-j | Manual for beyond-design-basis accidents control 51.BU.1 0.00.AB.WI.ATEX.008 | 4300-925627 08.03.2014 |  | ThecorrectedBDBA control Manual (РУЗА)was finalized byBNPP and submitted to NNSD by 01.12.2015LTR-1050-129517. Document No.10 | completed | ProjectManagerBNPP TheContractor |
| 4-k | Plan of measures for personnel protection in case of accident at the BNPP51.BU.1 0.00.AB.WI.ATEX.015 | 4300-925627 08.03.2014 |  | The document isfinalizedwith the Principal andNNSD.Document No.11 | completed | BNPP The Contractor |
| 4-l | Operation instruction.Fresh nuclear fuel transportation and storage system 16.BU.1 ZA.PL.AB.WI.ATEX.001 | 4300-925627 08.03.2014 |  | The document is agreed upon by the Principal and NNSD.Document No.12 | completed | BNPP The Contractor |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-m | Operation Instruction. Spent nuclear fuel handling system16.BU.1 ZA.PT.AB.WI.ATEX.001 | 4300-925627 08.03.2014 |  | The document is agreed upon by the Principal and NNSD.Document No.13 | completed | BNPP TheContractor |
| 4-n | Instruction for accounting and control during collection, processing, storage and transportation of radwaste51.BU.1 0.00.AB.WI.ATEX.023 | 4300-925627 08.03.2014 |  | Revision 2 of the document is approved byBNPPandNNSD.Handed over and agreed upon by the Principal and NNSD,Document No.14 | completed | BNPP TheContractor |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-o | Off-Site Emergency Plan | 4300-925625 08.03.2014 |  | ThedocumentsarefinalizedandapprovedbytheOperatingcompanyandtheProvince administration. However BNPP has stated that a series of changes must be introduced in the document. In progress. The Principal has submitted it to NNSD. | completed | BNPP ETS NNSD |
| 4-p | Duly formalizedvalid list of procedures and programmes of training and emergency drills to master action under accident conditions | 4300-925624 05.03.2014 |  | InstructionINS-1240-11 is prepared and approved. The Principal has submitted it toNNSD | completed | BNPP |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-q | Reference Report on assurance of physical protection of the Facility | 4300-925624 05.03.2014 |  | ItwasdevelopedbytheSafeguardandSecurityManagement. The Principal has submitted it to NNSD | completed | ProjectManagerBNPP |
| 4-r | Standard and workingprogrammes and schedules of control of base metal, welds of items and systems important to safety | 4300-925624 05.03.2014 |  | ThetableoftheconcernedprogrammesandschedulesispreparedintheformofWorkingProgramme 69.BU.10.0.ABT.PM.BNPP1278. The Programme is approved and put into production. Handed over and agreed upon by the Principal and NNSD.Document No.15 | completed | BNPP |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 4-s | Reference Report on BNPP-1 personnel, i.5.3 НП-00—97, ОПБ-88/97 | 4300-925624 05.03.2014 |  | All the stages of training and obtaining permissions for independent work according to documentОПБ 88/89, and individual programmes of professional training are in implementation process. The Report is being developed.The Principal has submitted it toNNSD. | The report is to be prepared by BNPP Training Dept. | BNPP Training Dept. |
|  |  | 4300-946452 07,11,2015 |  |  |  |  |
| 4-t | Reference Report on Annual refueling, outages, modernization and preventive maintenance | 4300-925624 05.03.2014 |  | 1. The list of corrections and modernizations of BNPP equipment and systems covering 230 positions in the form of one document has been prepared and is now at the stage of priority distribution of execution deadlines. 2. Schedule of preventive repairs and maintenance of equipment is under continuous, annual development and implementation. 3. The schedule of NPP outages once every four years for refueling is under development. The Principal has submitted it to NNSD. It shall be updated by 13.12.2015. | The Report is to be provided by the NPP | BNPP |
|  |  | 4300-946375 14,09,2015 |  |  |  |  |
| 5 | Duly formalized “List of Operational Documents to be submitted to the Principal within the Contract framework. BNPP-1” 38.BU.1 0.00.AB.WE.ATEX.001 | 4300-925624 05.03.2014 |  | Total quantity of operational documentation: 338. Quantity of additional documentation: 69. Quantity of final instructions (revision 2): 207. Quantity of documents without revision: 131. The Reference is in BNPP being updated as of actual date. It shall be updated by 13.12.2015. | completed | BNPP ETS |
| 6 | Duly formalized title pages of every document having 2B.4 code as per document 38.BU.1 0.00.AB.WE.ATEX.001 | 4300-925624 05.03.2014 |  | Outof 95 operational documents with 2B.4 status, 93 documents were approved byNNSD. 43 – revision 2. Titlesheetsof operational documents (43 docs wtih rev.2) are presented in the electronic form. The Reference is in BNPP being updated as of actual date. It shall be updated by 13.12.2015. | completed | BNPP |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 7 | Duly formalized valid Quality Assurance Programmefor Operation BNPP-1 QAP (O) | 4300-925624 05.03.2014 |  | Edition 2008 of Quality Assurance Programme for Operation in English is approved. The Russian version is in work. It is in BNPP, under rework. It shall be submitted by 13.12.2015. | completed | BNPP |
| 8 | Reference Report on preparedness and equipping of the on-site crisis centers with necessary equipment, instruments and communication means, wherefrom emergency plans are managed in case of an accident | 4300-925624 05.03.2014 1000-129624 01.12.15 |  | There are two telephone lines and one fax line in the main local crisis center in ZX building. Reserve crisis control center in ZV1. Installation of system of video conference with the LCC in NPPD. Video surveillance system. The Principal has submitted it to NNSD. | BNPP shall prepare and submit of all report completed | BNPP |
| 9 | Provision on organization of the system of accounting and control of nuclear materials | 4300-925624 05.03.2014 |  | The system of accounting and control of nuclear materials at the BNPP provides for organization within the established time limits of the necessary measures for determination of nuclear materials amount in the context of maintaining a balance. The measures for implementation of the system of accounting and control of nuclear materials: assignment of persons responsible for implementation of the system, including the manager of fuel handling and nuclear safety department, fuel control group manager, specialist for accounting and control over nuclear materials chosen based on the results of knowledge testing and preparedness for independent work. Determination of the structure of keeping the materials balance (MBA) and key measurement points (KMP) at the BNPP on the basis of the Instructions of accounting and control of nuclear materials. Accounting of nuclear materials and the development and formalization of the reports on the accounting to meet the requirements of the mentioned instructions, as well as the instructions on inventory-taking of physical availability of nuclear materials at the BNPP-1 is in implementation process. The Principal has sent it toNNSD. | The two mentioned instructions are developed (completed) | BNPP |
|  |  | 4300-946244 14.04.2015 |  |  |  |  |
| 10 | Report onforeign object |  |  | The Report has been produced and sent to GP for agreement via letter No.007/09-10/02-01/93 dd. 10.12.2015 and to BNPP on 09.12.2015. |  | BNPP The Contractor |

Deputy Head of Department for Construction of NPP in IRI									S.А. Ambartsumyan