Meeting Minutes of ‘IGALL Workshop on Ageing Management Establishment and Implementation’

08-10 May 2017, Tehran, Iran

Participants:

| No | Name | Position | E-mail |
| --- | --- | --- | --- |
| INRA |  |  |  |
| 1 | Ali Takht Ardeshir | Senior expert of inspection group | aardeshir@aeoi.org.ir |
| 2 | Abbas Sedghkerdar | Head of Inspection Group | asedghkerdar@aeoi.org.ir |
| Bushehr NPP |  |  |  |
| 3 | Ebrahim Deylami | Technical Department Director | deylami@nppd.co.ir |
| 4 | Hamid Ahmadi | Head of reliability and AM group | pambnpp@nppd.co.ir |
| TAVANA |  |  |  |
| 5 | Mr. Ghods | Director General | ghods@nppd.co.ir |
| 6 | Mr. Talebi | AMP manager | tavanaeng@nppd.co.ir |
| IAEA external experts |  |  |  |
| 7 | Peter Babics | HAEA , Hungary | Babics@haea.gov.hu |
| 8 | Jan Wandrol | UJV Rez , the Czech Republic | jan.wandrol@ujv.cz |
| 9 | Philippe D'Haeyer | Tihange NPP, Belgium | philippe.dhaeyer@engie.com |
| IAEA |  |  |  |
| 10 | Mr Robert Krivanek | Project manager for LTO | r.krivanek@iaea.org |

Background

Based on INRA invitation, an ‘IGALL Workshop on Ageing Management Establishment and Implementation’ was performed on 8-10 May 2017 by one IAEA staff and three external experts (IAEA team) with participants from INRA, BNPP and TAVANA. INRA sent to the IAEA in advance, a draft of ‘Ageing Management Safety Regulations for nuclear facilities’ for review. The IAEA team prepared comments on the draft of INRA regulation on ageing management prior to the workshop and sent them to INRA.

Work performed

First two and half day was devoted to presentations of IAEA team. INRA and TAVANA (on behalf of BNPP) also provided overview of their ageing management activities. Presentations followed based on the agreed agenda which is enclosed as Attachment A.

The third day afternoon of the workshop was devoted to presentation and discussion of INRA ‘Ageing Management Safety Regulations for nuclear facilities’. After a detail presentation, IAEA team asked supplementary questions to understand the objectives, function and details of presented regulations. During the last part of the third day, the IAEA team provided proposals for improvement of ‘Ageing Management Safety Regulations for nuclear facilities’. Further needs of IAEA support for INRA, BNPP and TAVANA were discussed and activities for 2017 and 2018 were agreed.

It was agreed that IAEA, INRA, BNPP and TAVANA will finalize meeting minutes within two weeks.

Conclusions

- Summary of proposals for improvement of INRA ‘Ageing Management Safety Regulations for nuclear facilities’

Peter Babics:

The basic principles can be summarized as follows:

The present document “Ageing Management Safety Regulations for Nuclear facilities” must be followed by licensees to guarantee their compliance with the basic safety principles as stipulated by the Iran Nuclear Regulatory Authority (INRA). In the introduction, the levels of regulation are described. According to this document ageing management safety regulations for nuclear facilities is on the third level of the regulation pyramid.

The findings:

- The document contains every regulation with great detail.

- Based on the level of this document (Regulation Document), it needs to be shorter and more concise.

- This kind of regulation leaves little room for developing the lower levels of documents (Guides) for the facilities.

- The regulations for the nuclear facilities and the other facilities should be presented in separately documents.

- The requirements are worded clearly and concisely, however some of the clarifications should be included in the lower level of regulatory documents (guides).

Requirement 7. Evaluation shall be completed for the management of ageing of each SSC or group….

1. Understanding ageing

2. Method to prevent ageing

3. Method to detect and monitor ageing other facilities

4. Methods to mitigate ageing

Requirement 12. The licensee shall establish ……………technological obsolescence that address the following:

1. Spare parts provision for planned service life and timely replacement of parts

2. Obsolescence is a general term, no need for explanation as some things may be left out.

According to a previous …, the reconciliation method should be used, which analyses the technical content and evaluates the up-to-date character of the procedure. 
The term obsolescence can be used for many things, e. g. documentation, equipment or regulations.

Summary: The main problem is excessive detail. It should be left to the INRA lower level document to expand the details. This is too rigorous.

Philippe d`Haeyer:

- Context

From 08-10 May 2017, a workshop on Ageing Management is organized by the Iran Nuclear Regulatory Authority (INRA).

The purpose of this workshop is to provide the Iran Nuclear Regulatory Authority with international information regarding the organizational structure of Ageing Management in Nuclear facilities. The purpose is to give information regarding the following topics:

- Regulatory context;

- Organization, planning, information sources, data management;

- Scoping and Ageing Management Review;

- Development of Ageing Management Programs and TLAAs

- Examples in the concerned domains (mechanical systems and structures, civil structures and E I&C).

In order to optimize the information exchange, The Iran Nuclear Regulatory Authority  (INRA) send  a draft version of the document integrating the  requirements on ageing management for nuclear facilities in the Islamic Republic of Iran.

The purpose of sending this document in prior is to give a preliminary overview of the comments before the scheduled meeting.

- Analysis framework

The analysis of the “Ageing Management Safety Regulations for nuclear facilities” document is performed by comparing its content to the new IAEA standards regarding “Ageing Management”, currently under review (“DS485”).

- Analysis results

The document “as presented” is a compilation of requirements integrated in the referenced documents:

- IAEA DS485, “Ageing Management and Development of a Program for Long Term Operation of Nuclear Power Plants” (draft version)

- STUK YVL A.8, “Ageing Management for a nuclear facility”

- RD-334, “Aging Management for nuclear Power Plants” (draft version).

During the writing of the expectations, requirements of the listed reference documents have been compiled. Minor modifications have been integrated:

- “Should” replaced by “shall” in order express the requirement;

- “Operating Organization” replaced by “Licensee”.

As such, the content of the document is globally in line with the reference documents used. As comment, the following items could be pointed out:

- Consider harmonizing “ageing” and “aging” (Canadian guidelines)

- What is the net added value of expectations different of summarizing IAEA expectations/standards?

- Consider consolidation of the document after the official issue of NS-G-2.12 (new version - e.g. “Corrective Program”)

Jan Wandrol:

Requirement 2. Here it is required to cover all SSCs. In the requirement 5 is required to use screening and selection system to establish a scope. These two requirements are in my point of view in contradiction.

Requirement 8. I miss here information that results of requirements shall be used as a basis for development and implementation of ageing management programme(s).

Requirement 9. Only specific AMPs? Other programmes important for ageing management are not required to follow these attributes?

Requirement 10. But the reason for increasing overhaul numbers and failure frequency can be other than ageing - e. g. human factor failures. I suggest to replace the word "improved" for the word "reviewed".

Requirement 19. What is the difference between specific AMPs and these AMPs? It should be defined somewhere.

Requirement 49. Why is the necessity for cooperation with design organizations  here?

Requirement 68. In my opinion this requirement should be general, not only specific for LTO.

IAEA Comments:

INRA requirements should reflect IAEA Specific Safety Requirement (SSR). SSR are different for different nuclear facilities and it should be reflected in INRA regulations. SSR 2/1 (e.g. Req.14, 15, 22, 23, 29, 30, 31) and SSR 2/2 (e.g. Req. 10, 11, 12, 13, 14, 15, 16, 29, 31) are applicable for nuclear power plants, SSR 3 is applicable for research reactors and SSR 4 is applicable for nuclear fuel cycle facilities.

IAEA Safety Guides can be used as more detail guidance. DS485 ‘AM and LTO for NNPs’ (NS-G-2.12 will be cancelled and superseded by DS485 soon) is a suitable guidance for NPPs and SSG-10 ‘AM for research reactors’. DS485 also applies to facilities for spent fuel storage and radioactive waste management but SSG-15 ‘Storage of Spent Nuclear Fuel’ should be also considered. For nuclear facilities other than NNPs and research reactors, there are no specific Safety Guides on ageing management but some recommendations from SSG-5 and SSG-6 are applicable.

It should be reflected in INRA regulations that requirements for different nuclear facilities are different, so guidance of their fulfilment should be also specific for different types of nuclear facilities. For example, SSG-25 on ‘PSR’ is intended only for NPPs and not for other nuclear facilities. Also GS-G-4.1 ‘Format and Content of the Safety Analysis Report for Nuclear Power Plants’ is intended primarily for NPPs and is only partially applicable for other nuclear facilities.

References to other national regulatory documents should not be mentioned.

- Future Activities

Based on discussions of current status of ageing management activities in Iran, it was agreed among the IAEA, INRA, BNPP and TAVANA representatives that the IAEA assistance is important and the following activities are requested by Iranian representatives for 2017 and 2018:

- Participation of INRA, BNPP and TAVANA experts in IGALL working groups in IGALL Phase 4 (2018-2019) - Ali Takht Ardeshir Iranian IGALL SC member will provide nominations based on results of IGALL SC before 31 January 2018.

- Participation of Iranian expert in a SALTO mission as an observer (BNPP/ TAVANA expert to South Ukraine NPP on 17-25 April 2018) - Mr. Deylami, BNPP/Mr. Ghods, TAVANA management will send to the IAEA the name and contact data of proposed expert, approval of his/her participation and approval of Iranian NLO to include this activity into BNPP TC project before 10 June 2017.

- BNPP TC project IRA2013 3.8.1-2 Scientific Visit on ‘Ageing Management Programmes Development and Implementation’ in Q4/2017 – INRA, BNPP and TAVANA and submit official nominations (max 4 persons) through Iranian NLO before 10 June 2017.

- J. Wandrol, UJV Rez will inform IAEA about possibility to host IRA2013 3.8.1-2 Scientific Visit in UJV Rez in Q4/2017 before 31 May 2017.

- IGALL workshop on ‘SSC scoping and development of AMPs’ for BNPP, INRA and TAVANA in Q1 2018 in Bushehr NPP. Mr. Deylami, BNPP will confirm exact topic and provide a contact data of contact person to IAEA before 10 June 2017.

- BNPP TC project IRA2013 3.8.1-1 Expert Mission on ‘Review of BNPP1 Ageing Management Programmes and TLAAs’ in Q3 2018 - Mr. Deylami, BNPP will provide a contact data of contact person to IAEA before 10 June 2017.

- Workshop on ‘IT support for ageing management’ – Mr. Deylami, BNPP will inform IAEA if this workshop is needed by email to IAEA before 10 June 2017 (BNPP  TC project).

- Support mission for INRA on development of regulations for ageing management, licensing renewal and PSR for nuclear power plants and research reactors in 2018 – INRA will confirm approval of management and Iranian NLO to include this activity into Iranian TC project before 10 June 2017.

Attachment A – Workshop agenda

DEPARTMENT of NUCLEAR SAFETY AND SECURITY

IAEA NATIONAL WORKSHOP

WORKSHOP AGENDA

IGALL Workshop on Ageing Management Establishment and Implementation

08-10 May, 2017

Tehran, Iran

Workshop subject, definition and details:

IGALL Workshop on Ageing Management Establishment and Implementation

- Type of assistance: National Workshop

- Organizations: INRA, NPPD

- Place: INRA, Tehran headquarter office, Tehran

- Liaison officer: Mr Ali Takht Ardeshir, AEOI, Senior expert of inspection group, National Nuclear Safety Department, Iran Nuclear Regulatory Authority (INRA), Tehran, Phone:+98-21-82067286, Email: aardeshir@aeoi.org.ir

• Needs and objective:

- Improve awareness and provide information on IAEA ageing management and LTO activities

- Provide presentations and discussions on lessons learned from ageing management and LTO preparation

- Identify terminology, references, approaches to scope setting for AM, AMR, AMP implementation and improvement

- Review of draft Iranian regulations for ageing management

• Scope of assistance:

- IAEA activities in LTO and AM

  - IAEA Safety Standards related to LTO and AM

  - New Safety Guide on AM and LTO

  - IGALL Programme and its results

- Provide presentations on national approaches to:

  - Regulatory requirements for ageing management

  - Ageing management – approach, scope of activities, planning, organizational structure to support AM, software support, databases

  - Scope setting of SSCs for AM

  - Ageing management review – performing and documenting

  - Establishment of ageing management programmes

  - Examples of AMPs in different professional areas

- Review of draft Iranian regulations for AM

Technical officers: Mr Robert Krivanek, IAEA (r.krivanek@iaea.org)

Experts:

- Mr. Peter Babics, Hungary, Hungarian Atomic Energy Authority (HAEA), Hungarian Atomic Energy Authority (HAEA), P.O. Box 676, Fenyes Adolf u. 4, 1036 Budapest, phone: 0036 1 4364900, email: Babics@haea.gov.hu

- Mr. Jan Wandrol, the Czech Republic, UJV Rez, a. s., Hlavni 130, 250 68 Husinec – Rez, phone: +420 266 172 517, cell: +420 725 648 916, email: jan.wandrol@ujv.cz

- Mr. P. d`Haeyer, Belgium, Electrabel SA, Avenue de l'Industrie, 1, Tihange 4500, phone: +32 85 24 68 01, mobile: +32 478 65 21 07, email: philippe.dhaeyer@electrabel.com

| Agenda |  |
| --- | --- |
| Day 1, Monday, 08 May 2017 |  |
| 08:00 08:30 08:40 | Departure from the hotel Workshop opening – Iranian host representative – Mr. Ardeshir 01_Mr. R.Krivanek – IAEA Safety Officer - Introduction, objectives and schedule Short introduction of the experts (Expert 1, Expert 2, Expert 3) Introduction of NPP and other participants |
| 08:50 09:20 | Short (max 10 min) country nuclear industry /company presentation of 02_ Expert 1 03_ Expert 2 04_ Expert 3 |
| 09:20 09:40 | 05_Regulatory requirements for ageing management in Iran —Mr. Ardeshir |
| 09:40 10:00 | 06_Ageing Management Program in Bushehr Nuclear Power Plant —Mr. Abyazi |
| Coffee break |  |
| 10:30 11:15 | 07_ IAEA Safety Standards related to LTO and ageing management – Mr. R.Krivanek, IAEA |
| 11:15 12:00 | 08_Regulatory requirements for ageing management in Hungary - Expert 1 |
| Lunch break |  |
| 13:00 13:45 | 09_ Regulatory requirements for ageing management in the Czech Republic - Expert 2 |
| 13:45 14:30 | 10_ Regulatory requirements for ageing management in Belgium – Expert 3 |
| Coffee break |  |
| 15:00 15:30 | 11_ New Safety Guide on Ageing Management and LTO – Mr. R.Krivanek, IAEA |
| 15:30 16:00 | 12_ Ageing management – scope of activities, planning, organizational structure to support AM – Expert 1 |

| Day 2, Tuesday, 09 May 2017 |  |
| --- | --- |
| 09:00 09:30 | 01_Ageing management – approach, scope of activities, planning, organizational structure to support AM, software support, databases – Expert 2 |
| 09:30 10:00 | 02_ Ageing management – approach, scope of activities, planning, organizational structure to support AM, software support, databases – Expert 3 |
| Coffee break |  |
| 10:30 11:15 | 03_ IGALL Programme – phase 1 and 2 results, phase 3 objectives (IGALL database, IGALL implementation, pilot plants, further development) – Mr. R.Krivanek, IAEA |
| 11:15 12:00 | 04_ Scope setting of SSCs for AM, Ageing Management Review - Expert 1 |
| Lunch break |  |
| 13:00 13:45 | 05_ Scope setting of SSCs for AM, Ageing Management Review - Expert 2 |
| 13:45 14:30 | 06_ Scope setting of SSCs for AM, Ageing Management Review - Expert 3 |
| Coffee break |  |
| 15:00 15:30 | 07_ Establishment of ageing management programmes - Expert 1 |
| 15:30 16:00 | 08_ Establishment of ageing management programmes - Expert 2 |

| Day 3, Wednesday, 10 May 2017 |  |
| --- | --- |
| 09:00 09:30 | 01_ Establishment of ageing management programmes - Expert 3 |
| 09:30 10:00 | 02_ Examples of AMPs in different professional areas - Expert 1 |
| Coffee break |  |
| 10:30 11:15 | 03_ Ageing management programme for RPV and reactor internals - Expert 2 |
| 11:15 12:00 | 04_ Examples of AMPs in different professional areas - Expert 3 |
| Lunch break |  |
| 13:00 14:30 | Review of draft Iranian regulations for AM – Experts 1, 2 and 3 |
| Coffee break |  |
| 15:00 15:30 | Review of draft Iranian regulations for AM – Experts 1, 2 and 3 |
| 15:30 16:00 | Conclusions, planning of further activities, wrap up of workshop |

Attachment B – List of Participants

Please add a list of Iranian participants (Name, surmane, Company, position, email)