**Форма РКЦ-4 (Format RCC-4 )**

**Запрос об оказании экспертной / консультативной и инженерно-технической поддержки/**

***Request for expert/consultative and engineering support***

**сообщение / *message* № *4***

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Адресат /*Аddressee:* | | | | *Bushehr NPP* | | | | | | | | | |
| От /*From:* | | | | Региональный кризисный центр ВАО АЭС в Москве  *WANO Moscow Centre Regional Crisis Centre* | | | | | | | | | |
| Факс /*Fax:* | | +7 (495) 644-33-88 | | | | Эл. почта / Email: | Bnpp.ics@nppd.co.ir | | | Телефон / Phone: | | | +7 (495) 589-25-25 |
| Число страниц (Pages) | | | | | | 1 | | | | | | | |
|  | срочно  */urgently* | |  | | требует ответа /*response required* | | |  | для ознакомления / *for information* | |  | подтвердить получение  */acknowledge receipt* | |

1. Станция /Plant: Bushehr NPP Блок / Unit: 1 Страна / Сountry:Iran

2. Ответ / Content of answer:

|  |
| --- |
| MC technical support centers has approved the way to feed the reactor by boric water from the stage-1&2 passive tanks of the reactor core emergency cooling system for prolongation of the reactor cooling. Technical support centers suggest to energize safety train by mobile diesel generators and, if it need, to request support from other MC RCC’s members for prompt supply mobile diesel generators from other sites. |

|  |
| --- |
| стр. 1 из 1  page 1 of 1 |