|  | World Association of Nuclear Operators Moscow Centre WANO – MC 25 Ferganskaya, Moscow, 109507, Russia Phone. +7 495 376 15 87 Fax: +7 495 376 08 97 info@wanomc.ru |
| --- | --- |

REQUEST

To provide technical and organizational information via WANO

- NPP/Organization: Kudankulam NPP

- The topic of information request: pH value at 25 Deg C and Ammonia concentration in blow down sample from salt compartment & bottom blow down of Steam Generator (SG), when plant is operating at full power.

- The goal of information request: Getting relevant information from operating VVER-1000 plants

4. Problem description: KKNPP is observing that pH at 25 Deg C of Steam Generator salt compartments blow down water is in the range 8.8 – 9.0 against the specified limit of 9.0 – 9.5 at full power. Ammonia is used as alkalizing medium for secondary circuit.

5. Specific questions: - What is the pH at 25 Deg C and Ammonia concentration for the following sample of VVER plant? Sl.No; Sampling point; pH at 25 Deg C; Ammonia (µg/Litre). Condensate water. Discharge of Condensate extraction pump #2. Deaerator water. Feed water after High Pressure Heater. SG blow down from salt compartment. SG blow down from bottom blow down. SG Steam. - SG salt compartment blow down rate and periodic line blowdown rate? - Mode of continuous and periodic blowdown? - How many SG blowdown purification filters LCQ71-74 in service? - What is the purification flow through LCQ71-74 filter?

6.Proposed organizations for sending this request: NPPs of WANO-MC having VVER type of units

7.Department – request initiator: Technical Services, Kudankulam NPP

9.Contact details of the requester: Sanjeev Bhardwaj , WANO-MC contact Person +91-9489080628, Email : sbhardwaj@npcil.co.in

10.Date of request: 06.07.2020