## 12.1 Provision of lowest possible levels of occupational exposure

### 12.1.1 Organizational activities

The main purpose of establishing an effective radiation protection is to maintain occupational risks, caused by radiation exposure of the plant personnel, below the level of occupational risks in other human work-related activities [1].

Optimization of the radiation protection design is performed by implementing the ICRP recommendation to limit the personnel radiation exposure on the basis of the so-called As Low As Reasonably Achievable (ALARA) principle [2, 3]. The ALARA principle is used only within the framework of qualitative optimization of radiation protection, based on the information obtained during the operation of plants with similar design, the available design experience, and selection of the most acceptable alternative from the economic point of view. The Balakovo NPP Unit 4 with WWER-1000 reactor (V-320) is taken as a reference unit. Experience in design and operation of the unit mentioned and other similar NPPs is utilized to verify the calculation programs [13,14], used for design substantiation of the Bushehr NPP Unit 1 radiation protection.

At the same time, in some cases, when estimating radiation doses, a conservative approach is used to reach adequate level of confidence in the results obtained.

The ALARA principle is applied only to optimization of personnel radiation exposure during plant normal operation. The practical application of the ALARA principle in the design is connected with analysis and the optimization of personnel collective dose during scheduled maintenance activities and refueling. In the case of accidents all technical and organizational solutions related to radiation protection are based on limiting individual emergency radiation doses.

Sub-section 13.5.2.2 of chapter13 FSAR contains description of procedures which have been developed to ensure that occupational exposure meets the ALARA principle.

Duties, responsibilities and appropriate actions of the management in charge of the radiation protection are described in Chapter 13 of the FSAR.

###### Normal operation

As an acceptable criterion of radiation protection effectiveness for normal operating conditions, the individual exposure dose limits for personnel have been established [4,5], which are presented in Table 12.1.1-1.

Table 12.1.1-1 Maximum permissible doses (MPD) for normal operating conditions

| Established value | MPD |  |
| --- | --- | --- |
|  | Personnel of group A | Personnel of group B |
| Effective doses | 20 mSv avg. per year for any consecutive 5 years, but not exceeding 50 mSv for any single year | 3/10 of MPD of group A (determined by the Principal) |
| Equivalent doses per year, mSv: |  |  |
| - crystalline lens | 150 | 45 |
| - skin | 500 | 150 |
| - hands, feet | 500 | 150 |

The limit of collective dose for personnel, employed at the plant, for 1 GW of net electric power is 5 pers.Sv/year.

For reliable fulfillment of this criterion, the design sets a target limit for personnel collective dose during scheduled works, connected with dose loads during disassembling, assembling, equipment inspection and refueling, for 1 GW of net electric power – 0,5 pers.Sv/year.

The refence level for personnel 0.5 man-Sv/year per 1 GW(e) of installed capacity pertains to yearly conducted regular operations for reactor disassembly, assembly, spent fuel handling. The dose limit 5 man-Sv/year includes, in addition to the above operations, the operations for full inspection on the reactor plant, conducted once every four years, and possible repairs.

Breakdown of the exposure dose rates by the types of activities during planned preventive maintenance at the Balakovo NPP, Unit 3 (03.06  31.07.2000):

| - RCP planned preventive maintenance - 0,0184 man. Sv; |  |
| --- | --- |
| - steam generator planned preventive maintenance - 0,6049 man. Sv; |  |
| - pressurizer planned preventive maintenance – 0.1411 man. Sv; |  |
| - control and protection system (CPS) parts and mecvhanismsplanned preventive maintenance - | 0.0079 man. Sv; |
| - handling operations with spent fuel container ТК-13 – 0.0017 man. Sv; |  |
| - active water treatment system transformers and equipment repair - | 0.0039 man. Sv; |
| - scaffolding and heat insulation activitites – 0.0079 man. Sv; |  |
| - radioactive waste handling – 0.0011 man. Sv; |  |
| - reactor activitites – 0.1411 man. Sv; |  |
| - other activitites – 0.0009 man. Sv. |  |

The plant is designed so that, during normal operation with consideration of off-design situations, the above-mentioned limits should not be exceeded.

Design estimation of personnel radiation exposure dose during normal operation and in anticipated operational occurrences is conducted with consideration of all factors influencing the exposure dose.

Each potentially substantial radiation exposure dose is estimated separately for main operations, such as maintenance, refueling, and for non-scheduled operations, such as repair, removal or replacement of equipment.

###### Design-basis accidents

As acceptable criteria for radiation protection effectiveness during design accidents, not considering their mitigation, the following personnel radiation dose limits have been established:

- personnel of group A - effective dose 50 mSv;

- personnel of group B – 3/10 of group A.

Planned increased radiation exposure during mitigation of the consequences of a radiation accident is permitted only in case, when there is no possibility to take measures on preventing these limits from being violated, and may be justified only by the necessity of saving people’s lives, prevention of accident spread and mass radiation exposure. Planned increased irradiation during mitigation of the consequences of accidents should not exceed the following level [5]:

#### 12.2.1.1  Radiation sources in the Reactor Building (ZA/B)

Reactor core and reactor pressure vessel internals

The main source of radiation in the primary system during power operation is the reactor core. Group densities of neutron fluxes in the core, averaged over the core volume are given in Table 12.2.1.1-1.

Table 12.2.1.1-1 Group neutron flux densities averaged over the core volume

| Neutron energy range, MeV | Neutron flux density, neutr./(cm2s) |
| --- | --- |
| 1,22101… 1,50101 | 2,091010 |
| 1,00101… 1,22101 | 1,111011 |
| 8,18100 …1,00101 | 4,341011 |
| 6,36100 …8,18100 | 1,751012 |
| 4,96100 …6,36100 | 4,241012 |
| 4,06100 …4,96100 | 5,691012 |
| 3,01100 …4,06100 | 1,181013 |
| 2,46100 …3,01100 | 1,171013 |
| 2,35100 …2,46100 | 3,141013 |
| 1,83100 …2,35100 | 1,461013 |
| 1,11100 …1,83100 | 3,101013 |
| 5,5010-1…1,11100 | 4,271013 |
| 1,1110-1…5,5010-1 | 6,031013 |
| 3,3510-3…1,1110-1 | 6,321013 |
| 5,8310-4…3,3510-3 | 2,541013 |
| 1,0110-4…5,8310-4 | 2,081013 |
| 2,9010-5…1,0110-4 | 1,011013 |
| 1,0710-5…2,9010-5 | 5,491012 |
| 3,0610-6…1,0710-5 | 4,901012 |
| 1,1210-6…3,0610-6 | 4,641012 |
| 4,1410-7…1,1210-6 | 4,42 1012 |
| 1,0010-9…4,1410-7 | 1,761013 |

Induced activity of the RPV internals determines the radiation situation for handling operations and scheduled maintenance and repair of the reactor internals. The activity analysis of RPV internals was carried out using the results of analysis of neutron flux distribution in the reactor volume.

Initial data for analysis of volumetric activity of radionuclides in the RPV internals are given in Table 12.2.1.1-2.

Table 12.2.1.1-2 Initial data for analysis of volumetric activity of radionuclides in the RPV internals

| Chemical element | Chromium | Iron |  | Nickel | Cobalt |
| --- | --- | --- | --- | --- | --- |
| Content in stainless steel, in parts of the unit | 0.185 | 0.700 |  | 0.110 | 2.500x10-4 |
| Mother nuclide | Cr-50 | Fe-54 | Fe-58 | Ni-58 | Co-59 |
| Content in natural mixture, in parts of the unit | 4.310x10-2 | 5.820x10-2 | 3.100x10-3 | 0.668 | 1.000 |
| Radionuclide produced | Cr-51 | Mn-54 | Fe-59 | Co-58 | Co-60 |
| Decay constant, s-1 | 2.870x10-7 | 2.740x10-8 | 1.780x10-7 | 1.120x10-7 | 4.160x10-9 |

Maximum activities of nuclides in the RPV internals components are given in Table 12.2.1.1-3.

Table 12.2.1.1-3 Maximum values of radionuclides volumetric activity in the reactor internals, Bq/ cm3

| RPV internals component | Radionuclide |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Cr-51 | Mn-54 | Co-58 | Fe-59 | Co-60 |
| Internal surface of the enclosure | 1.101011 | 9.20109 | 2.20109 | 3.30109 | 1.401010 |
| Internal surface of the vault | 2.501010 | 4.30108 | 1.10109 | 6.50108 | 2.60109 |
| Top of the support cylinders of the vault bottom | 8.40109 | 1.50108 | 3.60108 | 1.70108 | 5.90108 |
| Bottom of the lower plate of protective tubes | 7.60107 | 4.50106 | 1.10107 | 1.80106 | 6.40106 |

Activity of the fission products in the spent fuel is decisive with respect to the formation of gamma-radiation fields during transport operations with spent fuel and storage of spent fuel assemblies in the cooling pool. The sources of gamma-radiation from the spent fuel were determined depending on the sources of power, operation time and spent fuel assemblies cooling time with regard to fission fragment release and patterns of their radioactive transformations. The results for the most energy-critical spent fuel assembly and for 3-day, 10-day and 30-day cooling time are given in Table 12.2.1.1-4; the results for 1-year, 2-year and 3-year cooling time are given in Table 12.2.1.1-5.

Table 12.2.1.1-4 Volumetric intensity of gamma-radiation sources of a spent fuel assembly (FA)

| 3-day cooling |  | 10-day cooling |  | 30-day cooling |  |
| --- | --- | --- | --- | --- | --- |
| Effective energy, MeV | Volumetric intensity, /cm3s | Effective energy, MeV | Volumetric intensity, /cm3s | Effective energy, MeV | Volumetric intensity, /cm3s |
| 2.52 | 7.10109 | 2.48 | 6.50109 | 2.48 | 2.20109 |
| 2.10 | 8.70109 | 1.61 | 1.401011 | 1.62 | 4.701010 |
| 1.56 | 2.201011 | 1.24 | 1.501010 | 1.20 | 5.20109 |
| 0.79 | 5.501011 | 0.77 | 4.801011 | 0.77 | 3.601011 |
| 0.63 | 3.901011 | 0.53 | 3.101011 | 0.52 | 1.701011 |
| 0.44 | 3.801011 | 0.37 | 8.501010 | 0.37 | 2.301010 |
| 0.25 | 1.301011 | 0.26 | 3.201010 | 0.29 | 4.60109 |
| 0.17 | 2.201010 | 0.17 | 1.001010 | 0.17 | 3.20109 |
| 0.14 | 2.101011 | 0.14 | 1.101011 | 0.14 | 6.401010 |

Table 12.2.1.1-5 Volumetric intensity of gamma radiation sources of a spent FA

| 1-year cooling |  | 2-year cooling |  | 3-year cooling |  |
| --- | --- | --- | --- | --- | --- |
| Effective energy, MeV | Volumetric intensity, /cm3s | Effective energy, MeV | Volumetric intensity, /cm3s | Effective energy, MeV | Volumetric intensity, /cm3s |
| 2.18 | 3.90108 | 2.18 | 1.60108 | 2.18 | 6.60107 |
| 1.51 | 2.20108 | 1.52 | 1.10108 | 1.53 | 5.50107 |
| 1.21 | 1.20109 | 1.21 | 8.20108 | 1.23 | 5.70107 |
| 0.78 | 1.80108 | 0.80 | 5.60109 | 0.80 | 3.90109 |
| 0.64 | 2.101010 | 0.63 | 1.501010 | 0.64 | 1.201010 |
| 0.50 | 4.70109 | 0.50 | 2.30109 | 0.50 | 1.20109 |
| 0.36 | 1.30107 | 0.30 | 3.40106 | 0.30 | 2.50106 |
| 0.24 | 5.50107 | 0.24 | 4.00107 | 0.24 | 3.70107 |
| 0.16 | 6.90107 | 0.18 | 2.30107 | 0.18 | 1.80107 |
| 0.13 | 5.80109 | 0.13 | 2.60109 | 0.13 | 1.20109 |

The activities of the fission products accumulated in the fuel rods and in the gas space of the fuel rods during power operation are the sources in the analysis of radiation protection of the systems provided for mitigation of accidents connected with fuel element leakage. The total activity of fission products in the fuel rods and compensating volume of the core fuel elements during reactor operation at the rated power at the end of fuel residence time in the steady-state refuelling cycle are given in Table 12.2.1.1-6. The initial data for calculation are presented in Table 12.2.1.1-7.

Table 12.2.1.1-6. Activity of fission products in the fuel and compensating volume of the fuel elements

| Nuclide | Activity of fission products in fuel, Bq | Activity of fission products in compensating volume of fuel elements, Bq |
| --- | --- | --- |
| Br-84 | 8.921017 | 1.881014 |
| Kr-85m | 8.331017 | 4.291014 |
| Kr-85 | 3.601016 | 2.691014 |
| Br-87 | 2.211018 | 8.701013 |
| Kr-87 | 2.351018 | 6.401014 |
| Kr-88 | 3.151018 | 1.221015 |
| Rb-88 | 3.151018 | 1.221015 |
| Kr-89 | 4.111018 | 2.561014 |
| Rb-89 | 4.331018 | 7.361014 |
| Sr-89 | 4.331018 | 3.351016 |
| Kr-90 | 4.181018 | 1.261014 |
| Rb-90 | 4.001018 | 2.791014 |
| Sr-90 | 2.661017 | 1.931015 |
| Sr-91 | 4.401018 | 3.101015 |
| Sr-92 | 5.441018 | 1.971015 |
| Zr-95 | 6.071018 | 5.111016 |
| Nb-95 | 6.071018 | 8.811016 |

Continuation of Table 12.2.1.1-6

| Nuclide | Activity of fission products in fuel, Bq | Activity of fission products in compensating volume of fuel elements, Bq |
| --- | --- | --- |
| Zr-97 | 5.551018 | 4.881015 |
| Nb-97 | 5.621018 | 6.331015 |
| Mo-99 | 2.421017 | 5.881013 |
| Ru-103 | 2.761018 | 1.811016 |
| Ru-106 | 2.861017 | 1.991015 |
| Rh-106 | 2.861017 | 1.991015 |
| Te-131 | 2.461018 | 7.991014 |
| I-131 | 2.821018 | 9.511015 |
| Te-132 | 3.851018 | 7.361015 |
| I-132 | 3.851018 | 8.621015 |
| Te-133 | 4.001018 | 4.591014 |
| I-133 | 6.961018 | 7.811015 |
| Xe-133 | 6.961018 | 2.431016 |
| Cs-134 | 1.451018 | 1.261016 |
| I-134 | 7.251018 | 2.641015 |
| I-135 | 5.881018 | 3.221015 |
| Xe-135 | 8.731017 | 6.851014 |
| Cs-137 | 2.901017 | 2.101015 |
| Ba-139 | 5.771018 | 2.141015 |
| Ba-140 | 5.921018 | 2.221016 |
| La-140 | 5.961018 | 3.021016 |
| Ce-141 | 5.371018 | 3.301016 |
| Ce-144 | 4.401018 | 3.011016 |
| Pr-144 | 4.401018 | 3.061016 |
| Total IRG | 2.251019 | 2.791016 |
| Total Iodines | 2.681019 | 3.181016 |
| Grand Total | 1.491020 | 4.471017 |

Reactor coolant system

The sources of radiation in the primary coolant are fission products taken in through the leakage in the cladding, oxygen and admixtures activation products and activated products of the primary inside surfaces corrosion.

The oxygen activity of the primary coolant is decisive from the point of view of formation of gamma-radiation in the steam-generator enclosure and adjacent rooms.

The initial data for analysis of the primary coolant activity are given in 
Table 12.2.1.1-7.

Table 12.2.1.1-7  List of initial data for analysis of the primary coolant activity

| Parameters | Values |  |
| --- | --- | --- |
| Reactor thermal output, MWt | 3,000 |  |
| Normal time of FA residence in the core, years | 3 |  |
| Operation time between two refuellings (not less than), h | 7,000 |  |
| Primary system pressure, MPa | 15.7 |  |
| Primary system temperature, °С: |  |  |
| - inlet |  | 291 |
| - outlet |  | 321 |
| Coolant flowrate through the reactor, m3/h |  | 84,800 |
| Core sizes: |  |  |
| - volume, m3 |  | 27.800 |
| - diameter, m |  | 3.160 |
| - height, m |  | 3.550 |
| Coolant volume in the core, m3 |  | 14.800 |
| Coolant density, g/cm3: |  |  |
| - inlet |  | 0.743 |
| - outlet |  | 0.675 |
| - average |  | 0.709 |
| Coolant volume in the circulating pipelines (without the pressurizer), m3 |  | 294 |
| Surface outside irradiated area (stainless steel), m2 |  | 2.230104 |
| Core zirconium surface, m2 |  | 8.880103 |

Continuation of Table 12.2.1.1-7

| Parameters | Values |
| --- | --- |
| Neutron flux density, core volume averaged, n/cm2sec: |  |
| - heat | 6.0001013 |
| - fast Е>1,5 MeV | 5.9901013 |
| - fast Е>2,5 MeV | 2.5501013 |
| Amount of uranium in the core (averaged over the normal time of residence of FA in the core), kg | 1.260103 |
| Number of fuel rods in reactor core (FR/core) | 50,693 |
| Height of fuel column in fuel element, m | 3.530 |
| Fuel pellet axis hole diameter, m | 1.50010-3 |
| Fuel pellet OD, m | 7.57010-3 |
| Fuel pellet height, m | 1.10010-2 |
| Full surface of fuel element in reactor core, m2 | 5.140103 |
| Power peaking factor: |  |
| - radial | 1.420 |
| - axial | 1.160 |
| Fraction of sufficient cladding destruction – operation limit | 210-4 |
| Constant of fission product release into the coolant due to sufficient destruction, 1/sec | 1∙10-2 |
| Gas leakage fraction – operational limit | 210-3 |
| Constant of fission product release from the axis hole of failed fuel element into the coolant, 1/sec | 510-5 |
| Coolant flowrate for purification (TC system), t/h | 30 |
| Uncontrolled leakage flowrate, t/h | 0.1 |
| Coolant flowrate for deaeration, t/h | 34.8 |
| Time of coolant passage through the TC purification system, h | 0.054 |
| Time of coolant passage through the deaeration system, h | 4.150 |
| Time of activity accumulation on the TC purification system filter, h | 7000 |

Continuation of Table 12.2.1.1-7

| Parameters | Values |
| --- | --- |
| Sediment factor for bypass cleaning: - Na, Rb - I, Br - Cs - Ba, Sr - Mn, Co, etc Note  said chemicals sedimantation coefficients on the ТС system filters are taken from the operation experience (averaged values for operating nuclear power plants with VVER reactors). Possible fluctuations of the accepted values during plant operation may be insignificant and will not affect the primary coolant activity fluctuation whcih may cause exceeding of the exposure dose rates for the personnel and the public above the acceptance radiation criteria. | 0.990 0.900 0.000 0.990 0.750 |

1. The SGs heat exchanging pipes surfaces are subject to the following pretreatment (in Chapter 5 of FSAR this information is absent):

- inside – electrochemical polishing;

- outside – grinding.

2. Optimization of water chemistry mode was performed with COTRAN-M code  application. These parameters are provided in chapter9, subsection 9.2.6.3 of FSAR.

Primary coolant purification efficiency of corrosion products of high-temperature fuilter TC 60-90 obtained from the Balakovo NPP, are as follows:

| - general iron |  50…90 %; |
| --- | --- |
| - chrom-51 |  80…85 %; |
| - cobalt-60 |  50…70 %; |
| - iron-59 |  90 %. |

The data on volumetric activity of N-16 and N-17 radionuclides in various points of the primary system are given in Table 12.2.1.1-8.

Table 12.2.1.1-8 Activity of N-16 and N-17 radioactive nuclides in the primary circuit

| Part of the primary system | Radioactive nuclide activity, Bq/cm3 |  |
| --- | --- | --- |
|  | N-16 | N-17 |
| In the reactor at channel head level | 6.51106 | 1.55103 |
| In the reactor at outlet pipes axes level | 5.73106 | 1.25103 |
| In the reactor in the center of volume under the spherical cover | 5.20106 | 1.06103 |
| In the pipelines at the SG inlet | 5.00106 | 9.94102 |
| In the pipelines at the SG outlet | 3.59106 | 5.67102 |
| In the pipe at the reactor inlet | 2.70106 | 3.52102 |
| In the reactor in the center of volume under the core | 2.36106 | 2.79102 |

Outside the SG compartment due to the short half-life period of N-16 (7.35 sec), the activity of the primary coolant during power operation is in practice entirely determined by the fuel element cladding leakage. Activity of fission products in the primary coolant is used in designing protection and service systems in the operating reactor unit, and also in analysis of possible air contamination of controlled access area rooms.

The initial data for analysis of fission products activity are given in Table 12.2.1.1-7.

The equilibrium content of fission products in the primary coolant calculated for long-term power operation of the unit when fuel elements reach the operation limit for their leakage as per PBYA RU-89 (10) are given in Table 12.2.1.1-9.

Table 12.2.1.1-9 Activity of fission product in the primary coolant

| Nuclide | Volumetric activity of the primary coolant, Bq/m3 |  |
| --- | --- | --- |
|  | Full power operating conditions | In the process of decreasing the reactor power |
| Br-84 | 4.96108 | 1.11010 |
| Kr-85m | 1.76109 | 8.7109 |
| Kr-85 | 7.49105 | 2.08106 |
| Br-87 | 5.41108 | 2.631010 |
| Kr-87 | 2.69109 | 2.751010 |
| Kr-88 | 5.51109 | 3.461010 |
| Rb-88 | 5.85109 | 3.431010 |
| Kr-89 | 1.32109 | 4.781010 |
| Rb-89 | 2.05109 | 5.011010 |
| Sr-89 | 8.27106 | 8.27106 |
| Kr-90 | 8.98108 | 4.831010 |
| Rb-90 | 1.28109 | 4.621010 |
| Sr-90 | 2.87104 | 2.87104 |
| Sr-91 | 3.72108 | 3.72108 |
| Sr-92 | 5.49108 | 5.49108 |
| Mo-99 | 3.12106 | 3.12106 |
| Ru-103 | 2.67106 | 2.67106 |
| Ru-106 | 3.74104 | 3.74104 |
| Rh-106 | 3.74104 | 3.74104 |
| Te-131 | 2.82108 | 2.82108 |
| I-131 | 1.34109 | 2.21010 |
| Te-132 | 3.88107 | 3.88107 |
| I-132 | 3.3109 | 5.851010 |
| Te-133 | 5.09108 | 5.09108 |
| I-133 | 3.83109 | 4.861010 |
| Xe-133 | 4.53109 | 1.231010 |

Continuation of Table 12.2.1.1-9

| Nuclide | Volumetric activity of the primary coolant Bq/m3 |  |
| --- | --- | --- |
|  | Full power operating conditions | In the process of decreasing the reactor power |
| I-134 | 2.93109 | 4.531010 |
| Cs-134 | 1.16109 | 1.23109 |
| I-135 | 3.38109 | 3.641010 |
| Xe-135 | 3.30109 | 7.84109 |
| Cs-137 | 1.85109 | 1.96109 |
| Xe-138 | 1.82109 | 3.321010 |
| Cs-138 | 2.90109 | 3.541010 |
| Ba-139 | 1.22109 | 1.22109 |
| Ba-140 | 1.76107 | 1.76107 |
| La-140 | 2.52106 | 2.52106 |
| Ce-141 | 4.04106 | 4.04106 |
| Ce-144 | 6.17105 | 6.17105 |
| Pr-144 | 5.91105 | 5.91105 |
| Zr-95 | 3.61106 | 3.61106 |
| Nb-95 | 2.95104 | 2.95104 |
| Zr-97 | 2.22108 | 2.22108 |
| Nb-97 | 1.95108 | 1.95108 |
| Total IRG | 2.181010 | 2.201011 |
| Total Iodines | 1.481010 | 2.111011 |
| Grand Total | 5.621010 | 6.411011 |

In calculating the activity of the primary coolant, all the fission products release processes, which are described in [13], are taken into account.

Operational data for primary coolant activity during 100% power operation of Balakovo NPP, Unit 1. (To compare with the data provide4d in Table 12.2.1.1-9 in Chapter 12 of the FSAR)

| Radionuclide | Volumetric activity of the primary coolant, Bq/m3 |  |  |
| --- | --- | --- | --- |
|  | 06.03.01 | 02.04.01 | 04.06.01 |
| I-131 | 8,70107 | 7,70108 | 1,10108 |
| I-132 | 1,60108 | 1,40108 | 2,00108 |
| I-133 | 2,20108 | 2,10108 | 2,60108 |
| I-134 | 2,50108 | 2,10108 | 2,90108 |
| I-135 | 2,50108 | 2,10108 | 3,20108 |
| Cs-134 | 2,60107 | 2,40107 | 2,10107 |
| Cs-137 | 2,90107 | 2,10107 | 1,80107 |
| Rb-88 | 1,00108 | 1,30108 | 1,40108 |
| Rb-89 | 1,00108 | 6,90107 | 1,30108 |
| Na-24 | 1,60109 | 1,60109 | 1,70109 |
| K-42 | 8,70109 | 7,70109 | 8,90109 |
| Co-60 | no measured data | 2,60105 | no measured data |
| Fe-59 | no measured data | 2,60105 | no measured data |
| Xe-135 | 2,40107 | 5,30107 | 7,40107 |

Primary coolant activity at the Balakovo NPP.

Unit 2

| Radionuclide | Volumetric activity of the primary coolant, Bq/m3 |  |  |
| --- | --- | --- | --- |
|  | 10.04.2000 | 17.07.2000 | 20.02.2001 |
| I-131 | 2,52ּ108 | 3,98ּ108 | 7,42ּ108 |
| I-132 | 2,92ּ108 | 3,45ּ108 | 1,38ּ109 |
| I-133 | 6,89ּ108 | 6,36ּ108 | 1,78ּ109 |
| I-134 | 3,71ּ108 | 4,24ּ108 | 1,27ּ109 |
| I-135 | 5,83ּ108 | 5,04ּ108 | 1,80ּ109 |
| Cs-134 | 2,65ּ107 | 1,86ּ107 | 4,51ּ107 |
| Cs-137 | 3,71ּ107 | 2,39ּ107 | 3,45ּ107 |
| Rb-88 | 1,62ּ109 | 2,65ּ109 | 6,89ּ109 |
| Rb-89 | 2,54ּ108 | 2,54ּ108 | 6,63ּ108 |
| Xe-135 | 5,83ּ108 | 9,01ּ108 | 1,43ּ109 |

Primary coolant activity at the Balakovo NPP.

Unit 3

| Radionuclide | Volumetric activity of the primary coolant, Bq/m3 |  |  |
| --- | --- | --- | --- |
|  | 20.09.2000 | 22.01.2001 | 23.05.2001 |
| I-131 | 1,06ּ107 | 2,65ּ107 | 2,39ּ107 |
| I-132 | 1,33ּ107 | 3,18ּ107 | 2,92ּ107 |
| I-133 | 2,12ּ107 | 5,56ּ107 | 3,45ּ107 |
| I-134 | 3,71ּ107 | 4,24ּ107 | 3,98ּ107 |
| I-135 | 2,65ּ107 | 5,56ּ107 | 3,98ּ107 |
| Cs-134 | 3,98ּ107 | 2,39ּ107 | 3,18ּ106 |
| Cs-137 | 3,45ּ107 | 2,65ּ107 | 4,51ּ106 |
| Rb-88 | 6,10ּ107 | 1,62ּ108 | 1,64ּ108 |
| Rb-89 | no measured data | no measured data | 2,39ּ107 |
| Xe-135 | no measured data | 2,39ּ107 | 3,98ּ107 |

Unit 4

| Radionuclide | Volumetric activity of the primary coolant, Bq/m3 |  |  |
| --- | --- | --- | --- |
|  | 26.06.2000 | 25.10.2001 | 23.05.2001 |
| I-131 | 5,30ּ108 | 2,92ּ108 | 3,18ּ108 |
| I-132 | 5,04ּ108 | 6,89ּ108 | 8,75ּ108 |
| I-133 | 9,54ּ108 | 8,22ּ108 | 9,54ּ108 |
| I-134 | 6,36ּ108 | 1,01ּ109 | 1,33ּ109 |
| I-135 | 8,75ּ108 | 9,81ּ108 | 1,25ּ109 |
| Cs-134 | 3,98ּ108 | 3,71ּ108 | 1,40ּ108 |
| Cs-137 | 3,18ּ108 | 2,92ּ108 | 1,14ּ108 |
| Rb-88 | 2,65ּ109 | 3,97ּ109 | 5,04ּ109 |
| Rb-89 | 3,45ּ108 | 5,30ּ108 | 8,75ּ108 |
| Xe-135 | 3,71ּ108 | 5,83ּ108 | 1,62ּ108 |

The calculated values of the activity of tritium, Na-24 and K-42 in the primary coolant are presented in Chapter 11 of the PSAR; they amount to:

Tritium - 1.591010 Bq/m3;

Na-24 - 1.85109 Bq/m3;

K-42 - 8.14109 Bq/m3.

As can be seen from Table 12.2.1.1-9, in the process of decreasing the reactor power, the activity of the primary coolant increases due to additional release of gaseous and volatile fission products, stored in the gas space of leaking fuel elements because of the spike-process. This activity increase is short-term, about 4 h and after that it decreases down to the activity value under rated operating conditions and below due to constant treatment of the coolant with ion-exchange filters with further degassing.

The most intensive fission product release is observed under decrease of reactor power by lower than 30%.

The calculated levels of corrosion products activity are used for determination of exposure doses for the personnel during scheduled refueling.

The input data (reactor core parameters and process parameters of the primary coolant), which are necessary for the analysis of corrosion products activity are given in Table 12.2.1.1-7.

Activity of corrosion products in the primary coolant is given in Table 12.2.1.1-10.

Table 12.2.1.1-10 Activity of corrosion products in the primary coolant

| Nuclide | Activity of corrosion products, Bq/m3 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Fe-59 | Co-58 | Cr-51 | Mn-54 | Co-60 | Total |
| Colloids | 7.68103 | 3.38104 | 8.40104 | 1.25104 | 8.90104 | 2.27105 |
| Ions | 5.73104 | 2.23105 | 3.78105 | 5.46104 | 6.12105 | 1.32106 |
| Total | 6.50104 | 2.56105 | 4.62105 | 6.71104 | 7.01105 | 1.55106 |

Activity of the corrosion products on the equipment surfaces washed with the primary coolant is given in Table 12.2.1.1-11. The content of cobalt in the steel of SG, reactor coolant pipelines and protective tubes system is taken as 0.0915%.

Under calculations for chapter  12 PSAR NPP Busher  they  accept the  following  content of cobalt  in materials  swept with  the primary circuit coolant:

- core baffle, vessel core barrel,  bottom plate of the protective tube unit and  anticorrosive welding of  the reactor pressure vessel  – 0,025%;

- other surfaces of  stainless steel – 0,0915% (that is  equal to cobalt content  in  heat-exchange tube steel used to  manufacture the steam generators  of Russian NPP S VVER-1000 in period of 1980-1986). Difference is explained by different   processing capabilities of equipment  manufacturers.

Lower cobalt content  first of all in tubes  is explained by  absence of  cobalt content limits  in normative documentation for tube manufacturing  at that time. Imposing the restrictions was  featherbedding  at that time because of  absence of  collective dose limits, NPP construction slowdown, absence of  appropriate   customer requirements.

CPS Ars  guide channels, central tubes and  FA  spacing grids for NPP “Busher” will be manufactured  of  zirconium alloy   110  (Zr+1 % Nb)  instead of  stainless steel.

According to the estimations, replacement of stainless steel for zirconium alloy 110 results in 60Co activity reduction on non-irradiated surfaces (that is, not subjected to a considerable neutron flux exposure) of the primary circuit approximately up to 30 % under other identical conditions.

Table 12.1.1-11 Activity of corrosion products on the surfaces of the primary coolant system

|  | Activity of corrosion products, Bq/m2 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Component of structure | Radioactive nuclide |  |  |  |  |  |  |  |  |  |
|  | Fe-59 |  | Co-58 |  | Cr-51 |  | Mn-54 |  | Co-60 |  |
| Protective tubes system | 1.00∙107 |  | 1.22108 |  | 7.47107 |  | 9.29107 |  | 5.99108 |  |
| Hot pipeline | 1.29107 |  | 1.52108 |  | 1.04108 |  | 1.29108 |  | 7.59108 |  |
| Hot header of SG | 2.69107 |  | 3.00108 |  | 2.50108 |  | 3.08108 |  | 1.54109 |  |
| Tubes bundle of SG | 3.70106 |  | 3.13107 |  | 1.79107 |  | 2.29107 |  | 2.17108 |  |
| Cold header of SG | 2.97107 |  | 2.33108 |  | 1.56108 |  | 1.95108 |  | 1.92109 |  |
| Cold pipeline | 1.62107 |  | 1.42108 |  | 7.55107 |  | 9.62107 |  | 9.92108 |  |
| RCP |  | 5.07107 |  | 3.96108 |  | 3.26108 |  | 4.11108 |  | 3.96109 |
| Reactor pressure vessel |  | 1.33107 |  | 1.23108 |  | 5.92107 |  | 7.62107 |  | 7.96108 |

Primary coolant purification system (TC 60-90)

The TC 60-90 system is provided for permanent purification of the reactor coolant system from disperse corrosion products of the pipelines and components of the primary system in order to decrease sediments of those products in the coolant path. The purification system decreases the radiation exposure to the personnel who will perform inspection and maintenance of the primary system.

The TC 60-90 purification system operates at normal operating temperature and pressure of the reactor coolant system. The filters are switched on together with the RCP and operate permanently. Filter capacity is 100 m3/h. They are disconnected only when the RCPs are shut down.

The factor of purification from disperse corrosion products is 0.8. The activities of corrosion products on the filter of the TC 60-90 coolant purification system are given in Table 12.2.1.1-12.

Table 12.2.1.1-12 Activities of corrosion products on the filter of ТС 60-90 coolant purification system

| Nuclide | Activity of corrosion products on the filter of ТС 60-90 system, Bq/m3 |
| --- | --- |
| Cr-51 | 6.191010 |
| Mn-54 | 7.501010 |
| Fe-59 | 1.711010 |
| Co-58 | 1.441011 |
| Co-60 | 2.041012 |
| Total | 2.341012 |

In calculations for the BNPP the average decontamination factor has been used.  The decontamination factor for high-temperature filters depends on water chemistry mode of the primary circuit coolant and a reactor operation mode.

Decontamination factors of the primary circuit coolant from the corrosion product activity of the high-temperature filter, received from the Balakovo NPP are as follow:

– general iron         – 50…90%;

– chromium-51      – 80…85%;

– cobalt-60            – 50…70%;

– iron-59               – 90%.

Table 12.2.2-1 presents air activity in the enclosed space of the ZA/B building during normal unit operation after 7000 hours.

Table 12.2.2-1 Air activity in the enclosure space of building ZA/B during normal unit operation

| Nuclide | Airborne activity , Bq/m3 | AVApers, Bq/m3 |
| --- | --- | --- |
| Br-84 | 7.00.103 | 3,50105 |
| Kr-85m | 1.00∙105 | - |
| Kr-85 | 7.00.101 | - |
| Br-87 | 2,80.102 | - |
| Kr-87 | 7,80.104 | - |
| Kr-88 | 2,60.105 | - |
| Rb-88 | 5,20.104 | 4,70105 |
| Kr-89 | 2,20.103 | - |
| Rb-89 | 1,60.104 | 5,30105 |
| Sr-89 | 6,70.102 | 8.00103 |
| Kr-90 | 2,70.102 | - |
| Rb-90 | 1,80.103 | - |
| Sr-90 | 2,30 | 3,30102 |
| Sr-91 | 2,40.104 | 4,70104 |
| Sr-92 | 2,30.104 | 7,30104 |
| Mo-99 | 2,40.102 | 3,50104 |
| Ru-103 | 2,10.102 | 1,60104 |
| Ru-106 | 3.00 | 1.00∙103 |
| Rh-106 | 1.00∙10-2 | - |
| Te-131 | 3,40.103 | 3,50105 |
| I-131 | 1,10.105 | 1,10103 |
| Te-132 | 3,10.103 | 4,40103 |
| I-132 | 1,40.105 | 8,30104 |
| Te-133 | 3,10.103 | 40105 |
| I-133 | 2,95.105 | 5,30103 |
| Xe-133 | 4,10.105 | - |
| I-134 | 6,20.104 | 1,70105 |
| Cs-134 | 9,30.104 | 1,20103 |
| I-135 | 2,10.105 | 2,40104 |

Continuation of Table  12.2.2-1

| Nuclide |  | Airborne activity, Bq/m3 |  | AVApers, Bq/m3 |
| --- | --- | --- | --- | --- |
| Xe-135 | 2,50.105 |  | - |  |
| Cs-137 | 1,50.105 |  | 1,70103 |  |
| Xe-138 | 1,30.104 |  | - |  |
| Cs-138 | 4,40.104 |  | 3,10105 |  |
| Ba-139 | 3,70.104 |  | 2,20105 |  |
| Ba-140 | 1,40.103 |  | 8.00103 |  |
| La-140 | 1,90.102 |  | 1,30104 |  |
| Ce-141 | 3,10.102 |  | 2,60103 |  |
| Ce-144 | 4,80.101 |  | 2,40102 |  |
| Pr-144 | 4,80 |  | 4,20105 |  |
| Zr-95 | 3.00.102 |  | 3,20103 |  |
| Nb-95 | 2,30 |  | 5,70103 |  |
| Zr-97 | 1,60.104 |  | 1,90104 |  |
| Nb-97 | 5,20.103 |  | 1,80105 |  |
| Na-24 | 6,30.104 |  | 2,70.104 |  |
| K-42 | 2,80.105 |  | 6,20.104 |  |
| Fe-59 | 5,60 |  | 3,60.103 |  |
| Co-58 | 3.00.101 |  | 5,30.103 |  |
| Cr-51 | 4,10.101 |  | 3,80.105 |  |
| Mn-54 | 5,60 |  | 1,20.105 |  |
| Co-60 | 5,20.101 |  | 8,30.102 |  |

In periodically attended rooms having air contamination sources in a form of uncontrolled leakages of liquid radioactive fluids from the process equipment active ventilation systems provide content of airborne radionuclides considerably below the permissible volumetric activity for personnel, AVApers [5]. The content of radionuclides considerably below the AVApers level ensures that there will be no contribution to the effective exposure dose for personnel. Escape of radioactive gases to the ambient air of periodically attended rooms due to uncontrolled leakages can cause dose exposure rate per human body within the range 10-7…10-4 mSv/h that constitutes 0.001…1% of the permissible hourly exposure of personnel equal to 10-2 mSv/h.

Assessed inhalation personnel exposure dose from airborne radionuclides in the periodically attended rooms during personnel staying in them for a half of the working shift does not exceed 2.510-2 mSv (e.g. restricted access area inside the containment  maximum value),

Which is 24% of the regulated value.

The concentration of radionuclides in the controlled access area air inside the containment of the  ZA building during power operation of the plant and in the machine hall inside the containment during fuel handling is  assessed conservatively.

In this modes, radionuclides release into the air is caused by water evaporation from:

- fuel pond (power operation mode)

- fuel pond and reactor internal pools (refuelling mode).

In the assessment of the airborne concentrations, the operation of the ventilation systems TL06-07, TL09 (power operation mode) and TL32 (refuelling mode) was considered.

Results of the assessment of the airborne radionuclides concentration are provided in Table 12.2.2-2.

Table 12.2.2-2 Concentration of airborn radionuclides

| Radionuclide | Radionuclides concentration in the machine hall air, Bq/m3 |  | AVApers. Bq/m3 |
| --- | --- | --- | --- |
|  | Power operation mode | Preventive maintenance mode |  |
| Sr-89 | 6,8210-2 | 2,1710-2 | 8,00103 |
| Sr-90 | 1,3810-4 | 4,3610-5 | 3,30102 |
| Sr-91 | 1,7110-2 | 5,7310-3 | 4,70104 |
| Mo-99 | 8,8010-3 | 2,8210-3 | 3,50104 |
| Ru-103 | 1,3810-2 | 4,3710-3 | 1,60104 |
| Ru-106 | 2,0410-4 | 6,4710-5 | 1,00103 |
| Rh-106 | 2,0410-4 | 6,4710-5 | 0,00101 |
| I-131 | 7,55101 | 2,43101 | 1,10103 |
| Te-132 | 1,2110-1 | 3,8910-2 | 4,40103 |
| I-132 | 1,2510-1 | 4,0110-2 | 8,30104 |
| I-133 | 2,65101 | 8,66 | 5,30103 |
| Cs-134 | 2,11101 | 6,69 | 1,20103 |
| I-135 | 2,7010-1 | 9,2510-2 | 2,40104 |
| Cs-137 | 3,49101 | 1,11101 | 1,70103 |
| Ba-140 | 5,7310-2 | 1,8210-2 | 8,00103 |
| La-140 | 4,5810-2 | 1,4410-2 | 1,30104 |
| Ce-141 | 2,0910-2 | 6,6110-3 | 2,60103 |
| Ce-144 | 3,3510-3 | 1,0610-3 | 2,40102 |
| Pr-144 | 3,3510-3 | 1,0610-3 | 4,20105 |
| Na-24 | 3,8510-1 | 1,2710-1 | 2,70104 |
| Cr-51 | 6,34 | 2,01 | 3,80105 |
| Mn-54 | 1,26 | 3,9910-1 | 1,20105 |
| Fe-59 | 2,9810-1 | 9,4410-2 | 3,60103 |
| Co-58 | 1,73 | 5,5010-1 | 5,30103 |
| Co-60 | 6,30 | 2,00 | 8,30102 |
| Zr-95 | 1,9210-2 | 6,0710-3 | 3,20103 |
| Nb-95 | 1,1410-3 | 3,5510-4 | 5,70103 |
| Zr-97 | 9,5110-2 | 3,1310-2 | 1,90104 |
| Nb-97 | 1,0210-1 | 3,3710-2 | 1,80105 |
| H-3 | 1,06105 | 1,50105 | 4,40105 |
| Total | 1,06105 | 1,50105 |  |

Comparing the concentrations of airborne radionuclides with AVApers,. We can see that the design values are considerably less than the allowed ones.

.

Table 12.2.3.1-1 provides the exposure dose rates on the surfaces of the primary and secondary containmnets during the design-basis accident with a reactor coolant NB850 pipeline break.

Table 12.2.3.1-1 Dose rates on the outer surfaces of the primary and secondary containments

| Containment number | Exposure dose rate, mGy/hour |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Time since the beginning of accident, hour |  |  |  |  |
|  | 0 | 1 | 24 | 240 | 720 |
| 1. (steel) | 6,4103 | 4,6 103 | 4,9102 | 2,4102 | 9,5101 |
| 2. (concrete) | 7,810-6 | 6,210-6 | 7,710-7 | 1,810-7 | 5,910-8 |

The measurement ranges of the instrumentation used for monitoring the activity of IRG, aerosols and iodines are as follows:

- IRG:    2.5 104 - 8 109 Bq/m3;

- I-131    3.7 - 3.7 106 Bq/m3;

- Aerosols: 25 - 105 Bq/m3 and 1 - 106 Bq/m3.

Table 12.3.4 -1 The list and description of the laboratory and portable instruments are provided in Table 12.3.4-1.

| Instrument description and designation | Purpose | Instrumentation range | Limits of the allowed main instrumentation error, % | Working temperature and humidity range |
| --- | --- | --- | --- | --- |
| Portable instruments |  |  |  |  |
| Dosimeter – radiometer МKS АТ 117М with unit:  – BDKG-01 | MED measurement | 0.1 Sv/h to 10 Sv/h | ±15 | -30 to +50 С 98% at 35 С |
| Dosimeter – radiometer МKS АТ 117М with units:  – BDKG-01  – BDPB-01 | MED measurement Measuring  particles flow density from the surface | 0.1 Sv/h to 10 Sv/h | ±15 ±30 | -30 to +50 С 98% at 35 С |
| Dosimeter – radiation meter МKS АТ 117М with units:  – BDKG-01  – BDPB-01  – BDPA-01 | MED measurement Measuring  particles flow density from the surface Measuring  particles flow density from the surface | 0.1 Sv/h to 10 Sv/h 1 to 105 part./(min×cm2) 0.1 to 105 part./(min×cm2) | ±15 ±30 ±30 | -30 to +50 С 98% at 35 С |
| Portable air sampler PVP-04А | Measuring air samples on aerosol filters and sorption column with activated charcoal | Capacity: 20 to 120 l/min | ±10 | -10 to +40 С 80% at 25 С |

Table 12.3.4–1 (cont.)

| Instrument description and designation | Purpose | Instrumentation range | Limits of the allowed main instrumentation error, % | Working temperature and humidity range |
| --- | --- | --- | --- | --- |
| Iodine monitor (mobile) IM-201M | Volumetric activity of radioactive Iodine-131 | 3.7 to 3.7106 Bq/m3 |  15 | 0 to +55 С up to 80  at + 35 С |
| Laboratory instruments |  |  |  |  |
| One-channel gamma-spectrometer complex (one detector with 10 % recording efficiency) SKS-07-P-G64 | Gamma-spectrometer analysis |  |  | 1 to +40 С 80% at 25 С |
| Two-channel gamma-spectrometer complex (two detectors with 30 % recording efficiency) SKS-07P-G64-G64 | Gamma-spectrometer analysis |  |  | 1 to +40 С 80% at 25 С |
| Liquid beta-spectrometer, packaged SKS-07P-B11 | Beta-spectrometer analysis of liquid samples |  |  | 1 to +40 С 80% at 25 С |

Table 12.3.4–1 (cont.)

| Instrument description and designation | Purpose | Instrumentation range | Limits of the allowed main instrumentation error, % | Working temperature and humidity range |
| --- | --- | --- | --- | --- |
| Gas radiometer RGB-02 | Gas volumetric activity measurement |  |  | 1 to +40 С 80% at 25 С |
| Radiometer RKS-02С1 with detection units:  – BDIA-03С  – BDIB-04С |  |  |  | 1 to +40 С 80% at 25 С |
| Alpha-beta radiometer UMF-2000 | Measuring total alpha or beta-emitting activity in samples | : 0.01 to 1000 Bq : 0.1 to 3000 Bq | ±15 | 1 to +40 С 80% at 25 С |
| Low-background multifunctional radiometer RKS-18R | Provided for measurement of alpha- and beta- active radionuclides in flat sources (analytical filters АFА-RSP-20) | : 0.1 to 1×104 Bq : 1 to 1×105 Bq | ±15 | 1 to +40 С 80% at 25 С |

Table 12.3.4–2 Main technical characteristics of data processing, power supply and alarm devices and components.

| Device description and purpose | #### Tasks and functions | Working temperature and humidity range | Dimensions, weight | Protection level (as per GOST 14254-96) | Additional information |
| --- | --- | --- | --- | --- | --- |
| Radiation monitoring console UIK-47R Including workstation РС-1; Input/output device (interface and data exchange device) UVC-65R2 | - data acquisition from UVC-65R via data transmission channel RS 485; - data processing and display in digital and graphical form on the screen and color display; - monitoring and setpoints of working modes of instrumentation channels in automatic and manual modes; - data base support | +10 to +40 оС; 80 % at +35 оС | 1156x1380x605 mm 250.0 kg 405x480x235 mm 18 kg | IP20 | Only for ARMS normal operation Electric power supply: 220 V (+10, minus 15) %, 503 Hz, 650 VA |
| Input/output device (interface and data exchange device) UVC-65R | - data acquisition from UNO-201 via seven data transmission channels RS 485; - data exchange with power unit upper level system via ETHERNET network channels, as well as with the radiation monitoring workstation via data transmission channels RS 485 | +1 to +45 оС; 98 % at +35 оС | 405x480x235 mm 18 kg | IP20 | Electric power supply: 220 V (+10, minus 15) %, 503 Hz, 65 VA |

| ##### Table 12.3.4–2 (cont.) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Device description and purpose | Tasks and functions | Working temperature and humidity range | Dimensions, weight | Protection level (as per GOST 14254-96) | Additional information |
| Data acquisition and processing device UNO-201 | - obtaining signals from sensors via 10 independent channels; - processing of signals received from sensors by conventional algorithms; - formation of signals exceeding warning and accident levels; - demonstration of processing results as well as other data on built-in digital display by means of any of the selected channels; - local light and sound alarm device testing; - sensor testing signal formation according to established algorithms; - creation and storage of data archive of processing results by all channels; - creation and transmission of current data and archive via RS485 channels to the devices of the next hierarchical level; - receiving and checking the signals obtained from the next hierarchical level via RS485 channel; - formation of galvanicaly-isolated external device (safety panels indicators, gas-exchange device, electrically-operated valves) testing signals; - power supply with constant voltage of units BKK-77Е | +1 to +50 оС, 98 % at +35 оС | 600x400x380 mm 40 kg | IP54 | Up to 10 channel. Power supply: 220 V (+10, minus 15) %, 503 Hz, 160 VA (for 10 channels) |
| Switching module BKK-77E | - sensor energizing; - transfer and switching of status and monitoring data signals | 50 to +60 оС, 98 % at +35 оС | 202x132x262 mm 8.0 kg | IP55 | Connection of up to 2 sensors. Power supply: 30 – 50 V DC |
| Alarm device USR-2P (USR-2P-01) including: alarm module BSR-23P; light alarm modules (light indicators) BSS-17P (BSS-18P); sound alarm ZVRP220 | - data output in a form of optical and acoustical signals indicating that the parameters monitored exceeded warning and accident levels in the area of BSS-17P (BSS-18P)and ZVRP220 location; - data output via 5 independent channels; - at BSS-17P application in USR-2Р device information is provided in three levels: EXCEEDING IS ABSENT; WARNING LEVEL IS EXCEEDED; EMERGENCY LEVEL IS EXCEEDED; - at BSS-18P application in USR-2Р-01 device information is provided in two levels: EXCEEDING IS ABSENT; EMERGENCY LEVEL IS EXCEEDED | BSR-23P +1 to +50 оС 95 % at +35 оС BSS-17P or BSS-18P 40 to +70 оС 100 % at +35 оС ZVRP220 40 to +70 оС 95 % at +35 оС | BSR-23P 470x340x375 mm 26 kg BSS-17P or BSS-18P 620x110x165 mm 5,8 kg ZVRP220 310x192x160 mm 2,2 kg | BSR-23P IP54 BSS-17P (BSS-18P) IP55 | Power supply: 220 V (+10, minus 15) %, 503 Hz, 90 VA |

Table12.3.4-3 Sensor main technical characteristics

| Type of sensor | Measured physical value, unit of measurement | Instrumentation range | Allowed main instrumentation error, % | Working temperature and humidity range | Dimensions, weight | Protection level (as per GOST 14254-96) | Sensitivity |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Detection module BDMG-08R-03 | Gamma-radiation absorbed dose rate, Gy/h | 110-7 to 110-4 | ± 25 | 50 to + 60 С to 90  at +60 С | 65x400 mm 2.0 kg | IP67 | 0.82107 с-1Gy-1h (by Cs-137) |
| Detection module BDMG-08R-04 |  | 510-6 to 110-2 |  | 50 to + 60 С up to + 70 С during 5 h, up to +98 % at +60 С | 65x195 mm 0.8 kg | IP67 | 0.2106 с-1Gy-1h (by Cs-137) |
| Detection module BDMG-08R-05 |  | 510-3 to 10 |  |  | 65x200 mm 0.9 kg | IP67 | 1.0103 с-1Gy-1h (by Cs-137) |
| Detection device UDMS-20R Including: Processing module BPH-59R; Detection module BDMG-44R | Gamma-radiation absorbed dose rate, Gy/h | 510-3 to 1105 |  30 % | For sensors 30 to + 200 оС. up to 100 % at + 40 оС; for processing module 30 to +60 оС. up to 98 % at +35 оС | BPH-59R 526x275x153 mm 15.6 kg BDMG-44R 65x481 (cable length 28120 mm) 16.6 kg | IP55 | 1.0102 с-1Gy-1h |

| ##### Table 12.3.4-3 (cont.) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Type of sensor | Measured physical value, unit of measurement | Instrumentation range | Allowed main instrumentation error, % | Working temperature and humidity range | Dimensions, weight | Protection level (as per GOST 14254-96) | Sensitivity |
| Detection device UDPG-04R Including: Processing module BPM-15R; Detection module UDPG-05R | Volumetric activity of gamma-radionuclides in steam, Bqm3 | 1104 to 5104 5104 to 5108 | ± 40 ± 25 | +5 to +55 С up to 95  at + 30 С | BPM-15R 144x236x300 mm 11 kg UDPG-05R 460x470x360 mm 160 kg | IР55 | 1.410-4 с-1Bq-1m3 (by Ar-41) |
|  | Volumetric activity of Nitrogen-16 radionuclides in steam, Bqm3 | 3103 to 5108 | Error not prescribed by regulations (indicator channel) |  |  |  | 5.010-5 с-1Bq-1m3 (by N-16) |
| Detection device UDGB-02R Including: Processing module B¦I-10R; Detection module BDGB-29R | Gas airborne volumetric activity, Bqm3 | 2.5104 to 8109 | ± 50 | +1 to +50 С. up to 80  at + 35 С | BI-10R 300x240x90 mm 5.0 kg BDGB-29R 390x185x300 mm 15 kg | IР55 | 2.310-5 с-1Bq-1m3 (by Kr-85) |
| Detection device UDGB-02R1 Including; Processing module BI-10R1; Detection module BDGB-29R1 | Gas airborne volumetric activity, Bqm3 | 5107 to 11013 | ± 50 | +1 to +50 С. to 80  at + 35 С | BI-10R1 300x240x90 mm 5.0 kg BDGB-29R1 275x185x300 mm 24 kg | IР55 | 3.010-8 с-1Bq-1m3 (by Kr-85) |
| # Detection device UDZhG-20R Including: Processing module BPM-16R; Detection module UDZhG-25R | Radionuclide volumetric activity in liquid, Bqм3 | 3104 to 3108 | ± 30 | + 5 to +55 С to 95  at + 30 С | BPM-16R 144x236x300 mm 11 kg UDZhG-25R 565x740x370 mm 460 kg | IР55 | 2.010-4 с-1Bq-1m3 (by Cs-137) |
|  |  | 1.0104 to 3104 | ± 35 |  |  |  |  |
|  | Sodium 24 radionuclide volumetric activity in liquid, Bqm3 | 3.0103 to 3.0108 | Error not prescribed by regulations (indicator channel) |  |  |  | 2.010-4 с-1Bq-1m3 (by Cs-137) |
| Detection module BDAS-03P-01 | Beta-active aerosol airborne volumetric activity, Bqm3 | 2.5101 to 1105 | ± 50 | + 5 to +50 С to 80  at + 35 С | 405x267x292 mm 16 kg | IР54 | 5.010-2 с-1Bq-1м3 (by Cs-137) at Тi = 6 h and W=0.3310-3 m3s-1 |
| Iodine monitor (stationary) IM 201 | Iodine-131 airborne volumetric activity, Bqm3 | 3.7 to 3.7106 | ± 30 | 0 to +55 С to 80  at + 35 С | 1280x830x680 mm 300 kg | IР55 |  |

A list of instruments and equipment used in checking and testing the ARMS components is provided in Table 12.3.4-4.

Table 12.3.4-4  List of instruments and equipment used in checking and testing the ARMS components

| Decsription | Identification, specification (TU), drawing identification, brief | Quantity | Note |
| --- | --- | --- | --- |
| Reference Grade II gamma-radiation device with Caesium- 137 source | Shall ensure certified values of absorbed dose rates 410-6 to (8,0±0,8) Gy/h with an error not more than ±7 %. | 1 | Radioactive sources are not included in the ARMS delivery kit. The order is to be places by NPP services. |
| Testing device KPG-04R1 | ABLK.41 8234.41 8 |  | Delivered in commissioning kit EKDF.412919.020 |
| Reference spectrometer gamma-sources | ОSGI, ТU17-03-82: Cesium-137А=104 Bq, 105 Bq, 106 Бк; Cobalt-60 А= 105 Bq, 106 Bq | 1 each | Radioactive sources are not included in the ARMS delivery kit. The order is to be places by NPP services. |
| Reference Grade II beta-radiation sources Strontium-90 + Ittrium-90 | Sources 1СО-531, 1СО-213, 1СО-533, 1СО-135, 1СО-216 ТУ95 477-83 | 1 each | Sources shall be certified as reference Grade II measures |

Table 12.4-1 Man-hours  of reactor assembly/disassembly of   «Busher-1» APS.

| - Operation name | - Time, h | Brigade pers. |
| --- | --- | --- |
| Reactor disassembly |  |  |
| - Removal of upper unit traverse | 1 | 2 |
| - Disconnection of electrical interconnection unit cables | 1 | 3 |
| - Mount of the machine for disassembly of CPS drives on the steel embedment of concrete vault | 1 | 2 |
| - Decommutation of linear position indicators | 16 | 5 |
| - Linear position indicator transportation to the vessel internal transshipment pool | 10 | 3 |
| - Demultiplexing the flanges of the internal reactor control assembly | 8 | 2 |
| - Removal of electrical interconnection unit | 2 | 2 |
| - Disassembling the cooling air bleed vent caisings | 1 | 3 |
| - Demultiplexing the flange connection of the vent elbow | 1 | 2 |
| - Removal of the upper unit heat-insulation | 1 | 2 |
| - Demultiplexing the main reactor connector | 18 | 3 |
| - Setting the protective caps on internal reactor control rises | 2 | 2 |
| - Disconnection of crossbars and regulating unit and setting on bolt pins of motion blocks | 8 | 3 |

Тable  12.4-1 (cont.)

| - Operation name | - Time, h | Brigade, pers. |
| --- | --- | --- |
| - Removal of main connector wrench | 1 | 2 |
| - Setting the centring system supports on upper unit | 1 | 2 |
| - Setting the traverse on upper unit | 1 | 2 |
| - Removal of upper unit from reactor | 3 | 2 |
| - Setting the upper unit traverse on platform for transportation of protective tube unit | 1 | 5 |
| - Transportation of tare with studs from vessel internal revision vault | 2 | 2 |
| - Setting the platform on protective tube unit for transportation of protective tube unit | 1 | 2 |
| - Removal of protective caps from internal reactor control rises | 1 | 2 |
| - Setting the internal reactor control assembly to transportational position | 2 | 2 |
| - Filling the vessel internal transshipment pool | 4 |  |
| - Setting the protective tube unit on protective tube unit revision vault | 2 | 1 |
| - Setting the control system during transshipment into reactor | 8 | 3 |
| - Disassembling the disassemly device of control and protection system drives and its assembly in upper unit revision vault area | 1 | 2 |

Table12.4-1 (cont.)

| - Operation name | - Time,h |  |  | Brigade, pers. |  |
| --- | --- | --- | --- | --- | --- |
| Reactor assembly |  |  |  |  |  |
| - Setting the disassemly device of control and protection system drives near concrete vault |  | 1 |  | 2 |  |
| - Disassembling the control system during transshipment |  |  | 3 |  | 3 |
| - Setting the protective tube unit into reactor |  |  | 3 |  | 2 |
| - Draining the transshipment pool |  |  | 4 |  |  |
| - Setting the internal reactor control assembly into lower position |  |  | 2 |  | 2 |
| - Setting the protective caps of internal reactor control rises |  |  | 1 |  | 2 |
| - Setting the platform for transpotation of protective tube unit to protective tube unit revision vault |  |  | 1 |  | 2 |
| - Setting the main connector gaskets |  |  | 2 |  | 2 |
| - Setting the main connector studs |  |  | 16 |  | 2 |
| - Setting the upper unit on the reactor pressure vessel and removal of the centring system supports |  |  | 2 |  | 2 |
| - Removal of traverse from the upper unit |  |  | 1 |  | 2 |
| - Bar coupling with control rod |  |  | 16 |  | 3 |
| - Tightening the reactor pressure vessel with the wrench |  |  | 20 |  | 7 |
| - Removal of the main connector wrench |  |  | 1 |  | 1 |
| - Setting the heat insulation of the upper unit |  |  | 1 |  | 2 |
| - Setting the vent elbow |  |  | 1 |  | 2 |
| - Assembling the cooling air bleed vent caisings |  |  | 1 |  | 3 |
| - Setting the electrical interconnection unit |  |  | 1 |  | 2 |
| - Transpotation and setting the linear alignment transducers |  |  | 24 |  | 3 |

Table 12.4-1 (cont.)

| - Operation name | - Time,h | Brigade, pers. |
| --- | --- | --- |
| - Tightening the linear position indicators | 20 | 3 |
| - Tightening the assembly flanges of the internal reactor monitoring system | 10 | 3 |
| - Stub line connection of electrical interconnection unit | 21 | 3 |
| - Setting the upper unit traverse after exterior check of upper unit | 1 | 1 |

Radiation dose distribution according to  items of work during scheduled preventive maintenance in  the third unit  of Balakovo NPP (03.06  31.07.2000 ):

| repair of reactor coolant pump - 0,0184 man. Sv; |  |
| --- | --- |
| Repair of steam generator - 0,6049 man. Sv; |  |
| Repair of pressurizer - 0,1411 man. Sv; |  |
| Repair of details and mechanisms of the control and protection system (CPS) - | 0,0079 man. Sv; |
| Transport technological procedures with spent fuel container ТК-13 – 0,0017 man. Sv; |  |
| Repair of transformers and special water treatment system equipment - | 0,0039 man. Sv; |
| Operation with falsework and heat insulation – 0,0079 man. Sv; |  |
| Operation with radioactive wastes – 0,0011 man. Sv; |  |
| Reactor operations – 0,1411 man. Sv; |  |
| Other opereations – 0,0009 man. Sv. |  |

Comparison of  estimated and actual data according to collective  dose spending  during reactor  disassembly/assembly shows  that actual data for Balakovo NPP  (0,1411 man.Sv/year) don’t exceed estimated data for  NPP  Bushehr-1   (0,46 man.Sv/year).

It is subject to  conservative lead-up:

- When calculating  the dose  capacities they used   radiomuclide activity values which were maximum  for in-service time of unit  (30 years);

- When calculating the collective dose spending they estimated  necessary man hours conservatively rated.

The management direction and practical assistance to the divisions in organizing activities to provide radiation safety is the responsibility of Dosimetry service, which report directly to the Chief of Chemical-Dosimetry Department.

In order to successfully carry out the tasks assigned to the dosimetry service, this division should include the organizational units shown in Figure 12.5.1.1-1.

In order to maintain personnel and population exposure doses at lowest possible levels, «Radiation monitoring routine» should be developed.

«Radiation monitoring routine» is the basic document, stipulating the volume, types and periodicity of radiation monitoring at the NPP, based on the following:

- requirements of sanitary rules and standards for radiation safety assurance, codes for design and operation of nuclear power plants;

- specifications for specific instrumentation and auxiliary equipment;

- techniques of measuring specific radiation parameters;

- requirements for provision of routine and overhaul repairs, metrological inspections and equipment testing.

«Radiation monitoring routine» is developed to perform the following main tasks:

- providing methodological documents with instructions on implementing the requirements of the effective codes and regulations for radiation safety at the NPP;

- control of radiation situation in controlled access area, common access area, sanitary-protective area and surveillance area of NPP;

- accounting exposure doses of all individuals, developing and implementing activities, aimed at reducing personnel radiation exposure;

- developing and carrying out activities, directed at increasing NPP radiation safety;

- maintaining radiation safety at the level, conforming to the requirements of regulation documents.

«Radiation monitoring routine» the basis for development of operating instructions for systems and equipment, which should include specific directions to personnel as to methods and technique of their work during normal operating conditions, as well as for instructions, stipulating personnel actions in cases where the permissible levels of radiation monitoring parameters have been exceeded. These instructions are referred to the working documents and are the basis for the administrative structures to perform effective organizational and technical protective measures.

Table 12.5.2.2-1 Main technical characteristics of the APDMS instruments

| Type of instruments | Purpose | Measured value | Instrumentation range | Allowed main error, % |
| --- | --- | --- | --- | --- |
| Personal dosimetry monitoring complex DVG-07 «Framcard» including: Photo-luminiscent measuring device UIF-01; Data eraser USI-01; Personal photon radiation dosimeter DVG-01m | Current monitoring of external photon radiation based on the dosimeter radiophoto-luminiscent system "Framcard DVG-07" | Hp(10), mSv | 0.05 1.0104 | ± 15 (at Hp(10)>0.05 Зв) |
|  |  |  |  | ± [15+1.75/Hp(10) мЗв] (at Hp(10)<0.05 Зв) |
| Dosimeter thermo-luminiscent device DVG-02TM including: Counter DVG-02ТМ; Neutron radiation individual dosimeter DVN-А-02 | Current monitoring of external neutron radiation based on dosimeter thermo-luminiscent system DVG -02ТМ | Hp(10), mSv | 0.1  100 | ± 30 |
| Personal gamma-radiation dosimeter DKG-05D including: Counter US-05S; Personal gamma-radiation dosimeter DKG-05D; Cassette charger KZU-27 | On-line monitoring of external photon radiation based on electronic direct indication dosimeters DKG-05D | Hp(10), mSv | 110-4  1.5104 | ± [15+20/Hp(10) Sv] |
|  |  | Personal equivalent dose rate Нр(10), мSv/h | 110-3 1.0104 | ± [15+60/ dose rate Hp(10). Sv/h] |

Table 12.5.2.2-1 (cont.)

| Type of instruments | Purpose | Measured value |  | Instrumentation range | Allowed main error, % |
| --- | --- | --- | --- | --- | --- |
| Human radiation spectrometer with shadow protection SEG-10P | Internal personnel radiation monitoring equipment based on whole body counter (WBC) | 60Co activity in human lungs, Bq | 501.0105 |  | ± 40 |
| Human radiation spectrometer with shadow protection SEG-10P-01 |  | 60Co activity in human lungs, Bq | 501.0105 |  | ± 40 |
|  |  | 137Cs activity in the whole human body, Bq | 3,31027.0105 |  | ± 40 |
|  |  | 131I in human thyroid gland, Bq | 35  2.0106 |  | ± 40 |
| APDMS server CM1820МС | Data acquisition from reading devices, data processing and display in digital and graphic form on color display; data base keeping | - | - |  | - |
| Workstation PPC-5070 |  | - | - |  | - |

Human radiation counter can measure the contents of the following isotopes:

- iodine-131 in thyroid gland in the range of 3,7102…3,7105 Bq;

- cobalt-60 and cesium-137 in whole body in the range of 3,7104…3,7107 Bq;

- cobalt-60 and cesium-137 in lungs in the range of 3,7103…3,7106 Bq.

The data from detecting units of HRM are supplied to the personal computer where they are processed and internal radiation dose can be calculated.

The information from the personal computer is transferred to the APDMS .database.

Information on the databases of the APDMS and report system description of the APDMS is provided in the document «Software-hardware complex of the APDMS for the BNPP-1. Operation Manual PBAV.412161.007 RE»

Pocket electronic dosimeters provide the means to measure gamma radiation with the use of G-M counters or a semiconductor detector, in the energy range from 0.06 to 3 MeV. The measurement ranges are as follows:

- for equivalent dose rate (EDR) 10-6…1 Sv/h;

- for equivalent dose 10-6…1 Sv.

The information about the EDR value or about the equivalent dose is indicated on the display, and, when the threshold levels are exceeded, light and audible annunciation is actuated.

The human radiation counter installation comprises an easy chair and changeable collimators with scintillation detecting units (NaI).

To assess intake of aerosols to the personnel bodies during radiation-hazardous activities (such as repair of equipment contaminated by radioactive compounds, refueling, radwaste disposal, etc.), portable instruments shall be used to monitor volumetric activity of aerosols in the area of works conducted. The monitoring shall be performed by the automated radiation situation monitoring subsystem in rooms  described in Section 12.3.4.

Results of individual dosimetric monitoring are supplemented by regular medical survey of the personnel.

#### Table 12.5.2.3-1 Nomenclature and main technical parameters of the surface contamination monitoring equipment

| Instrument description and designation | Purpose | Instrumentation range | Allowed main instrumentation error, % | Working temperature and humidity range |
| --- | --- | --- | --- | --- |
| Control device RZB-05 | #### Monitoring of contamination of personnel's hands, feet, bodies, work clothes by  – active nuclides and signaling on excess of prescribed contamination level | from 10 to 6103  – particle/(min×cm2) | ±10 | from 5 to +50 С 80% at 35 С |
| Control device RZB-04-04 | #### Signaling on excess of prescribed contamination threshold level by  – active nuclides of skin surface or main clothes of personnel | from 10 to 6103  – particle/(min×cm2) | ±10 | from 5 to +50 С 80% at 35 С |
| Dosimeter – radiometer МКС АТ 117M with block  – BDKG-01 | #### MED measuring | from 0,1 μSv/hr to 10 Sv/hr | ±15 | from -30 to +50 С 98% at 35 С |
| Dosimeter – radiometer МКС АТ 117M with blocks  – BDKG-01  – BDPB-01 | MED measuring #### Measurement of  – particles flux density from the surface | from 0,1 μSv/hr to 10 Sv/hr | ±15 ±30 | from -30 to +50 С 98% at 35 С |

Table 12.5.2.3-1  (Cont.)

| Name and designation of device | Function | Measurement scope | Limits of admissible basic measurement error, % | Range of working temperature and humidity |
| --- | --- | --- | --- | --- |
| Dosimeter – radiometer МКС АТ 117M with blocks  – BDKG-01  – BDPB-01  – BDPA-01 | MED measuring Measurement of  – particles flux density from the surface #### Measurement of  – particles flux density from the surface | from 0,1 μSv/hr to 10 Zv/hr from 1 to 105 particle/(min×cm2) from 0,1 to 105 particle./(min×cm2) | ±15 ±30 ±30 | from -30 to +50 С 98% at 35 С |
| Two-channel impulse count-rate meter UIM 2-3 with blocks  – UDZA-10P  – BDB2-02I2 – BDМG-08R-04 | #### Impulse counting rate measurement and signaling on excess of prescribed threshold level of impulses coming through two channels from detection blocks  –,  –, – radiation | from 0,01 to 105 с-1 | ±10 | from 5 to +50 С 80% at 35 С |

Table 12.5.2.4-1 Nomenclature and main technical parameters of main laboratory equipment

| Instrument description and designation | Purpose | Instrumentation range | Limits of the allowed main instrumentation error, % | Working temperature and humidity range |
| --- | --- | --- | --- | --- |
| One-channel gamma-spectrometer complex (one detector with 10 % recording efficiency) SKS-07-P-G64 | Gamma-spectrometer analysis |  |  | 1 to +40 С 80% at 25 С |
| Two-channel gamma-spectrometer complex (two detectors with 30 % recording efficiency) SKS-07P-G64-G64 | Gamma-spectrometer analysis |  |  | 1 to +40 С 80% at 25 С |
| Liquid beta-spectrometer, packaged SKS-07P-B11 | Beta-spectrometer analysis of liquid samples |  |  | 1 to +40 С 80% at 25 С |

Table 12.5.2.4-1 (cont.)

| Instrument description and designation | Purpose | Instrumentation range | Limits of the allowed main instrumentation error, % | Working temperature and humidity range |
| --- | --- | --- | --- | --- |
| Gas radiometer RGB-02 | Gas volumetric activity measurement |  |  | 1 to +40 С 80% at 25 С |
| Radiometer RKS-02С1 with detection units:  – BDIA-03С  – BDIB-04С |  |  |  | 1 to +40 С 80% at 25 С |
| Alpha-beta radiometer UMF-2000 | Measuring total alpha or beta-emitting activity in samples | : 0.01 to 1000 Bq : 0.1 to 3000 Bq | ±15 | 1 to +40 С 80% at 25 С |
| Low-background multifunctional radiometer RKS-18R | Provided for measurement of alpha- and beta- active radionuclides in flat sources (analytical filters АFА-RSP-20) | : 0.1 to 1×104 Bq : 1 to 1×105 Bq | ±15 | 1 to +40 С 80% at 25 С |

Abbreviations List

| EDR | - Equivalent Dose Rate |
| --- | --- |
| IRG | - Inert Radioactive Gases |
| NPP | - Nuclear Power Plant |
| RMS | - Radiation Monitoring System |
| ARMS | - Automated Radiation Monitoring System |
| APDMS | - Automated Personal Dosimetric Monitoring System |
| RMS | - Radiation Monitoring System |
| CCP ARSMS | - Central Control Post of Automated System of Radiation Situation Monitoring |
| RM AWS | - Automated Workstation of Radiation Monitoring |
| RMD AWS | - Automated Workstation of Radiation Monitoring and Dosimetry |
| AOO | - Anticipated Operational Occurrences |
| MCR | - Main Control Room |
| SG | - Steam Generator |
| OP | - Operating parameters |
| NOL | - Normal operation limits |
| ADR | - Absorbed Dose Rate |