Summary of replies to the comments on: Technical assignment (TA) For “Emergency response documentation elaboration for Bushehr NPP power unit No.1 in symptom-based emergency operating instruction form (SBEOI)”

Сводка отзывов на замечания компании TAVANA к документу: Техническое задание (ТЗ) на “Разработку комплекта противоаварийной документации для АЭС Бушер-1 в симптомно-ориентированном формате (СОАИ)”

| Comment No. | Content | Reply |
| --- | --- | --- |
| А. General comments: |  |  |
| А.1. | The more detailed time schedule shall be elaborated in the TA include detailed information on works performance sequence (stages, sub stages, i.e. performing safety analysis) with the executives. | Not accepted. The time schedule provided in TA contains sufficient information on the works performance sequence |
| А.2. | Updating of emergency response documentation shall be considered as the last stage based on modification of other systems and equipment such as stress test mobile devices, etc. | Accepted partially. Requirements to updating of the emergency response documentation are specified in item 7.5 |
| А.3. | The duration which is considered in the TA seems to be too long. It is highly recommended to reduce the duration of the project. | Accepted partially. Duration of work stages, for which JSC ATEX is responsible, is selected based on capabilities of our personnel and the personnel of NPP and RP designers. Minor duration reducing is possible at stages 6.4-6.6 (Approval by BNPP, NNSD). You are requested to send to our address your suggestions on reducing these terms. Any way, JSC ATEX will take all efforts for the mentioned terms reducing. |
| А.4. | The elaborated documentation set shall be comprehensive and covers all the aspects of emergency response in Bushehr NPP power unit No.1. In addition to operation procedures (AEI, BDBAG, SAMG) the technical assignment for the following procedures shall also be provided: - Emergency plan implementing procedures (51.BU.1 0.00.AB.WI.ATEX.015) - Security procedures - Extreme damage mitigation guidelines (stress test guidelines) - Technical Support Guidelines (TSGs) - Support procedures - Control parameter guidelines - System status assessment guideline - Plant status assessment guideline - Action assessment guideline | Not accepted. These procedures are not comprised into the set of emergency response documentation being elaborated for BNPP in the symptom-based emergency operation instructions form (SBEOI). These procedures shall be elaborated after SBEOI documents elaboration. JSC ATEX agree to take part in elaboration of the mentioned procedures by a separate Work-Order after SBEOI documents elaboration. |
| В. Specific comments: |  |  |
| В.1. Page 2, Section 6 | NNSD and BNPP approval (Items 4.7, 4.8 and 4.9) shall be performed after verification and validation stage (item 5) | Accepted. Verification and validation stage is shifted to be performed before the stage Emergency response documentation approval by NPP and RP design developers, BNPP, NNSD |
| В.1. Page 2, Section 6 | The detailed sub stages of items 3.1, 3.2, 3.3, 4.1, 4.2 and 4.3 shall be explained in the table of section 6 or 7.3. | Accepted. Explanations are provided in item 7.3 |
| В.1. Page 2, Section 6 | Description of works for stage 3.1 shall be changed to "Optimizing the existing accident elimination instruction (AEI) for all states of the power".(AEI was developed previously by the ASE and exists in the BNPP-1) | Not accepted. AEI in SBEOI form will be completely different from existing AEI both by composition and contents. Therefore, there is no point in talking about optimization, we should talk about new document (documents) elaboration. In symptom-based emergency operation procedures, the solutions and measures for an emergency response are based on a Power Unit states. When using the symptom-based approach, an operator must identify an accident before commencement of actions for emergency response. The advantage of symptom-based procedures is that the decisions in such procedures are taken based on symptoms and states of the Power Unit systems. It allows the operator to maintain optimal operational parameters without necessity to monitor over the accident scenario development. |
| В.1. Page 2, Section 6 | Description of works for stage 3.2 shall be changed to "Optimizing the existing beyond-design basis accident management guide (BDBAMG) for all states of the power unit"".(BDBA CM was developed previously by the ASE and exists in the BNPP-1) | Not accepted. BDBAMG in SBEOI form will be completely different from the existing BDBAMG both by composition and contents. Therefore, there is no point in talking about optimization, we should talk about new document (documents) elaboration. |
| В.1. Page 2, Section 6 | Amendment of documentations (Items 4.4 4.5 4.6 4.7 4.8 and 4.8) shall be removed in the table of section 6 and only the following item shall be added "Agreeing and approval of accident response documentation set by NPP&RP design developers, BNPP and NNSD". It will be conducted by BNPP. According to the comments provided by BNPP, documents shall be amended by JSC. | Not accepted. Explanations are provided in item 7.3 |
| В.1. Page 2, Section 6 | Stages and phases of works shall bear the following items: - Integration of procedures, guidelines and the plant’s emergency arrangements; - Maintenance and upgrading based on training program, stress test results. etc. | Not accepted. These works are within BNPP competence and they shall be included into BNPP Directorate plans after putting emergency operation instructions in SBEOI form into effect. |
| В.2. Page 3, Section 7.1 | Item "Requirements to structure and content…" shall be changed to "Requirements of accident management procedures and instructions elaboration" | Not accepted. One of sections of «Manual for writing emergency response documentation set procedures and instructions» is named as «Requirements to structure and content of accident management instructions and procedures set». This section shall contain requirements to structure and content of AEI, BDBAMG and SAMG, which may consist of the set of accident management procedures and instructions. Nevertheless, they will contain requirements to structure and content of each document. |
| В.2. Page 3, Section 7.1 | The following item shall be added: 5) Basic principles of emergency documentation elaboration 6) Structure and content of the accident management procedures and instructions set in symptom-based emergency operating instruction form 7) General principles of the organizational aspects of AEI, BDBAMG, SAMG (evaluation, decision making and implementation) 8) Rules for information exchange between the various teams of the emergency response organization 9) Justification of applied method to modify generic Westinghouse symptom-based emergency operating instructions for BNPP-1 | Accepted partially. It is mentioned in TA section 7.1 that «Manual for writing emergency response documentation set procedures and instructions» shall contain the following tentative list of section. Therefore, its structure and content will be detailed at elaboration of «Manual…». The following additional items are comprised into section 7.1: 5) The main principles for emergency response documentation elaboration. 6) General principles of AEI, BDBAMG, SAMG organizational aspects (assessment, decisions taking and implementation). 7) Justification of using "symptom-based" approach on methodological basis adopted by Westinghouse (USA) at elaboration of “Function Restoration Guideline” (FRG) comprised into “Emergency Response Guideline” (ERG) for BNPP-1. i.6) of the comments is not accepted as far as i.3) is available in TA section 7.1. i.8) of the comments is not accepted as far as «Rules for information exchange between the various teams of the emergency response organization» are not related to AEI, BDBAMG and SAMG content, they shall be elaborated in the form of an individual procedure and they are within BNPP responsibility area. |
| В.3. Page 4, Section 7.3 | The following points shall be added as well: - AEI, BDBAMG and SAMG shall cover shutdown plant configurations (such as an open containment equipment hatches), accidents with rapid progress, accidents taking place in the spent fuel pool and performing AM actions under conditions of severely damaged environment. - The decision making for the transition from each of the instructions (AEI, BDBAMG, SAMG) shall be clearly determined. - Any limitations of the equipment and instrumentation identified need to be specifically listed and included in the SAMGs. - Specifying the criteria for operator action taking into account ability to deactivate I&C functions without major delays. - Used the PSA results in preparation of Emergency Documentation. | Accepted partially. - Not accepted. In the titles of documents in TA Table in section 6 (items 3.1, 3.2, 3.3) it is mentioned «…for all states of the Power Unit», it means both for «hot» and for «cold» RP state. - Accepted. TA item 7.3 is supplemented with the following paragraph: - “AEI, BDBAMG and SAMG texts content shall clearly define decisions taking by SSU (emergency director) related to changeover from one instruction to another (AEI, BDBAMG, SAMG)”. - Not accepted. It is not clear, what identified limitations of equipment and instrumentation do you mean. Limitations of equipment and instrumentation identified during operation shall be removed and, if required, modifications shall be introduced into the design documentation for their elimination. It is within responsibilities of NPP operating organization. - Not accepted. The main principle of NPP safety assurance is to eliminate “human factor”. Therefore, all operator’s activities during an accident development are intended to monitor automatics functioning and the operator’s intervention into automatics functioning is allowed in some individual cases only. These cases will be described in emergency response documents with the special warnings. - Not accepted. Item 5.1 specifies the content of input data for BNPP-1 works performance with accounted amendments and supplements. PSA is comprised into the design documentation set. |
| В.4. Page 5, Section 7.4.1 | The following points shall be added as well: - Survivability of the equipment and instrumentation shall be evaluated in severe accident conditions. - Accessibility and habitability of the physical locations of the teams of evaluators and implementers as well as of the emergency director under severe accident conditions. - Analysis shall be performed to investigate the effectiveness of the accident management guidance and, where feasible, the associated reduction of risks at the plant. Analysis shall also be used to demonstrate that dominant scenarios are mitigated. | Accepted partially. Item 7.4.1 is supplemented with the following text: - survivability of the equipment and instrumentation in severe accident conditions; - accessibility and habitability of the physical locations of the personnel teams as well as of the emergency director under severe accident conditions in NPP premises; - availability of possibility for associated reduction of risks at NPP and dominant scenarios mitigation at severe accidents. |
| В.5. Page 5, Section 7.5 | The standards and approach to verification and validation of AEI, BDBAMG and SAMGs shall be clarified | Accepted. Section 7.5 is modified |
| В.5. Page 5, Section 7.5 | The need for supporting analysis for verification and validation of AEI, BDBAMG and SAMGs shall be mentioned | Accepted. Section 7.5 is modified |
| В.6. Page 6, Section 7.6 | Currently, there is no possibility of training staff by simulator for severe accident, alternative method shall be considered. | Accepted. Section 7.7 is modified |
| В.6. Page 6, Section 7.6 | The following item shall be added to the section works performance: 4 Qualification of the staff to carry out their new duties. 5 Full scope emergency exercising with SAMG implementation and management team involvement. 6 Self-assessment/critique performance during exercises 7 amendment procedures and guidelines according to self-assessment feedback. | Not accepted. These functions are comprised into responsibilities of NPP operating organization |
| В.7. Page 7, Section 7.7 | PPA plan (51.BU.1 0.00.AB.WI.ATEX.015) shall be modified base on new Emergency Documentation | Not accepted. Modification of ED «Emergency personnel protection plan in case of emergency at BNPPP-1» 52.BU.1 0.00.AB.WI.ATEX.015» is beyond this TA scope. JSC ATEX agree to take part in ED modification as per a separate Work-Order after SBEOI documents elaboration. |
| В.7. Page 7, Section 7.7 | Title shall be changed to "7.7 FSAR and EP amendment" | Not accepted. Emergency personnel protection plan in case of emergency at BNPPP-1 is beyond this TA scope. |
| В.8. Page 7, Section 7.8 | In line 14 of section 7.8 sentence "The works shall be performed by JSC A TEX personnel" shall be changed to "The works shall be performed by BNPP personnel." | Not accepted. According to agreements reached at the video-conference, as well as for establishing single responsibility for Russian and English versions, it is suggested to leave as it is " The works shall be performed by JSC ATEX personnel " |
| В.9. Page 9, Appendix No.1 | Stage number 3.1 “Elaboration of an accident elimination instruction …” shall be changed to “Optimizing the existing accident elimination instruction (AEI)…” | Not accepted. AEI in SBEOI form will be completely different from existing AEI both by composition and by contents. Therefore, there is no point in talking about optimization, we should talk about new document (documents) elaboration. |
| В.9. Page 9, Appendix No.1 | Stage number 3.2 “Elaboration of beyond-design basis accident management guide …” shall be changed to “Optimizing the existing beyond-design basis accident control manual” | Not accepted. BDBAMG in SBEOI form will be completely different from existing BDBAMG both by composition and by contents. Therefore, there is no point in talking about optimization, we should talk about new document (documents) elaboration. |
| В.9. Page 9, Appendix No.1 | Completion period of FSAR amendment (stage 7) shall be increased to "6 month". | Accepted. Completion period is changed to 6 months |
| В.9. Page 9, Appendix No.1 | Completion period of verification and validation (stage 5) shall be increased to "6 month". | Accepted partially. Completion period is changed up to 4 months |
| В.9. Page 9, Appendix No.1 | The cost of stage 3.1 and 3.2 shall be reduced, due to existing AEI and BDBA CM of Bushehr NPP unit 1. The cost of stage 3.1 and 3.2 shall be less than the cost of stage 3.3 | Not accepted. AEI and BDBAMG in SBEOI form will be completely different from existing documents both by composition and by contents. Therefore, there is no point in talking about optimization, we should talk about new documents elaboration. |
| В.9. Page 9, Appendix No.1 | Detailed resources and cost concerning the different activities shall be formed and expressed in man-days (stages 3.1, 3.2 and 3.3). Costs of feasibility study for BDBAMG and AEI are not reasonable in comparison with feasibility study for SAMG | Not accepted. Activities of personnel dispatched to IRI may be expressed in man-months partially (stages 2, 5 and 7). Calculations of activities to be performed in RF are performed as per existing Russian Price-Lists and time allowances. Costs of documents and feasibility studies development for AEI, BDBAMG and SAMG, and their agreeing by NPP and RP design developers are specified based on commercial proposals of the companies – NPP and RP design developers. |
| В.9. Page 9, Appendix No.1 | The contractor shall guarantee the agreement of design developer and approval of NNSD and BNPP for provided documentation. Therefore, the Principal should not pay expense for the amendment activities (stages 4.4, 4.5, 4.6, 4.7, 4.8 and 4.9) | Not accepted. Clarifications are provided in item 7.3 |