*Andrey Latchkov*

*MA-04-LA*

# FEED WATER PUMP MAINTENANCE

## SCOPE OF OBSEVATION

Observation over the 4 FWP – Б,В maintenance has been performed in the turbine hall of Unit 3 in course of about one hour. A workers group of 3 people of the electrical shop performed the maintenance.

## OBSEVATIONS

1. The maintenance documentation for conduction of the pressure test of the electrical motor air coolers was missing in work zone (turbine hall, level 0,0) in course of 4 FWP – Б overhaul. Failure to apply maintenance documentation for works conduction can cause human errors and low quality maintenance. (*MA-04-LA-01-pr*)
2. Failure to place plugs on the dismantled and decompressed service water supply and export pipelines of the 4 FWP-В electrical motors air coolers. However, the same pipelines of 4 FWP –Б have the plugs placed properly. Foreign Material ingress into the open pipelines can cause equipment damage. (*MA-04-LA-02-pr*)